## Executive Summary
Executive Summary: DISIS-2023-001 Phase 1 of Power Flow
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on January 29, 2023. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 2.2 posted on https://spp.org/engineering/generator-interconnection contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2023-001 Phase 1 includes study requests in the following cluster groups: ( 01 NORTH, 02 NEBRASKA, 03 CENTRAL, 04 SOUTHEAST, 05 SOUTHWEST, WECC )
DISIS Manual Version 2.2
https://www.spp.org/documents/71111/disis-study-manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
45,537.1 MW
The standard cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $7,195,472,474.22 Steady State Network Upgrade $4,924,243,471.54 Interconnection Costs: $2,271,229,002.68
Models Used in Steady State Study
2022 ITP Series, WECC Models
Winter: 2027
Summer: 2024, 2027 WECC Summer: 2023, 2028
Light: 2027 WECC Light: 2023
By: SPP Generator Interconnection Department
Published: March 1, 2024
Costs for Solar/Battery Requests were allocated using the 27SP (summer peak) model.
Costs for Wind Requests were allocated using the 27L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.

## Revision History
Revision History
Date | Author | Change Description
4533800% | SPP | Phase 1 Draft Posting
4535200% | SPP | Phase 1 Final Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4535200% | TO name | 7 | Upgrade Summary | Updated the TO owner from SUNC to WERE for network upgrade "Build a new 30 MVAR cap bank at TV1MNDV4" and "Build a new 10 MVAR cap bank at HUDSON-2"
4535200% | TO name | 7 | Upgrade Summary | Updated the TO owner From WAPA, BEPC to WAPA, MRES for the network upgrade "Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2"
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the interconnection cost for UID 158697 per TO feedback
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the interconnection cost for UID 158740 per TO feedback. Updated the Upgrade Details to remove boilerplate language associated to good faith non-TO cost estimates.
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Added a new interconnection cost (UID 158741) for project GEN-2023-036 per TO feedback
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the interconnection cost for UID 158940 per TO feedback. Updated the Upgrade Details to remove boilerplate language associated to good faith non-TO cost estimates.
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Added a new interconnection cost (UID 158941) for project GEN-2023-171 per TO feedback
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the interconnection cost for UID 158968 per TO feedback
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the interconnection cost for UID 158977 per TO feedback
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the interconnection cost for UID 158784 per TO feedback
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the interconnection cost for UIDs 158686 and 158687 per TO feedback
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the interconnection cost for UIDs 158808 and 158809 per TO feedback
4535200% | Interconnection Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the interconnection cost for UIDs 158985 and 158986 per TO feedback
4535200% | Network Upgrade Costs | 5, 6, 7, 8 | Constraint Summary/Assigned Upgrade Costs/Upgrade Summary/All Thermal | Removed the network upgrade "Rebuild the BIGSTON4 to BLAIR-ER4 230kV line 1"
4535200% | Remove Duplicates | 8 | All Thermal | Removed duplicated rows due to iterations for Group 01ALL
4535200% | Network Upgrade Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the cost for upgrade "Build a new 200 MVAR cap bank at Oahe 345 kV" from $45,256,400 to $ to be $4,978,200 consistent with capacitor bank conceptual estimates.
4535200% | Network Upgrade Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Updated the cost for upgrade "Build 150Mvar Reactive Support at Maurine 345kV" from $33,942,300to $ to be $3,733,650 consistent with capacitor bank conceptual estimates.
4535200% | Network Upgrade Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Remove the network upgrade "Rebuild OAHE 4 to SULLYBT-ER4 230kV line" and replace with the contingent upgrade "Oahe 230 kV Terminal Upgrades (WAPA)" identified in 2021 ITP
4535200% | Network Upgrade Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Removed the network upgrade "Rebuild the WHITLOCK_-RM to GLENHAM4 230kV line" and replace with the contingent upgrade "Whitlock - Glenham 230 kV Clearance Increase" identified in 2021 ITP
4535200% | Add constraint data | 5 | Constraint Summary | Added BC Loading % for some missing Group 01ALL Thermal constraints
4535200% | Upgrade Name/Network Upgrade Costs | 5, 6, 7 | Constraint Summary/Assigned Upgrade Costs/Upgrade Summary | Updated the upgrade name and description for upgrade "Rebuild the MORRILL7 to GERINGT_-TS7 115kV line 1" to indicate it is not a SPP facility). Updated allocated cost to $0 and changed upgrade type to contingent (DISIS-2020-001).
4535200% | LOIS and Limiting Element | 4 | Requests | Updated LOIS and/or Limiting Elements for GEN-2023-003, GEN-2023-035, GEN-2023-038, GEN-2023-051, GEN-2023-057, GEN-2023-072, GEN-2023-088, GEN-2023-103, GEN-2023-134, GEN-2023-166, GEN-2023-167, GEN-2023-168, GEN-2023-174, GEN-2023-177, GEN-2023-205, GEN-2023-210, GEN-2023-195, GEN-2023-196
4535200% | Constraints data and Network Upgrade | 5 | Constraints Summary | Updated Constraint details and Network Upgrade data for Group 04ALL Thermal constraints. Replaced network upgrade "Upgrade the AFTON 161/69 kV transformer 1" with "Build a new AFTON5 to MIAMI5 161kV line 2" Replaced network upgrade "Rebuild the FAIRNEO2 to FAIRTAP2 69kV line 1" with "Build a new AFTON5 to MIAMI5 161kV line 2" Removed network upgrades "Rebuild the PENSA to CLEORTP2 69kV line 1" and "Rebuild the AFTON2 to CLEORTP2 69kV line 1"
4535200% | Allocated Cost, % Allocated, PTDF | 6 | Assigned Upgrade Costs | Updated Allocated Costs. % Allocated, and PTDF for 04 SOUTHEAST requests. Updated Allocated Costs, % Allocated for a few shared network upgrades
4535200% | Allocated Cost, % Allocated, PTDF | 6 | Assigned Upgrade Costs | Updated Allocated Costs. % Allocated, and PTDF for network upgrade "Build a new HANNA to WELEETK 138kV line 1".
4535200% | Allocated Cost, % Allocated, PTDF | 6 | Assigned Upgrade Costs | Updated Allocated Costs. % Allocated, and PTDF for network upgrade "Build a new TOLK to NEEDMORE 230kV line 2".
4535200% | Allocated Cost, % Allocated, PTDF | 6 | Assigned Upgrade Costs | Updated and/or Added Allocated Costs. % Allocated, and PTDF for network upgrade "Build a new AFTON5 to MIAMI5 161kV line 2".
4535200% | Network Upgrade Costs | 6 & 7 | Assigned Upgrade Costs/Upgrade Summary | Removed network upgrades "Upgrade the AFTON 161/69 kV transformer 1", "Rebuild the FAIRNEO2 to FAIRTAP2 69kV line 1", "Rebuild the PENSA to CLEORTP2 69kV line 1" and "Rebuild the AFTON2 to CLEORTP2 69kV line 1"
4535200% | Thermal Constraints | 8 | All Thermal | Thermal constraints for group 04ALL were updated based on network upgrade changes.
4535200% | Non-Converged Constraints | 8 | All Thermal | Non-convergence constraints for groups 04ALL and 05ALL were updated to remove a few requests.

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
GEN-2023-012 | 01 NORTH | 25 | DIS-23-1 | Wind | 98.6 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | Kingsbury County 115kV Substation | DISIS STAGE
GEN-2023-013 | 01 NORTH | 25 | DIS-23-1 | Wind | 200 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | Leland Olds to Groton 345 kV Line | DISIS STAGE
GEN-2023-014 | 01 NORTH | 25 | DIS-23-1 | Wind | 200 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | Leland Olds to Groton 345 kV Line | DISIS STAGE
GEN-2023-031 | 01 NORTH | 25 | DIS-23-1 | Solar | 200 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Washburn 230 kV Substation | DISIS STAGE
GEN-2023-054 | 01 NORTH | 25 | DIS-23-1 | Solar | 400 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | LeLand Olds-Fort Thompson 345kV line | DISIS STAGE
GEN-2023-062 | 01 NORTH | 25 | DIS-23-1 | Thermal | 98 | 98 | None | ER | BEPC-SPP | REN 115 kV Substation | DISIS STAGE
GEN-2023-066 | 01 NORTH | 25 | DIS-23-1 | Hybrid; Solar/Storage | 130 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Tap Pierre - Midland 115 kV line | DISIS STAGE
GEN-2023-067 | 01 NORTH | 25 | DIS-23-1 | Wind | 41 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Sulphur 115 kV Substation | DISIS STAGE
GEN-2023-082 | 01 NORTH | 25 | DIS-23-1 | Battery/Storage | 175 | 0 | System Intact Non-Cnv | ER/NR | WAPA | White 115 kV Substation | DISIS STAGE
GEN-2023-084 | 01 NORTH | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Groton South 115 kV Substation | DISIS STAGE
GEN-2023-097 | 01 NORTH | 25 | DIS-23-1 | Battery/Storage | 250 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | Judson 345 kV Substation | DISIS STAGE
GEN-2023-098 | 01 NORTH | 25 | DIS-23-1 | Hybrid; Solar/Storage | 200 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Bison - Maurine 230 kV Line | DISIS STAGE
GEN-2023-105 | 01 NORTH | 25 | DIS-23-1 | Wind | 249 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | Chappelle Creek 345 kV | DISIS STAGE
GEN-2023-106 | 01 NORTH | 25 | DIS-23-1 | Wind | 504 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | Chappelle Creek 345 kV Substation | DISIS STAGE
GEN-2023-114 | 01 NORTH | 25 | DIS-23-1 | Wind | 425 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Jamestown 230 kV Substation | DISIS STAGE
GEN-2023-130 | 01 NORTH | 25 | DIS-23-1 | Hybrid; Solar/Storage | 96 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Whitlock 230 kV Substation | DISIS STAGE
GEN-2023-144 | 01 NORTH | 25 | DIS-23-1 | Solar | 265 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Bismarck - Jamestown 230 kV | DISIS STAGE
GEN-2023-154 | 01 NORTH | 25 | DIS-23-1 | Solar | 200 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Fort Thompson - Huron 230 kV Tap | DISIS STAGE
GEN-2023-160 | 01 NORTH | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | Belfield - Rhame 230 kV Line | DISIS STAGE
GEN-2023-181 | 01 NORTH | 25 | DIS-23-1 | Battery/Storage | 100 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | Groton - Leland Olds 345 kV Line | DISIS STAGE
GEN-2023-182 | 01 NORTH | 25 | DIS-23-1 | Wind | 300 | 0 | System Intact Non-Cnv | ER/NR | BEPC-SPP | Groton - Leland Olds 345 kV Line | DISIS STAGE
GEN-2023-198 | 01 NORTH | 25 | DIS-23-1 | Solar | 250 | 0 | System Intact Non-Cnv | ER/NR | WAPA | Hebron 230 kV Substation | DISIS STAGE
GEN-2023-011 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 190 | 160.9113 | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | ER/NR | NPPD | Harbine 115 kV Substation | DISIS STAGE
GEN-2023-040 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 105 | 51.6658 | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | ER/NR | NPPD | Carleton Junction 115 kV Substation | DISIS STAGE
GEN-2023-071 | 02 NEBRASKA | 25 | DIS-23-1 | Hybrid; Solar/Storage | 200 | 0 | Non-Cnv | ER/NR | BEPC-SPP | Elsie Tap - Paxton 115 kV Line | DISIS STAGE
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 303 | 303 | None | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 303 | 303 | None | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 303 | 303 | None | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2023-083 | 02 NEBRASKA | 25 | DIS-23-1 | Hybrid; Solar/Storage | 200 | 0 | Non-Cnv | ER/NR | BEPC-SPP | Laramie River -Sidney 345 kV Line | DISIS STAGE
GEN-2023-116 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 500 | 0 | Non-Cnv | ER/NR | NPPD | Keystone 345 kV Substation | DISIS STAGE
GEN-2023-117 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 300 | 0 | Non-Cnv | ER/NR | NPPD | Keystone 345 kV Substation | DISIS STAGE
GEN-2023-133 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 250 | 51.6958 | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | ER | NPPD | Sweetwater 345 kV Substation | DISIS STAGE
GEN-2023-146 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 125 | 125 | None | ER/NR | NPPD | Seward 115 kV Substation | DISIS STAGE
GEN-2023-147 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 85 | 0 | Non-Cnv | ER/NR | NPPD | Victory Hill - Crawford 115 kV Line | DISIS STAGE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Hybrid; Solar/Storage | 120 | 0 | Non-Cnv | ER/NR | BEPC-SPP | Grant 115 kV Substation | DISIS STAGE
GEN-2023-189 | 02 NEBRASKA | 25 | DIS-23-1 | Battery/Storage | 200 | 200 | None | ER/NR | LES | NW 68th - Holdrege 345 kV Substation | DISIS STAGE
GEN-2023-197 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 150 | 150 | None | ER/NR | OPPD | Sub 1366 - Sub 1258 161 kV | DISIS STAGE
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Hybrid; Solar/Storage | 250 | 250 | None | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2023-202 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 150 | 116.3059 | 640173 FREMONT7 115 996707 FREMONT T4 69.0 1 | ER/NR | OPPD | Tekamah - Raun 161 kV Line | DISIS STAGE
GEN-2023-216 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 200 | 41.3567 | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | ER/NR | NPPD | Turtle Creek 345 kV Substation | DISIS STAGE
GEN-2023-217 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 200 | 41.3567 | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | ER/NR | NPPD | Turtle Creek 345 kV Substation | DISIS STAGE
GEN-2023-218 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 200 | 41.3567 | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | ER/NR | NPPD | Turtle Creek 345 kV Substation | DISIS STAGE
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | 453.2632 | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | 214.2632 | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | 478 | None | ER | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | 217 | None | ER | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2023-006 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 202 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | ER | WERE | Wolf Creek- Blackberry 345 kV Line Break | DISIS STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SPS | Finney-Carpenter 345 KV line | DISIS STAGE
GEN-2023-017 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | 505492 SPRGFLD5 161 547479 LAR382 5 161 2 ftlo: 300045 7MORGAN 345 300949 7JASPER 345 1 | ER/NR | EMDE | Carl Junction Northeast 161 kV Substation | DISIS STAGE
GEN-2023-021 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | KCPL | Blue Mills 161kV Substation | DISIS STAGE
GEN-2023-023 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | KACY | Center City 161 kV Substation | DISIS STAGE
GEN-2023-024 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Rose Hill 138 kV Substation | DISIS STAGE
GEN-2023-025 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 532932 LITCH 5 161 547476 ASB349 5 161 1 ftlo: 547469 RIV4525 161 764310 G20-079-TAP 161 1 | ER/NR | WERE | Franklin - Jayhawk 161 kV Line | DISIS STAGE
GEN-2023-026 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 300 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | LaCygne - Wolf Creek 345 kV Line | DISIS STAGE
GEN-2023-032 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | KCPL | Odessa and Lexington 161 kV Line | DISIS STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | KCPL | Liberty South 161 kV Substation | DISIS STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Clear Water - Waco 138 kV line | DISIS STAGE
GEN-2023-036 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | INDN | Eckles Road 161 kV Substation | DISIS STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | KACY | Quindaro Bluffs 161 kV Substation | DISIS STAGE
GEN-2023-039 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2023-042 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | 0 | Voltage: P42:345:OKGE:SB_SOER7383:::: | ER/NR | EMDE | Noel Southwest 161 kV Substation | DISIS STAGE
GEN-2023-043 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2023-044 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2023-045 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2023-046 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2023-047 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2023-048 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2023-050 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Solar/Storage | 400 | 0 | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 ftlo: 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | ER/NR | WERE | Neosho 345 kV Substation | DISIS STAGE
GEN-2023-052 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Rose Hill 345 kV Substation | DISIS STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 100 | 0 | 505492 SPRGFLD5 161 547479 LAR382 5 161 2 ftlo: 300045 7MORGAN 345 300949 7JASPER 345 1 | ER/NR | SWPA | Carthage 161 kV Substation | DISIS STAGE
GEN-2023-063 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Solar/Storage | 135 | 0 | 509771 LLAN ET4 138 509790 CATOOSA4 138 1 ,System Intact | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | DISIS STAGE
GEN-2023-065 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 140 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Halstead 69 kV Substation | DISIS STAGE
GEN-2023-068 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2023-073 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 400 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Rose Hill 345 kV Substation | DISIS STAGE
GEN-2023-085 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 150 | 0 | Voltage: P42:345:OKGE:SB_SOER7383:::: | ER/NR | SWPA | Mansfield - Logan 161 kV Line | DISIS STAGE
GEN-2023-087 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | KCPL | Archie 161 kV Substation | DISIS STAGE
GEN-2023-089 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Buckner 345 kV Substation | DISIS STAGE
GEN-2023-090 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Buckner 345 kV Substation | DISIS STAGE
GEN-2023-091 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 504 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Buckner 345 kV Substation | DISIS STAGE
GEN-2023-093 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2023-094 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | 0 | Voltage: P12:345:OKGE:BKRBKR357_1:::: | ER/NR | WERE | Jeffery Energy Center 345 kV Substation | DISIS STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER | SUNC | Setab 345 kV | DISIS STAGE
GEN-2023-111 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Buffalo Flats 345 kV Substation | DISIS STAGE
GEN-2023-115 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | KCPL | Tap Georgetown Overton to Sedalia East 161 kV Line | DISIS STAGE
GEN-2023-118 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Buffalo Flats 345 kV Substation | DISIS STAGE
GEN-2023-121 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 50 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Tie 69 kV Substation | DISIS STAGE
GEN-2023-122 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Wolf Creek - LaCygne 345 kV Line | DISIS STAGE
GEN-2023-149 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 300 | 0 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 ftlo: P23:345:KCPL:WGARDNER-R10-12:::EHV: | ER/NR | KCPL | LaCygne - Stilwell 345 kV Line | DISIS STAGE
GEN-2023-157 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | KCPL | Bucyrus 161 kV Substation | DISIS STAGE
GEN-2023-163 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 150 | 0 | 541251 MARYVLE5 161 635034 CLRNDA 5 161 1 ,System Intact | ER/NR | KCPL | Midway - Avenue City 161 kV | DISIS STAGE
GEN-2023-169 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 125 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | KCPL | Missouri City - Liberty South 161 kV Line | DISIS STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | Voltage: 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | ER | KCPL | Salisbury 161 kV Substation | DISIS STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 ftlo: 300069 5CHOTEAU1 161 301348 5CHOTEAU2 161 Z1 | ER/NR | INDN | Sub M 161 kV Substation | DISIS STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Holcomb 345 kV | DISIS STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Holcomb 345 kV | DISIS STAGE
GEN-2023-175 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | SUNC | Hickock 115 kV Substation | DISIS STAGE
GEN-2023-186 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Solar/Storage | 200 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2023-191 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 74 | 0 | 509771 LLAN ET4 138 509790 CATOOSA4 138 1 ,System Intact | ER/NR | EMDE | Hockersville 138 kV Substation | DISIS STAGE
GEN-2023-194 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 225 | 0 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 ftlo: P12:345:WERE:N345-AECI-345:::EHV: | ER/NR | EMDE | Riverton - Neosho 161 kV Line Tap | DISIS STAGE
GEN-2023-200 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | 0 | Non-Converge: 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | ER/NR | WERE | Caney River 345 kV Substation | DISIS STAGE
GEN-2023-219 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 125 | 0 | Non-Converge: 533304 LANG 3 115 767120 G22-007-TAP 115 1 | ER/NR | WERE | Reading - Osage Jct 115 kV Line | DISIS STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | 0 | Voltage: P12:345:OKGE:BKRBKR357_1:::: | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | DISIS STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | 0 | Voltage: P12:345:OKGE:BKRBKR357_1:::: | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | DISIS STAGE
GEN-2023-226 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 505492 SPRGFLD5 161 547479 LAR382 5 161 2 ftlo: 300045 7MORGAN 345 300949 7JASPER 345 1 | ER/NR | EMDE | La Russell 161 kV Substation | DISIS STAGE
GEN-2023-231 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Wind/Storage (studied as Solar/Storage) | 310 | 0 | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 ftlo: 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | ER | WERE | Neosho - LaCynge 345 kV Line | DISIS STAGE
GEN-2023-003 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 200.6 | 116.38 | 505490 CARTHG 2 69.0 998101 CRG X1 69.0 1 | ER/NR | SWPA | Greasy Creek 138kV Switchyard | DISIS STAGE
GEN-2023-009 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 250 | 250 | None | ER/NR | WFEC | Hugo 138 kV Substation | DISIS STAGE
GEN-2023-016 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 130 | 45.3226 | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | ER/NR | SWPA | Tupelo-Brown 138 kV Line | DISIS STAGE
GEN-2023-019 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 200 | 200 | None | ER/NR | WFEC | Cherry Road 138 kV Substation | DISIS STAGE
GEN-2023-020 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 220 | 220 | None | ER/NR | WFEC | Russett-S Brown 138 kV | DISIS STAGE
GEN-2023-022 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 250 | 250 | None | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2023-027 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Battery | 150 | 150 | None | ER/NR | AEPW | Bird Hollow (Langley) - Pryor Junction 138 kV Line | DISIS STAGE
GEN-2023-028 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Battery | 230 | 230 | None | ER/NR | GRDA | Dry Gulch - Pensacola 161 kV Line | DISIS STAGE
GEN-2023-029 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 50 | 50 | None | ER/NR | AEPW | Adair - Pryor 69 kV Line | DISIS STAGE
GEN-2023-030 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 25 | 25 | None | ER/NR | AEPW | Tap between 345 kV SW Shreveport to Dolet Hills Substations | DISIS STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | 200 | None | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | DISIS STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | 200 | None | ER/NR | OKGE | Lula 138 kV Substation | DISIS STAGE
GEN-2023-049 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | 150 | None | ER/NR | GRDA | Dry Gulch - Pensacola 161 kV Line | DISIS STAGE
GEN-2023-051 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | 150 | None | ER/NR | AEPW | Red Rock Road - Weatherford Junction 138 kV Line | DISIS STAGE
GEN-2023-053 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 212 | 212 | None | ER/NR | AEPW | Pittsburg - Valiant 345kV line | DISIS STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 100 | 100 | None | ER/NR | GRDA | Kerr Grove 161 kV | DISIS STAGE
GEN-2023-056 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | 65.1858 | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | ER/NR | SWPA | Van Buren 161 kV | DISIS STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | 150 | None | ER/NR | GRDA | Pawnee Switch 138 kV | DISIS STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/RECIP Gas | 200 | 200 | None | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | DISIS STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 200 | 115.3453 | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | DISIS STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | 100 | None | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | DISIS STAGE
GEN-2023-070 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 50 | 50 | None | ER/NR | AEPW | Lane - McGee Creek Tap 69 kV | DISIS STAGE
GEN-2023-072 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 250 | 0 | Non-Converged: 520886 DUSTIN 4 138 520932 HANNA 4 138 1 | ER/NR | WFEC | McAlister 138 kV Substation | DISIS STAGE
GEN-2023-075 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 200 | 200 | None | ER/NR | WERE | Delaware to Neosho 345 kV | DISIS STAGE
GEN-2023-076 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 100 | 100 | None | ER/NR | WERE | Delaware - Neosho 345 kV | DISIS STAGE
GEN-2023-080 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 200 | 200 | None | ER/NR | AEPW | Lydia - Northwest Texarkana 345 kV | DISIS STAGE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | 117 | None | ER/NR | WFEC | Pharaoh 138 kV Substation | DISIS STAGE
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 125 | 125 | None | ER/NR | WFEC | Unger - Frogville 138 kV line | DISIS STAGE
GEN-2023-100 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 300 | None | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2023-101 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | 150 | None | ER/NR | SPS | Tap Stateline Demarc - Wheeler 230 kV Line | DISIS STAGE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 475 | 475 | None | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2023-103 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 200 | 200 | None | ER/NR | AEPW | Northeastern 138 kV Substation | DISIS STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | 100 | None | ER/NR | WFEC | Mooreland - Noel 138 kV Line | DISIS STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | 132.698 | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | ER/NR | SWPA | Jonesboro - Independence 161 kV | DISIS STAGE
GEN-2023-134 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 252 | 252 | None | ER/NR | AEPW | Fixico Tap to Weleetka 138 kV Line | DISIS STAGE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | 52 | None | ER/NR | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2023-136 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | 150 | None | ER/NR | AEPW | Vinita Junction - Hockerville 138 kV | DISIS STAGE
GEN-2023-137 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | 150 | None | ER/NR | AEPW | North Boston - Bann 138 kV Line Tap | DISIS STAGE
GEN-2023-138 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 250 | 250 | None | ER/NR | GRDA | GRDA1 - Tonece7 345 kV Line | DISIS STAGE
GEN-2023-145 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | 96 | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 | ER/NR | SWPA | Eufaula - Gore 161 kV Line | DISIS STAGE
GEN-2023-148 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 110 | 92.4942 | 512111 LAKEP2WT 69.0 520896 ELDORDO2 69.0 1 | ER/NR | AEPW | Russell - Lake Pauline 138 kV Line | DISIS STAGE
GEN-2023-150 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | 150 | None | ER/NR | OKGE | Gracemont 138 kV Substation | DISIS STAGE
GEN-2023-151 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | 100 | None | ER/NR | AEPW | South Nashville - South Murfreesboro 138kV | DISIS STAGE
GEN-2023-152 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 140 | 140 | None | ER/NR | AEPW | Allen NG4 138 kV Substation | DISIS STAGE
GEN-2023-155 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | 200 | None | ER/NR | AEPW | Longwood - Lieberman 138 kV | DISIS STAGE
GEN-2023-156 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 200 | 200 | None | ER/NR | WFEC | Between South Wilson - Ringling 138 kV Line | DISIS STAGE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 74.9 | 74.9 | None | ER/NR | OKGE | Roman Nose 138 kV Substation | DISIS STAGE
GEN-2023-162 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | 100 | None | ER/NR | AEPW | Grove - Jay 138 kV Line | DISIS STAGE
GEN-2023-164 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 210 | 210 | None | ER/NR | OKGE | Gracemont 345 kV Substation | DISIS STAGE
GEN-2023-165 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 210 | 210 | None | ER/NR | OKGE | Gracemont 345 kV Substation | DISIS STAGE
GEN-2023-166 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | ER | OKGE | 84th Street - Tennessee Tap 138 kV Line | DISIS STAGE
GEN-2023-167 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 250 | 250 | None | ER/NR | OKGE | Washington Park 138 kV Substation | DISIS STAGE
GEN-2023-168 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 175 | 175 | None | ER/NR | OKGE | Classen 138 kV Substation | DISIS STAGE
GEN-2023-174 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | ER | WFEC | Paoli West 138 kV Substation | DISIS STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | 200 | None | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | DISIS STAGE
GEN-2023-180 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | 150 | None | ER/NR | AEPW | Hackett - N Huntington 161 kV Line Tap | DISIS STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 175 | 175 | None | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | DISIS STAGE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 953 | 953 | None | ER/NR | AEPW | Welsh-Lydia 345kV Line | DISIS STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | 180 | None | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | DISIS STAGE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 50 | 50 | None | ER/NR | OKGE | Battlefield BESS 161 kV Substation | DISIS STAGE
GEN-2023-207 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 50 | 50 | None | ER | WFEC | Colbert 138 kV Substation | DISIS STAGE
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | 191 | None | ER/NR | WFEC | Prague - Chernicky 138 kV Line | DISIS STAGE
GEN-2023-211 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Battery/Wind | 250 | 0 | Non-Converged: P42:345:OKGE:SB_RARD7383:::: | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2023-212 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 400 | 400 | None | ER/NR | AEPW | Northwest Texarkana - Valliant 345 kV Line | DISIS STAGE
GEN-2023-213 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 100 | 100 | None | ER/NR | AEPW | Chamber Springs 161 kV Substation | DISIS STAGE
GEN-2023-214 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 100 | 100 | None | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2023-227 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 200 | 200 | None | ER/NR | AEP | Petty to Chapel 138 kV Line | DISIS STAGE
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | 230 | None | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | DISIS STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | 150 | None | ER/NR | AEPW | Red Pointe 138 kV Substation | DISIS STAGE
GEN-2023-235 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 250 | 250 | None | ER/NR | AEPW | Chamber Springs 345 kV Substation | DISIS STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | 93 | None | ER | AEPW | Winnsboro 138 kV Substation | DISIS STAGE
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | 0 | Non-Converged; 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | ER/NR | SPS | Chevron Eddy 115 kV | DISIS STAGE
GEN-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 230 | 0 | Non-Converged; 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | ER/NR | SPS | T14 Circuit 115 V Line | DISIS STAGE
GEN-2023-005 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 256 | 256 | None | ER/NR | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2023-008 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 75 | 75 | None | ER/NR | SPS | Tuco - Carlisle 230 kV line | DISIS STAGE
GEN-2023-010 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 280 | 280 | None | ER/NR | SPS | Moore Co 230 kV Substation | DISIS STAGE
GEN-2023-060 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 256 | 256 | None | ER/NR | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2023-081 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 625 | 0 | Non-Converged; 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | ER/NR | SPS | Crossroads - Hobbs 345 kV Line | DISIS STAGE
GEN-2023-086 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 300 | None | ER/NR | SPS | Potter - Newhart 230 kV line | DISIS STAGE
GEN-2023-109 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 65 | 65 | None | ER/NR | SPS | Dumas and 19th Street 115 kV Substation | DISIS STAGE
GEN-2023-110 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 250 | 250 | None | ER/NR | SPS | Tap Border to Tuco 345 kV Line | DISIS STAGE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | 130 | None | ER/NR | SPS | Kress 115 kV Substation | DISIS STAGE
GEN-2023-123 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 285 | 285 | None | ER/NR | SPS | Pringle Interchange 230 kV Substation | DISIS STAGE
GEN-2023-124 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 200 | 200 | None | ER/NR | SPS | Spearman Interchange 115 kV Substation | DISIS STAGE
GEN-2023-142 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 275 | 275 | None | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2023-143 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 200 | 200 | None | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2023-158 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 335 | 0 | Non-Converged; 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | ER/NR | SPS | Needmore - Yoakum 230 kV Line | DISIS STAGE
GEN-2023-159 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | Non-Converged; 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | ER/NR | SPS | Needmore - Yoakum 230 kV Line | DISIS STAGE
GEN-2023-176 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 300 | 300 | None | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2023-178 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 200 | 200 | None | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2023-183 | 05 SOUTHWEST | 25 | DIS-23-1 | Thermal | 217 | 217 | None | ER/NR | SPS | Tuco 345kV | DISIS STAGE
GEN-2023-184 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 200 | 0 | Non-Converged; 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | ER/NR | SPS | Phantom 115 kV Substation | DISIS STAGE
GEN-2023-185 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 150 | 150 | None | ER/NR | SPS | Nichols - Amarillo 230 kV line tap | DISIS STAGE
GEN-2023-188 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 160 | 160 | None | ER/NR | AEPW | Oklaunion - Lawton 345 kV Line | DISIS STAGE
GEN-2023-195 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 250 | 250 | None | ER/NR | SPS | Roosevelt - Tolk 230 kV line tap | DISIS STAGE
GEN-2023-196 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 150 | 150 | None | ER/NR | SPS | Roosevelt - Tolk 230 kV line tap | DISIS STAGE
GEN-2023-201 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 0 | Non-Converged; 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | ER/NR | SPS | Crossroads - Hobbs 345 kV Line | DISIS STAGE
GEN-2023-203 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 0 | Non-Converged; 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | ER/NR | SPS | Hobbs - Ink Basin 230 kV Transmission Line | DISIS STAGE
GEN-2023-208 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 200 | 200 | None | ER | SPS | Rolling Hills 115 kV | DISIS STAGE
GEN-2023-209 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 125 | 125 | None | ER/NR | SPS | Amarillo South 115 kV | DISIS STAGE
GEN-2023-228 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 250 | 250 | None | ER/NR | SPS | Tuco-Okalunion 345 kV line | DISIS STAGE
GEN-2023-236 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 400 | 0 | Non-Converged; 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | ER/NR | SPS | Hobbs - Yoakum 345 kV | DISIS STAGE
GEN-2023-237 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 500 | 500 | None | ER/NR | SPS | Crawfish Draw 345 kV Substation | DISIS STAGE
GEN-2023-238 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 280 | 280 | None | ER/NR | SPS | Potter County 345 kV Substation | DISIS STAGE
GEN-2023-239 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 300 | 300 | None | ER/NR | SPS | Rolling Hills 230 kV Substation | DISIS STAGE
GEN-2023-240 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 550 | 550 | None | ER/NR | SPS | Tolk 345 kV Substation | DISIS STAGE
GEN-2023-074 | WECC | 25 | DIS-23-1 | Hybrid; Solar/Storage | 85 | 0 | Non-Converged | ER/NR | WAPA-WECC | Custer to Rosebud Creek 230 kV Line Tap | DISIS STAGE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | - | - | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | - | - | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-068 | 01 NORTH | 24 | DIS-22-1 | Wind | 250 | - | - | ER/NR | BEPC | Chappelle Creek 345 kV | DISIS STAGE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | - | - | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-219 | 01 NORTH | 24 | DIS-22-1 | Solar | 350 | - | - | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2022-077 | 02 NEBRASKA | 24 | DIS-22-1 | Solar | 255 | - | - | ER/NR | NPPD | Enders 115 kV Substation | DISIS STAGE
GEN-2022-152 | 02 NEBRASKA | 24 | DIS-22-1 | Battery/Storage | 80 | - | - | ER/NR | NPPD | Humboldt 161 kV Substation | DISIS STAGE
GEN-2022-162 | 02 NEBRASKA | 24 | DIS-22-1 | Wind | 118 | - | - | ER/NR | NPPD | Friend 115 kV Substation | DISIS STAGE
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | - | - | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2022-005 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | WERE | Northeast Parsons 138kV Substation | DISIS STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | WERE | Neosho - N345 161 kV Substation | DISIS STAGE
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | - | - | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | DISIS STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | - | - | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | - | - | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | DISIS STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2022-025 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | SUNC | Tap of Mingo--Red Willow 345kV line | DISIS STAGE
GEN-2022-026 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | SUNC | Tap of Mingo--Red Willow 345kV line | DISIS STAGE
GEN-2022-041 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 100 | - | - | ER/NR | WERE | Tie Substation 69 kV | DISIS STAGE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Tap | DISIS STAGE
GEN-2022-058 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 180 | - | - | ER/NR | EDE | Sibley 161 kV substation on the Noel Southwest - Decatur 161 kV line | DISIS STAGE
GEN-2022-062 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | WERE | Wolf Creek- Blackberry 345 kV | DISIS STAGE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | - | - | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | DISIS STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | - | - | ER/NR | KCPL | Nashua 161 kV Substation | DISIS STAGE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | - | - | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | DISIS STAGE
GEN-2022-076 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 500 | - | - | ER/NR | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2022-079 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 192 | - | - | ER | EDE | Dadeville East - Bolivar South 161kV | DISIS STAGE
GEN-2022-080 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 96 | - | - | ER | EDE | Dadeville East - Bolivar South 161kV | DISIS STAGE
GEN-2022-081 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 218 | - | - | ER/NR | SUNC | Clifton 115kV Substation | DISIS STAGE
GEN-2022-094 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 250 | - | - | ER | MIDW | Postrock to Axtell 345 kV line | DISIS STAGE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Hybrid | 80 | - | - | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | DISIS STAGE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | - | - | ER/NR | KCPL | Liberty West 161 kV | DISIS STAGE
GEN-2022-103 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 74.99 | - | - | ER/NR | EDE | Ozark South 161kV | DISIS STAGE
GEN-2022-113 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | EDE | Tipton Station 161 kV Substation | DISIS STAGE
GEN-2022-131 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | KCPL | Warrensburg East - Odessa161kV Substation | DISIS STAGE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | KCPL | Shoal Creek 161 kV Substation | DISIS STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | KCPL | Blue Mills BESS 161kV Substation | DISIS STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 400 | - | - | ER | WERE | Burns 345kV Substation | DISIS STAGE
GEN-2022-168 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 380 | - | - | ER/NR | KCPL | Silwell - Clinton 161 kV Line | DISIS STAGE
GEN-2022-186 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 684 | - | - | ER/NR | WERE | Wolf Creek - Benton 345 kV Substation | DISIS STAGE
GEN-2022-204 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 250 | - | - | ER/NR | SUNC | Post Rock - Spearville 345 kV | DISIS STAGE
GEN-2022-205 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 250 | - | - | ER/NR | SUNC | Post Rock - Spearville 345 kV | DISIS STAGE
GEN-2022-206 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 250 | - | - | ER/NR | SUNC | Post Rock - Spearville 345 kV | DISIS STAGE
GEN-2022-208 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 400 | - | - | ER/NR | KCPL | Tap on the Mullen Creek to Ketchum 345 kV Line | DISIS STAGE
GEN-2022-209 | 03 CENTRAL | 24 | DIS-22-1 | Hybrid | 600 | - | - | ER/NR | KCPL | Tap on the Mullen Creek to Ketchum 345 kV Line | DISIS STAGE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | - | - | ER | WERE | Gill - Viola 138 kV Line Break | DISIS STAGE
GEN-2022-001 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | - | - | ER/NR | AEP | Catoosa 138 kV Substation | DISIS STAGE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | - | - | ER/NR | OGE | Woodward 345 kV Substation | DISIS STAGE
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | - | - | ER/NR | OGE | Woodward 345kV Substation | DISIS STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | - | - | ER/NR | OGE | Woodward 345kV Substation | DISIS STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | AEP | Longwood to Scottville 138 kV line | DISIS STAGE
GEN-2022-042 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 174 | - | - | ER/NR | OGE | Sunnyside to Pooleville 138 kV line | DISIS STAGE
GEN-2022-048 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 250 | - | - | ER/NR | WFEC | Mooreland 138 kV | DISIS STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | WFEC | Sunshine North to Anadarko 138 kV | DISIS STAGE
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | - | - | ER/NR | AEP | Talawanda to Canadian River 138 kV Line Tap | DISIS STAGE
GEN-2022-072 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 181 | - | - | ER/NR | GRDA | Grand River Dam - Claremore 161 kV Line | DISIS STAGE
GEN-2022-074 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 220.86 | - | - | ER/NR | WFEC | Hanna 138kV Substation | DISIS STAGE
GEN-2022-085 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 241.4 | - | - | ER/NR | OGE | Seminole to Muskogee 345kV Substation | DISIS STAGE
GEN-2022-088 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 74.99 | - | - | ER/NR | AEP | South Foreman 138 kV Substation | DISIS STAGE
GEN-2022-089 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 74.99 | - | - | ER/NR | AEP | South Foreman 138 kV Substation | DISIS STAGE
GEN-2022-090 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | - | - | ER/NR | AEP | Valiant Substation 138kV | DISIS STAGE
GEN-2022-091 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | - | - | ER/NR | AEP | Valiant Substation 138kV | DISIS STAGE
GEN-2022-092 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 299.2 | - | - | ER/NR | AEP | Neosho-Delaware 345 kV | DISIS STAGE
GEN-2022-093 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 83 | - | - | ER/NR | AEP | Turk - Hope 115 kV line | DISIS STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | OGE | Bison 345kV Substation | DISIS STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | - | - | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | DISIS STAGE
GEN-2022-108 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 100 | - | - | ER/NR | AEP | Tap between 345kV SW Shreveport to Dolet Hills Substations | DISIS STAGE
GEN-2022-110 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | - | - | ER/NR | AEP | Lehigh 138kV Station | DISIS STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Hybrid | 150 | - | - | ER/NR | AEP | Wilkes 345 kV Substation | DISIS STAGE
GEN-2022-129 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | AEP | Webb City Tap - Shidler 138 kV line | DISIS STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | OGE | Battlefield BESS 161kV | DISIS STAGE
GEN-2022-132 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | - | - | ER/NR | WFEC | Anadarko 138kV Substation | DISIS STAGE
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | WFEC | Colbert 138 kV Substation | DISIS STAGE
GEN-2022-137 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | WFEC | Canadian Switchyard 138kV | DISIS STAGE
GEN-2022-138 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | - | - | ER/NR | AEP | Tulsa North - Northeast Station 345 kV Substation | DISIS STAGE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | - | - | ER/NR | AEP | Pirkey 345kV Substation | DISIS STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | OGE | Caney Creek 138 kV Substation | DISIS STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 195 | - | - | ER | AEP | Weatherford Jct. to Hinton 138 kV line | DISIS STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | - | - | ER | WFEC | Canadian Switch 138 kV Substation | DISIS STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER | OGE | Horseshoe Lake 138 kV Substation | DISIS STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | - | - | ER | GRDA | Silver City 138 kV Substation | DISIS STAGE
GEN-2022-163 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | OGE | Cimarron 345kV Substation | DISIS STAGE
GEN-2022-167 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 250 | - | - | ER/NR | AEP | Tulsa North - Northeastern 345 kV Line | DISIS STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | - | - | ER/NR | AEP | Northeastern - Delaware 345 kV transmission line | DISIS STAGE
GEN-2022-196 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | - | - | ER | AEP | Pittsburg 345kV Substation | DISIS STAGE
GEN-2022-218 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 95 | - | - | ER/NR | SWPA | Highland (Ash Flat) - Water Valley 161 kV Substation | DISIS STAGE
GEN-2022-231 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 166 | - | - | ER/NR | OGE | Crescent to Cottonwood Creek 138 kV Line | DISIS STAGE
GEN-2022-234 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | - | - | ER/NR | AEP | Alluwe Tap â€“ Chelsea 138 kV line | DISIS STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | - | - | ER/NR | WFEC | El Reno SW 138 kV | DISIS STAGE
GEN-2022-237 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | - | - | ER/NR | OGE | Maud 138 kV substation | DISIS STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | - | - | ER/NR | OGE | Maud 138 kV substation | DISIS STAGE
GEN-2022-239 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 350 | - | - | ER/NR | AEP | John W Turk Jr Power Plant 345 kV sub | DISIS STAGE
GEN-2022-240 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | AEP | John W Turk Jr Power Plant 345 kV sub | DISIS STAGE
GEN-2022-241 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | - | - | ER/NR | AEP | John W Turk Jr Power Plant 345 kV sub | DISIS STAGE
GEN-2022-011 | 05 SOUTHWEST | 24 | DIS-22-1 | Solar | 374 | - | - | ER/NR | AEP | Tap of Oklaunion - Lawton Eastside 345 kV line | DISIS STAGE
GEN-2022-019 | 05 SOUTHWEST | 24 | DIS-22-1 | Battery/Storage | 100 | - | - | ER/NR | AEP | Tap of Oklaunion - Lawton Eastside 345 kV line | DISIS STAGE
GEN-2022-021 | 05 SOUTHWEST | 24 | DIS-22-1 | Battery/Storage | 100 | - | - | ER/NR | AEP | Tap of Oklaunion - Lawton Eastside 345 kV line | DISIS STAGE
GEN-2022-082 | 05 SOUTHWEST | 24 | DIS-22-1 | Solar | 180 | - | - | ER/NR | SPS | Tuco - Carlisle 230 kV line | DISIS STAGE
GEN-2022-105 | 05 SOUTHWEST | 24 | DIS-22-1 | Solar | 300 | - | - | ER/NR | AEP | Tap of Oklaunion to Lawton Eastside 345 kV Transmission Line | DISIS STAGE
GEN-2022-106 | 05 SOUTHWEST | 24 | DIS-22-1 | Solar | 300 | - | - | ER/NR | AEP | Tap of Oklaunion to Lawton Eastside 345 kV Transmission Line | DISIS STAGE
GEN-2022-107 | 05 SOUTHWEST | 24 | DIS-22-1 | Solar | 400 | - | - | ER/NR | AEP | Tap of Oklaunion to Lawton Eastside 345 kV Transmission Line | DISIS STAGE
GEN-2022-109 | 05 SOUTHWEST | 24 | DIS-22-1 | Solar | 150 | - | - | ER/NR | SPS | Hobbs - Yoakum 345 kV transmission line | DISIS STAGE
GEN-2022-114 | 05 SOUTHWEST | 24 | DIS-22-1 | Wind | 250 | - | - | ER/NR | AEP | Lawton to Oklaunion 345kV Line | DISIS STAGE
GEN-2022-128 | 05 SOUTHWEST | 24 | DIS-22-1 | Battery/Storage | 150 | - | - | ER/NR | SPS | Pecos Interchange 115 kV Substation | DISIS STAGE
GEN-2022-135 | 05 SOUTHWEST | 24 | DIS-22-1 | Battery/Storage | 150 | - | - | ER/NR | SPS | Taylor Switching Station 115kV | DISIS STAGE
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | - | - | ER | SPS | Tuco 345kV | DISIS STAGE
GEN-2022-150 | 05 SOUTHWEST | 24 | DIS-22-1 | Battery/Storage | 150 | - | - | ER/NR | SPS | Randall 115 kV Substation | DISIS STAGE
GEN-2022-159 | 05 SOUTHWEST | 24 | DIS-22-1 | Wind | 280 | - | - | ER/NR | SPS | Crossroads - Hobbs 345 kV Line | DISIS STAGE
GEN-2022-160 | 05 SOUTHWEST | 24 | DIS-22-1 | Wind | 280 | - | - | ER/NR | SPS | Crossroads - Hobbs 345 kV Line | DISIS STAGE
GEN-2022-171 | 05 SOUTHWEST | 24 | DIS-22-1 | Wind | 200 | - | - | ER | SPS | Pleasant Hill 230 kV Substation | DISIS STAGE
GEN-2021-008 | 01 NORTH | 23 | DIS-21-1 | Solar | 200 | - | - | ER/NR | BEPC | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND | DISIS STAGE
GEN-2021-024 | 01 NORTH | 23 | DIS-21-1 | Wind | 203.04 | - | - | ER | WAPA | WAPA 230kV Jamestown Substation | DISIS STAGE
GEN-2021-072 | 01 NORTH | 23 | DIS-21-1 | Solar | 600 | - | - | ER/NR | BEPC | 345kV Transmission Line from Antelope Valley to Leland Olds Substation | DISIS STAGE
GEN-2021-007 | 02 NEBRASKA | 23 | DIS-21-1 | Wind | 600 | - | - | ER/NR | NPPD | 345kV bus of Turtle Creek Substation | DISIS STAGE
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | - | - | ER | NPPD | Olive Creek 115 kV Substation | DISIS STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | - | - | ER | LES | Rokeby 115 kV Substation | DISIS STAGE
GEN-2021-037 | 02 NEBRASKA | 23 | DIS-21-1 | Wind | 244.22 | - | - | ER/NR | NPPD | NPPD Sidney to Keystone 345 kV Line | DISIS STAGE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | - | - | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | DISIS STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | - | - | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | DISIS STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | - | - | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | DISIS STAGE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | - | - | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 250 | - | - | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-057 | 02 NEBRASKA | 23 | DIS-21-1 | Wind | 300 | - | - | ER | NPPD | Antelope 345kV substation | DISIS STAGE
GEN-2021-073 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 240 | - | - | ER/NR | NPPD | Tap on the Sweetwater to Gerald Gentleman 345 kV Line | DISIS STAGE
GEN-2021-106 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | - | - | ER/NR | NPPD | Hebron North 115Kv substation | DISIS STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | - | - | ER/NR | OPPD | OPPD 345KV Cass County Substation | DISIS STAGE
GEN-2021-005 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 350 | - | - | ER/NR | WERE | Summit 345 kV substation in Saline County, KS | DISIS STAGE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | - | - | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | DISIS STAGE
GEN-2021-013 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 74.9 | - | - | ER/NR | MIDW | Smoky Hills Tap 230kV | DISIS STAGE
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | - | - | ER | SUNC | Elm Creek 345 kV interconnection substation | DISIS STAGE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | - | - | ER | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2021-023 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 306.18 | - | - | ER | WERE | Wild Plains 345kV Substation | DISIS STAGE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | - | - | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | - | - | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | - | - | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | DISIS STAGE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | - | - | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | DISIS STAGE
GEN-2021-050 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 200 | - | - | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-051 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 75 | - | - | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | - | - | ER | WERE | Viola 345kV Substation | DISIS STAGE
GEN-2021-061 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 100 | - | - | ER | WERE | Gordan Evans 138 kV Substation | DISIS STAGE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | - | - | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | - | - | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | - | - | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-076 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | - | - | ER/NR | MIDW | ITC Post Rock 345 kV Substation | DISIS STAGE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | - | - | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | DISIS STAGE
GEN-2021-085 | 03 CENTRAL | 23 | DIS-21-1 | Hybrid | 100 | - | - | ER/NR | SUNC | Crooked Creek - Fort Dodge 115kV | DISIS STAGE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | - | - | ER/NR | WERE | Wolf Creek - Benton 345 kV | DISIS STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | - | - | ER/NR | WERE | Evergy's Midland Substation 115kV bus | DISIS STAGE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | - | - | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | DISIS STAGE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | - | - | ER | WERE | Evergy 345kV Jeffrey Energy Center | DISIS STAGE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | - | - | ER/NR | OKGE | 138kV Brown Substation | DISIS STAGE
GEN-2021-002 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | - | - | ER/NR | WFEC | 138kV Okeene Switch Station | DISIS STAGE
GEN-2021-004 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 250 | - | - | ER/NR | OKGE | Poolville 138kV Bus | DISIS STAGE
GEN-2021-015 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 74.9 | - | - | ER | OKGE | Bobcat 345 kV interconnection substation | DISIS STAGE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | - | - | ER | AEPW | Sunnyside-Johnston 345 kV | DISIS STAGE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | - | - | ER | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | - | - | ER/NR | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | - | - | ER | WFEC | Western Farmers 138kV Mooreland Substation | DISIS STAGE
GEN-2021-028 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | - | - | ER | WFEC | Western Farmers 138kV Mooreland Substation | DISIS STAGE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | - | - | ER | OKGE | Grand Prairie 161kV Substation | DISIS STAGE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | - | - | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | DISIS STAGE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | - | - | ER/NR | AEPW | Welsh 345kV Substation | DISIS STAGE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | - | - | ER/NR | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | - | - | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | DISIS STAGE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | - | - | ER | OKGE | Pecan Creek 345kV substation | DISIS STAGE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | - | - | ER | OKGE | Pecan Creek 345 kV Substation | DISIS STAGE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 155 | - | - | ER/NR | AEPW | Craig JCT 138kV | DISIS STAGE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 100 | - | - | ER/NR | AEPW | Carnegie South 138kV | DISIS STAGE
GEN-2021-075 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 300 | - | - | ER/NR | AEPW | CAMPCOR4 138kV Substation | DISIS STAGE
GEN-2021-086 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 165 | - | - | ER/NR | AEPW | Okay - Turk 138kV | DISIS STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | - | - | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | DISIS STAGE
GEN-2021-098 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 160 | - | - | ER/NR | OKGE | Dewey District 138 kV Substation | DISIS STAGE
GEN-2021-104 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 100 | - | - | ER/NR | AEPW | 138kV bus at Red Point Substation | DISIS STAGE
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid | 50 | - | - | ER/NR | SPS |  | DISIS STAGE
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid | 40 | - | - | ER/NR | SPS |  | DISIS STAGE
GEN-2021-010 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 231 | - | - | ER | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-012 | 05 SOUTHWEST | 23 | DIS-21-1 | Battery/Storage | 225 | - | - | ER | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-014 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 231 | - | - | ER | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-083 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid | 50 | - | - | ER/NR | SPS | SPP / Central Valley Electric Cooperative (CV) 69 kV transmission line | DISIS STAGE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid | 400 | - | - | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
IR41 | 02 NEBRASKA | 22.5 | DIS-20-1-PQ | Solar | 50 | - | - | ER/NR | ALTW |  | SIP
IR42 | 02 NEBRASKA | 22.5 | DIS-20-1-PQ | Solar | 50 | - | - | ER/NR | ALTW |  | SIP
GIA-108 | 04 SOUTHEAST | 22.5 | DIS-20-1-PQ | Solar | 201.735 | - | - | ER/NR | AECI
GEN-2020-006 | 01 NORTH | 22 | DIS-20-1 | Solar | 250 | - | - | ER/NR | BEPC | Bowman 230kV substation | DISIS STAGE
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | - | - | ER/NR | BEPC | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-021 | 01 NORTH | 22 | DIS-20-1 | Wind | 235 | - | - | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | DISIS STAGE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid | 74.5 | - | - | ER/NR | WAPA | Fairview 115kV Substation | DISIS STAGE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | - | - | ER/NR | BEPC | Patent Gate Substation 345 kV | DISIS STAGE
GEN-2020-001 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 200 | - | - | ER/NR | BEPC | Sidney 345 kV Substation | DISIS STAGE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | - | - | ER | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 320 | - | - | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | DISIS STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 215 | - | - | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | DISIS STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | - | - | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-027 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 50 | - | - | ER | OPPD | S1281 â€“ S1362 161kV (S1363) | DISIS STAGE
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | - | - | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-030 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 50 | - | - | ER | OPPD | S1281 â€“ S1362 161kV (S1363) | DISIS STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 303 | - | - | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-033 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 50 | - | - | ER | OPPD | S1281 â€“ S1362 161kV (S1363) | DISIS STAGE
GEN-2020-036 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 303 | - | - | ER | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 303 | - | - | ER | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | - | - | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | - | - | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | - | - | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | - | - | ER/NR | NPPD | Cody to Valentine 115kV line | DISIS STAGE
GEN-2020-077 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 151.2 | - | - | ER | NPPD | North Hebron to Fairbury 115 kV | DISIS STAGE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | - | - | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | DISIS STAGE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | - | - | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | DISIS STAGE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | - | - | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | DISIS STAGE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 35 | - | - | ER | KCPL |  | DISIS STAGE
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 35 | - | - | ER | KCPL |  | DISIS STAGE
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | - | - | ER/NR | WERE | East Substation 69 kV | DISIS STAGE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 650 | - | - | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | DISIS STAGE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 250 | - | - | ER | SPS | Corporation Carpenter 345kV Substation | DISIS STAGE
GEN-2020-015 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 104 | - | - | ER/NR | OGE | Johnston County 345 kV Substation | DISIS STAGE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | - | - | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | - | - | ER/NR | KCPL | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | - | - | ER/NR | KCPL | Evergy Atlantic 345kV Substation | DISIS STAGE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | - | - | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | DISIS STAGE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | - | - | ER/NR | EDE | 4544 Stateline CC 161kV Substation | DISIS STAGE
GEN-2020-070 | 03 CENTRAL | 22 | DIS-20-1 | Wind | 255 | - | - | ER | MIDW | Postrock to Axtell 345 KV line | DISIS STAGE
GEN-2020-071 | 03 CENTRAL | 22 | DIS-20-1 | Wind | 252 | - | - | ER | WERE | Swissvale to Morris 230 KV line | DISIS STAGE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 150 | - | - | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | DISIS STAGE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 150 | - | - | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | DISIS STAGE
GEN-2020-076 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 200 | - | - | ER/NR | WERE | Benton to Wolf Creek 345 kV Line | DISIS STAGE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 225 | - | - | ER/NR | EDE | Riverton-Neosho 161kV line | DISIS STAGE
GEN-2020-086 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 500 | - | - | ER/NR | WERE | Benton to Wolf Creek 345 kV Line | DISIS STAGE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | - | - | ER/NR | EDE | La Russell 161 kV Substation | DISIS STAGE
GEN-2020-089 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 104 | - | - | ER/NR | KCPL | Dakota 161 kV Substation | DISIS STAGE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 204.3 | - | - | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | DISIS STAGE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid | 140 | - | - | ER/NR | WFEC | Seiling-Taloga Substations 138kV | DISIS STAGE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid | 113 | - | - | ER/NR | AEPW | Snyder â€“ Altus Jct. 138kV | DISIS STAGE
GEN-2020-016 | 04 SOUTHEAST | 22 | DIS-20-1 | Wind | 202 | - | - | ER/NR | WFEC | Snyder SW-Cache 138 kV line | DISIS STAGE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid | 201.6 | - | - | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | DISIS STAGE
GEN-2020-023 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 202 | - | - | ER/NR | OGE | Woodring 345 KV Station | DISIS STAGE
GEN-2020-052 | 04 SOUTHEAST | 22 | DIS-20-1 | Wind | 251 | - | - | ER/NR | WERE | Neosho-Delaware 345 kV | DISIS STAGE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | - | - | ER/NR | AEPW | Lydia 345 kV Station | DISIS STAGE
GEN-2020-074 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | - | - | ER/NR | AEPW | Lawton to Sunnyside 345 kV Substation | DISIS STAGE
GEN-2020-075 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | - | - | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | - | - | ER/NR | AEPW | Tenaska Switching Substation 345kV | DISIS STAGE
GEN-2020-085 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | - | - | ER/NR | AEPW | Lawton to Sunnyside 345 kV Line | DISIS STAGE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | - | - | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | - | - | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | DISIS STAGE
GEN-2020-009 | 05 SOUTHWEST | 22 | DIS-20-1 | Hybrid | 300 | - | - | ER/NR | AEPW | Lawton East Side to Oklaunion 345kV | DISIS STAGE
GEN-2020-017 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 74.88 | - | - | ER/NR | SPS | 230kV Lamb County Interchange | DISIS STAGE
GEN-2020-059 | 05 SOUTHWEST | 22 | DIS-20-1 | Hybrid | 250 | - | - | ER | SPS | Tuco-Yoakum-Hobbs 345 kV | DISIS STAGE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | - | - | ER | SPS | Lubbock East Substation 230 kV | DISIS STAGE
GEN-2020-062 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 256 | - | - | ER | SPS | OASIS 230kV Substation | DISIS STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | - | - | ER | SPS | Hobbs-Andrews 345 kV Line | DISIS STAGE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | - | - | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2020-068 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 400 | - | - | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GIA-106 | 03 CENTRAL | 21.5 | DIS-19-1 PQ | Solar | 118.696 | - | - | ER/NR | AECI
GIA-107 | 03 CENTRAL | 21.5 | DIS-19-1 PQ | Solar | 125 | - | - | ER/NR | AECI
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | - | - | ER | BEPC-SPP | 115kV Strandahl sub | DISIS STAGE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | - | - | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | - | - | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal | 15.15 | - | - | ER/NR | BEPC-SPP | Siouxland 69kV | DISIS STAGE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Hybrid | 110 | - | - | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | - | - | ER/NR | BEPC-SPP | Leland Olds 345kV substation | DISIS STAGE
GEN-2018-065 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 19.8 | - | - | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-068 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 302.4 | - | - | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 250 | - | - | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | - | - | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | - | - | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | - | - | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | - | - | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | - | - | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | - | - | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-069 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | - | - | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 50 | - | - | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | - | - | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2018-063 | 03 CENTRAL | 21 | DIS-18-2 | Solar | 57 | - | - | ER | EMDE | Sedalia Marshfield Springfield Nichols Street 69kV circuit | DISIS STAGE
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | - | - | ER | SUNC | Thistle 345kV substation | DISIS STAGE
GEN-2018-116 | 03 CENTRAL | 21 | DIS-18-2 | Solar | 150 | - | - | ER/NR | SUNC | Frey Street 115kV bus | DISIS STAGE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | - | - | ER/NR | WERE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | - | - | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal | 15.56 | - | - | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | - | - | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-035 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 80 | - | - | ER/NR | EMDE | Reeds Spring-Aurora 161kV Line | DISIS STAGE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | - | - | ER | SUNC | North Fort Dodge 115kV Substation | DISIS STAGE
GEN-2019-048 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | - | - | ER | KCPL | Duncan 69kV substation | DISIS STAGE
GEN-2019-051 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 40 | - | - | ER/NR | SUNC | Frey St 115kV bus | DISIS STAGE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | - | - | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | - | - | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | - | - | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | - | - | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | - | - | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | - | - | ER/NR | SUNC | Great Bend - Circle 230kV line | DISIS STAGE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | - | - | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | - | - | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | - | - | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | - | - | ER | AEPW | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | - | - | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-088 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 130 | - | - | ER | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | - | - | ER | AEPW | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid | 250 | - | - | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | - | - | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 200 | - | - | ER/NR | OKGE | Woodward 345kV substation | DISIS STAGE
GEN-2019-013 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 50 | - | - | ER/NR | AEPW | Dempsey 230kV sub/Sweetwater 230kV | DISIS STAGE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | - | - | ER | OKGE | DeGrasse 138kV Substation | DISIS STAGE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | - | - | ER | AEPW | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | - | - | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | - | - | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | - | - | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | - | - | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | - | - | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
MPC04300 | 01 NORTH | 20.5 | DIS-18-2-PQ | Wind | 200 | - | - | ER/NR | OTP
GIA-100 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 40 | - | - | ER/NR | AECI
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 460 | - | - | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 75 | - | - | ER/NR | AECI
GIA-99 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 470 | - | - | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | - | - | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | - | - | ER/NR | AECI
GIA-105 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | - | - | ER/NR | AECI
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | - | - | ER | WAPA |  | DISIS STAGE
GEN-2018-008 | 01 NORTH | 20 | DIS-18-1 | Wind | 252 | - | - | ER/NR | BEPC-SPP | Groton-Leland Olds 345kV Line | DISIS STAGE
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery/Storage | 74.1 | - | - | ER/NR | BEPC-SPP | Neset 230kV Substation | DISIS STAGE
GEN-2018-039 | 01 NORTH | 20 | DIS-18-1 | Solar | 72 | - | - | ER/NR | WAPA | Edgeley 115kV substation | DISIS STAGE
GEN-2018-012 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 74.1 | - | - | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | - | - | ER | OPPD | Fort Calhoun 345kV Substation
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | - | - | ER | OPPD | Cass County 345kV Substation
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | - | - | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | - | - | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break
GEN-2018-056 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 102.6 | - | - | ER/NR | WAPA | Grand Prairie 345kV | DISIS STAGE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | - | - | ER | KCPL |  | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | - | - | ER | KCPL |  | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | - | - | ER | KCPL |  | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | - | - | ER | KCPL |  | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | - | - | ER | KCPL |  | DISIS STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | - | - | ER | SUNC | Cimarron 115kV Substation | DISIS STAGE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | - | - | ER | WERE | Abilene Energy Center-Northview 115kV Line | DISIS STAGE
GEN-2018-022 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 300 | - | - | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | - | - | ER | KCPL | Blue Valley 161kV Substation | DISIS STAGE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | - | - | ER | WERE | Neosho 345kV Substation | DISIS STAGE
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | - | - | ER | SUNC | Thistle 345kV Substation | DISIS STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | - | - | ER/NR | WERE | Gordon Evans 138kV | DISIS STAGE
GEN-2018-060 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 50 | - | - | ER/NR | NPPD | Axtell-Post Rock 345 kV | DISIS STAGE
GEN-2018-062 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 75.6 | - | - | ER/NR | KACY | Nearman 161kV substation | DISIS STAGE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | - | - | ER/NR | AEPW | North Boston-Bann 138kV Line | DISIS STAGE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | - | - | ER/NR | WFEC | Dover 138 kV Switching Station | DISIS STAGE
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | - | - | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | DISIS STAGE
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | - | - | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | - | - | ER | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | - | - | ER | AEPW | Tulsa Power Station 138kV Substation | DISIS STAGE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | - | - | ER | AEPW | Tulsa North 138kV Substation | DISIS STAGE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | - | - | ER | OKGE | Horseshoe Lake 138kV Substation | DISIS STAGE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | - | - | ER | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | - | - | ER | AEPW | Longwood 345kV Substation | DISIS STAGE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | - | - | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | DISIS STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | - | - | ER | SPS | T14 Circuit 115kV line
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | - | - | ER/NR | SPS | Tuco-Oklaunion 345kV Line
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | - | - | ER | SPS | Roadrunner 115kV Substation | DISIS STAGE
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | - | - | ER/NR | MDU |  | IA PENDING
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery | 20 | - | - | ER/NR | XEL |  | IA PENDING
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | XEL |  | IA PENDING
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | IA PENDING
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | IA PENDING
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | - | - | ER | ALTW |  | IA PENDING
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER | XEL |  | IA PENDING
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | GRE |  | IA PENDING
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | XEL |  | IA PENDING
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | DPC |  | IA PENDING
J1325 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | ALTW |  | IA PENDING
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | IA PENDING
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | IA PENDING
J1474 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | XEL |  | IA PENDING
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 125 | - | - | ER | OTP |  | IA PENDING
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | ALTW |  | Not Started
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | ALTW |  | Not Started
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | Not Started
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER/NR | ALTW |  | Not Started
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | XEL |  | Not Started
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | - | - | ER/NR | OTP |  | Not Started
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | Not Started
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | Not Started
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | Not Started
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 60 | - | - | ER/NR | XEL |  | Not Started
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 62.5 | - | - | ER/NR | XEL |  | Not Started
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | Not Started
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | - | - | ER/NR | XEL |  | Not Started
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 80 | - | - | ER/NR | DPC |  | Not Started
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 148 | - | - | ER/NR | DPC |  | Not Started
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | - | - | ER/NR | XEL |  | Not Started
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | - | - | ER/NR | XEL |  | IA PENDING
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER | OTP |  | DISIS STAGE
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER | OTP |  | DISIS STAGE
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | - | - | ER/NR | OTP |  | DISIS STAGE
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 151.2 | - | - | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | - | - | ER/NR | OTP
IR39 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 12.5 | - | - | ER/NR | ALTW
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | - | - | ER/NR | ALTW |  | IA PENDING
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | ALTW |  | IA PENDING
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | - | - | ER/NR | ALTW |  | IA PENDING
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | - | - | ER | ALTW |  | IA PENDING
J1181 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | - | - | ER/NR | ALTW |  | IA PENDING
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | - | - | ER/NR | MEC |  | IA PENDING
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | ALTW |  | IA PENDING
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 47.5 | - | - | ER/NR | ALTW |  | IA PENDING
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | - | - | ER/NR | ALTW |  | IA PENDING
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | ALTW |  | IA PENDING
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | - | - | ER/NR | ALTW |  | Not Started
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | MEC |  | Not Started
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | MEC |  | Not Started
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | MEC |  | Not Started
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 100 | - | - | ER/NR | MEC |  | Not Started
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | - | - | ER | MEC |  | IA PENDING
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 290 | - | - | ER/NR | AMMO |  | IA PENDING
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 380 | - | - | ER/NR | AMMO |  | IA PENDING
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | - | - | ER/NR | AMMO |  | IA PENDING
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | - | - | ER/NR | AMMO |  | IA PENDING
J1191 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 64 | - | - | ER/NR | CWLD |  | IA PENDING
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 68.4 | - | - | ER/NR | AMIL |  | IA PENDING
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | - | - | ER/NR | AMIL |  | IA PENDING
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | - | - | ER/NR | AMIL |  | IA PENDING
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 30 | - | - | ER/NR | AMMO |  | IA PENDING
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 92.5 | - | - | ER/NR | AMIL |  | IA PENDING
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 165 | - | - | ER/NR | AMIL |  | IA PENDING
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | AMMO |  | IA PENDING
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 95 | - | - | ER/NR | SIPC |  | IA PENDING
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | AMIL |  | IA PENDING
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER/NR | AMIL |  | IA PENDING
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 500 | - | - | ER/NR | AMMO |  | IA PENDING
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 1000 | - | - | ER/NR | AMMO |  | IA PENDING
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | AMMO |  | IA PENDING
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | AMMO |  | IA PENDING
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | AMMO |  | IA PENDING
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | AMMO |  | IA PENDING
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 97.5 | - | - | ER | AECI
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER | EES |  | IA PENDING
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | - | - | ER/NR | AMMO |  | IA PENDING
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | AMMO |  | IA PENDING
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | AMMO |  | IA PENDING
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | - | - | ER | CLEC |  | IA PENDING
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 77.5 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1231 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | - | - | ER/NR | BREC |  | IA PENDING
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER | EES |  | IA PENDING
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 50 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 149 | - | - | ER/NR | AMMO |  | IA PENDING
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 0 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER | CLEC |  | IA PENDING
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER | EES |  | IA PENDING
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 90 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 105 | - | - | ER | EES |  | IA PENDING
J1509 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EMI |  | Not Started
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | Not Started
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | EES-EAI |  | Not Started
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | EES-EAI |  | Not Started
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | EES-EAI |  | Not Started
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | Not Started
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 108.34 | - | - | ER/NR | EES |  | Not Started
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 25 | - | - | ER/NR | EES |  | Not Started
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | Not Started
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | - | - | ER | EES |  | Not Started
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | EES-EAI |  | Not Started
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER | EES |  | Not Started
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | EES-EMI |  | Not Started
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | CLEC |  | Not Started
J1709 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 100 | - | - | ER | EES |  | Not Started
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 107.5 | - | - | ER/NR | EES-EAI |  | Not Started
J1723 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 10 | - | - | ER/NR | EES-EAI |  | Not Started
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | EES-EMI |  | Not Started
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EMI |  | Not Started
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | - | - | ER/NR | EES |  | Not Started
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | - | - | ER/NR | EES-EAI |  | Not Started
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | Not Started
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | - | - | ER/NR | EES |  | Not Started
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 43.5 | - | - | ER/NR | EES |  | Not Started
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | - | - | ER | EES-EAI |  | Not Started
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | - | - | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | - | - | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | - | - | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | - | - | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | - | - | ER/NR | OPPD | Tekamah - Raun 161 kV Line
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | - | - | ER | NPPD | Holt County 345kV | DISIS STAGE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | - | - | ER/NR | NPPD | Tobias 345kV Substation
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | - | - | ER/NR | NPPD | Tobias 345kV Substation
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | - | - | ER | OPPD | Jones St. No 1201 69kV substation
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | - | - | ER/NR | NPPD | Hoskins 345kV Substation
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid | 310 | - | - | ER | NPPD | McCool 345kV Substation
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | - | - | ER | NPPD | Spalding to North Loup 115kV
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | - | - | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | - | - | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | - | - | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | - | - | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | - | - | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-125 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 252 | - | - | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-131 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 29.6 | - | - | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | - | - | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | - | - | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | - | - | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | - | - | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | - | - | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-202 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 | - | - | ER/NR | SWPA | New Madrid - Sikeston 161kV | DISIS STAGE
GEN-2017-209 | 03 CENTRAL | 19 | DIS-17-2 | Hybrid | 300 | - | - | ER | KCPL | LaCygne - Neosho 345kV | DISIS STAGE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | - | - | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | - | - | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | - | - | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | - | - | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | - | - | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-132 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 400 | - | - | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | - | - | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | - | - | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | - | - | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | - | - | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | - | - | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | - | - | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | - | - | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-152 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 252 | - | - | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-154 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 255 | - | - | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | - | - | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-167 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | - | - | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-168 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | - | - | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-169 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | - | - | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | - | - | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | - | - | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | - | - | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | - | - | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Hybrid | 210 | - | - | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | - | - | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | - | - | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | - | - | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | - | - | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | - | - | ER | SPS | Deaf Smith-Plant X 230kV
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | - | - | ER | SPS | TUCO-Oklaunion 345kV | DISIS STAGE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | - | - | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | - | - | ER | SPS | Flatland 115 kV Substation | DISIS STAGE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | - | - | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | - | - | ER | XEL
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | - | - | ER | OTP
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | - | - | ER | DPC |  | DISIS STAGE
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | - | - | ER/NR | XEL |  | DISIS STAGE
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | - | - | ER | DPC
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 93.6 | - | - | ER | XEL
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | - | - | ER/NR | ALTW |  | IA PENDING
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | - | - | ER | ALTW
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 125 | - | - | ER/NR | MEC |  | DISIS STAGE
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | - | - | ER/NR | AECI
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | - | - | ER/NR | AECI
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | - | - | ER/NR | AECI
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | - | - | ER/NR | AECI
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | - | - | ER/NR | AECI
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 128.8 | - | - | ER/NR | AECI
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | - | - | ER | WAPA | Rhame 230 kV Sub | DISIS STAGE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | - | - | ER | WAPA | Philip Tap 230 kV | DISIS STAGE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | - | - | ER | BEPC-SPP | Neset 230 kV Substation | DISIS STAGE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | - | - | ER | WAPA | Fort Thompson-Huron 230 kV | DISIS STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | - | - | ER | WAPA | Underwood 115 kV Sub | DISIS STAGE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | - | - | ER | SUNC | Elm Creek - Summit 345 kV | DISIS STAGE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | - | - | ER | WERE | Marmaton - Litchfield 161 kV | DISIS STAGE
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | - | - | ER | EMDE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | - | - | ER/NR | SUNC | Thistle 345 kV sub | DISIS STAGE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | - | - | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | - | - | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | - | - | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | - | - | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | - | - | ER | WERE | Viola 345kV | DISIS STAGE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | - | - | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | - | - | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | DISIS STAGE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | - | - | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | DISIS STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | - | - | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | - | - | ER | WFEC | Snyder - Cache 138 kV | DISIS STAGE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | - | - | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | - | - | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | - | - | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | DISIS STAGE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | - | - | ER | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | - | - | ER | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | - | - | ER | GRDA | Dry Gulch 161kV sub | DISIS STAGE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | - | - | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | - | - | ER | OKGE | Hugo-Sunnyside 345 kV | DISIS STAGE
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | - | - | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | - | - | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | - | - | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | - | - | ER | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | - | - | ER/NR | SPS | Cole 115kV
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | - | - | ER/NR | SPS | Texas County 115kV
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | - | - | ER | BEPC-SPP
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | - | - | ER | BEPC-SPP
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | - | - | ER | BEPC-SPP
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | - | - | ER | BEPC-SPP
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | - | - | ER | BEPC-SPP
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 49.98 | - | - | ER/NR | DPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | - | - | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | - | - | ER | WAPA
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 100 | - | - | ER/NR | MEC
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | - | - | ER | NPPD
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | - | - | ER | SWPA
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | - | - | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | - | - | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | - | - | ER | WAPA | Bismark-Glenham 230 kV line | IA PENDING
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | - | - | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | - | - | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | - | - | ER | BEPC-SPP | Tande 345kV
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | - | - | ER | NPPD | Sweetwater 345kV
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | - | - | ER | NPPD | Sidney 115 kV Sub
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | - | - | ER | WERE | Reno - Summit 345kV | IA PENDING
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | - | - | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | - | - | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | - | - | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | - | - | ER | WERE | Viola 345kV | IA PENDING
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | - | - | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | - | - | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | - | - | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | - | - | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | - | - | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | - | - | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | - | - | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | - | - | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | - | - | ER | OKGE | Spring Creek-Sooner 345kV | IA PENDING
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | - | - | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | - | - | ER | OKGE | Woodring 345kV | IA PENDING
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | - | - | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | - | - | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | - | - | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | - | - | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | - | - | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | - | - | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | - | - | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | - | - | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | - | - | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | - | - | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | - | - | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | - | - | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | - | - | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | - | - | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-123 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 298 | - | - | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 150 | - | - | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 74 | - | - | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal | 17 | - | - | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | Wind | 100 | - | - | ER/NR | XEL
ASGI-2017-006GIA-53 | 03 CENTRAL | 16.5 | Dis-16-2-PQ | Wind | 238 | - | - | ER/NR | AECI
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 246 | - | - | ER/NR | AMMO
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.4 | - | - | ER | SWPA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.73 | - | - | ER | SWPA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | - | - | ER | WFEC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | - | - | ER | BEPC-SPP | Utica 230 kV Substation
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | - | - | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 NORTH | 16 | DIS-16-1 | Wind | 100.05 | - | - | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | - | - | ER | BEPC-SPP | Chappelle Creek 345kV
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | - | - | ER | NPPD | Hoskins 345kV
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | - | - | ER | NPPD | Hoskins 345kV
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | - | - | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 15.8 | - | - | ER | KCPL |  | IA PENDING
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 29 | - | - | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 10 | - | - | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 10 | - | - | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 78.2 | - | - | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | - | - | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-050 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 250.7 | - | - | ER | NPPD | Axtell â€“ Post Rock 345 kV
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | - | - | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | - | - | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 176 | - | - | ER | OKGE | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | - | - | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 148.4 | - | - | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | - | - | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | - | - | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | - | - | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | - | - | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | - | - | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | - | - | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 04 SOUTHEAST | 16 | DIS-16-1 | Thermal | 24 | - | - | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | - | - | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | - | - | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | - | - | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | - | - | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | - | - | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | - | - | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 57 | - | - | ER | OKGE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | - | - | ER | SPS
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | Thermal | 5 | - | - | ER | SPS | TUCO 345kV
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | - | - | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 15 | DIS-15-2 | Wind | 300 | - | - | ER | BEPC-SPP | Tande 345kV
GEN-2015-096 | 01 NORTH | 15 | DIS-15-2 | Wind | 150 | - | - | ER | BEPC-SPP | Brady 230kV substation
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | - | - | ER/NR | NPPD | Tobias 345kV Substation
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | - | - | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-064 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 197.8 | - | - | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | - | - | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | - | - | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 200.1 | - | - | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | - | - | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 20 | - | - | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | - | - | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | - | - | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 100 | - | - | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | - | - | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | - | - | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | - | - | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 | - | - | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 | - | - | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 20 | - | - | ER | WAPA
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 20 | - | - | ER | WAPA
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | - | - | ER/NR | BEPC-SPP
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | - | - | ER/NR | BEPC-SPP
GEN-2005-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | - | - | ER/NR | BEPC-SPP
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 50 | - | - | ER/NR | BEPC-SPP
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | - | - | ER/NR | XEL
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 53 | - | - | ER/NR | WAPA
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | - | - | ER/NR | XEL
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 50 | - | - | ER/NR | BEPC-SPP
GEN-2007-013IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | - | - | ER/NR | BEPC-SPP
GEN-2007-014IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 50 | - | - | ER/NR | BEPC-SPP
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | - | - | ER/NR | BEPC-SPP
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 16 | - | - | ER/NR | BEPC-SPP
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | - | - | ER/NR | WAPA
GEN-2009-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 200 | - | - | ER/NR | BEPC-SPP
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | - | - | ER | BEPC-SPP
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 80 | - | - | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 110 | - | - | ER/NR | BEPC-SPP
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | - | - | ER/NR | BEPC-SPP
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 34 | - | - | ER/NR | BEPC-SPP
GEN-2013-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 19.5 | - | - | ER | WAPA
GEN-2014-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 103.24 | - | - | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 125 | - | - | ER/NR | BEPC-SPP
GEN-2014-010IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 150 | - | - | ER/NR | BEPC-SPP
GEN-2014-014IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 150 | - | - | ER/NR | BEPC-SPP
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | - | - | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | - | - | ER/NR | OPPD
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | - | - | ER | NPPD | Hoskins 345kV
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | - | - | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | - | - | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | - | - | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200 | - | - | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | - | - | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | - | - | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-004 | 04 SOUTHEAST | 14 | DIS-15-1 | Thermal | 56.4 | - | - | ER | GRDA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | - | - | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | - | - | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | - | - | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | - | - | ER | SPS | Tap Cochran - Lehman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | - | - | ER/NR | GRIS | Meadow Grove 230kV
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | - | - | ER/NR | NPPD | Meadow Grove 230kV
GEN-2004-017 | 03 CENTRAL | 13 | DIS-14-2 | Thermal | 250 | - | - | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 300 | - | - | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | - | - | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | Thermal | 50 | - | - | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2014-014 | 04 SOUTHEAST | 13 | DIS-14-2 | Thermal | 56.4 | - | - | ER | GRDA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 100 | - | - | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | - | - | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | - | - | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | - | - | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | - | - | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | - | - | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | - | - | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | - | - | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | - | - | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 4 | - | - | ER | NPPD | Steele City 115kV | DISIS STAGE
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | - | - | ER/NR | LES | Meadow Grove 230kV
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | - | - | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | - | - | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | - | - | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 73.6 | - | - | ER/NR | NPPD | Monolith 115kV
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | - | - | ER | NPPD | Antelope 115kV
ASGI-2013-004 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 36.6 | - | - | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Thermal | 75.6 | - | - | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Thermal | 28 | - | - | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 04 SOUTHEAST | 11 | DIS-13-2 | Thermal | 538 | - | - | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | - | - | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | - | - | ER | SPS
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | - | - | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 50.6 | - | - | ER/NR | NPPD | Monolith 115kV
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | - | - | ER | NPPD | Steele City 115kV
GEN-2006-010 | 04 SOUTHEAST | 10 | DIS-13-1 | Thermal | 620 | - | - | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | - | - | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 04 SOUTHEAST | 10 | DIS-13-1 | Thermal | 30 | - | - | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 04 SOUTHEAST | 10 | DIS-13-1 | Thermal | 147 | - | - | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | - | - | ER | SPS
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | - | - | ER | SPS
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | - | - | ER | SPS
GEN-2013-016 | 05 SOUTHWEST | 10 | DIS-13-1 | Thermal | 203 | - | - | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Thermal | 4.8 | - | - | ER | LES | Terry Bundy Generating Station 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | - | - | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | - | - | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | - | - | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | - | - | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 9 | DIS-12-2 | Thermal | 121.5 | - | - | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | - | - | ER | SPS
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | - | - | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 7 | - | - | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 7 | - | - | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 7 | - | - | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 203 | - | - | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | - | - | ER | NPPD | Ainsworth Wind Tap 115kV
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Thermal | 75 | - | - | ER | NPPD | Columbus Co 115kV
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | - | - | ER | NPPD | Bloomfield 115kV
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | - | - | ER | NPPD | Broken Bow 115kV
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | - | - | ER | NPPD | Petersburg North 115kV
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | - | - | ER | NPPD | Bloomfield 115kV
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | - | - | ER | OPPD | S1399 161kV
NPPDBrokenBow | 02 NEBRASKA | 8 | PQ | Heat | 7.3 | - | - | ER | NPPD
NPPDBuffaloCountySolar | 02 NEBRASKA | 8 | PQ | Solar | 10 | - | - | ER | NPPD
NPPDBurtCountyWind | 02 NEBRASKA | 8 | PQ | Wind | 10 | - | - | ER | NPPD
NPPDBurwell | 02 NEBRASKA | 8 | PQ | Heat | 3.3 | - | - | ER | NPPD
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 15 | - | - | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | - | - | ER | NPPD
NPPDStuart | 02 NEBRASKA | 8 | PQ | Heat | 1.8 | - | - | ER | NPPD
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | - | - | ER | SUNC
ASGI-2012-008 | 03 CENTRAL | 8 | PQ | Gas | 3.655 | - | - | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 03 CENTRAL | 8 | PQ | Thermal | 50 | - | - | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | - | - | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | - | - | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | Thermal | 50 | - | - | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | - | - | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 CENTRAL | 8 | PQ | Wind | 100.5 | - | - | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | - | - | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | - | - | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 152 | - | - | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | - | - | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | - | - | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | - | - | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 8 | DIS-12-1 | Thermal | 120 | - | - | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 CENTRAL | 8 | PQ | Wind | 110 | - | - | ER | SUNC
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | - | - | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | - | - | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | - | - | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | - | - | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 04 SOUTHEAST | 8 | PQ | Wind | 100 | - | - | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | - | - | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | - | - | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 04 SOUTHEAST | 8 | PQ | Wind | 20.6 | - | - | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 30.6 | - | - | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | - | - | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | - | - | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | - | - | ER | AEP | Arsenal Hill 138kV | DISIS STAGE
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | - | - | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | - | - | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | - | - | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | - | - | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | Wind | 40.8 | - | - | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 05 SOUTHWEST | 8 | PQ | Wind | 180 | - | - | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 05 SOUTHWEST | 8 | PQ | Wind | 80 | - | - | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | - | - | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | - | - | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 05 SOUTHWEST | 8 | PQ | Wind | 159.1 | - | - | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 05 SOUTHWEST | 8 | PQ | Thermal | 150 | - | - | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 05 SOUTHWEST | 8 | PQ | Thermal | 150 | - | - | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | Thermal | 168.1 | - | - | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | - | - | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 05 SOUTHWEST | 8 | PQ | Thermal | 604 | - | - | ER | SPS | Hobbs 230kV & Hobbs 115kV
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | - | - | ER | SPS | Tap Grassland Â- Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | - | - | ER | SPS
SPSCarson | 05 SOUTHWEST | 8 | PQ | Wind | 10 | - | - | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 10 | - | - | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 10 | - | - | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | - | - | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | - | - | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | - | - | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | - | - | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 10 | - | - | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | - | - | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 10 | - | - | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | - | - | ER | SPS
GEN-2011-056 | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | - | - | ER | NPPD | Jeffrey 115kV
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | - | - | ER | NPPD | John 1 115kV
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 18 | - | - | ER | NPPD
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | - | - | ER | NPPD | John 2 115kV
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 18 | - | - | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | - | - | ER | NPPD
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | - | - | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | - | - | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 111 | - | - | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | - | - | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | - | - | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | - | - | ER | SPS
GEN-2011-045 | 05 SOUTHWEST | 7 | DIS-11-2 | Thermal | 205 | - | - | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 05 SOUTHWEST | 7 | DIS-11-2 | Thermal | 23 | - | - | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 05 SOUTHWEST | 7 | DIS-11-2 | Thermal | 175 | - | - | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 73.6 | - | - | ER/NR | NPPD | Steele City 115kV
GEN-2011-027 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 120 | - | - | ER/NR | NPPD | Wakefield 230kV
GEN-2004-008 | 03 CENTRAL | 6 | DIS-11-1 | Thermal | 850 | - | - | ER | KCPL |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | - | - | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | - | - | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 6 | DIS-11-1 | Thermal | 4.5 | - | - | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | - | - | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | - | - | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | - | - | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | - | - | ER | SPS
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | - | - | ER | SPS
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | - | - | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | - | - | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 5 | DIS-10-2 | Wind | 200 | - | - | ER | NPPD | Wakefield 230kV
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | - | - | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.757 | - | - | ER | WERE
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | - | - | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | - | - | ER | SPS
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | - | - | ER | SPS
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | - | - | ER | SPS
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | - | - | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | - | - | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | - | - | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 48.3 | - | - | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 72 | - | - | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | - | - | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | - | - | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 165.6 | - | - | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | - | - | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 197.8 | - | - | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 29.7 | - | - | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 46.5 | - | - | ER | SPS
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | - | - | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | - | - | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-006 | 05 SOUTHWEST | 4 | DIS-10-1 | Thermal | 205 | - | - | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-037N1 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 75 | - | - | ER | NPPD | Broken Bow 115kV
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | - | - | ER | OPPD | North Petersburg 115kV
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | - | - | ER | NPPD | Meadow Grove 230kV
GEN-2007-040 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 131.1 | - | - | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | - | - | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.5 | - | - | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 | - | - | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 CENTRAL | 3 | DIS-09-1 | Thermal | 72 | - | - | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | - | - | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | - | - | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | - | - | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | - | - | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | - | - | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | - | - | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 04 SOUTHEAST | 2 | ICS1 | Wind | 200 | - | - | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | - | - | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | - | - | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 04 SOUTHEAST | 2 | ICS1 | Thermal | 150 | - | - | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 2 | ICS1 | Wind | 424 | - | - | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 2 | ICS1 | Wind | 101.2 | - | - | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | - | - | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | - | - | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640226HOSKINS3345640588TURTLE.CRK33451 | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640226HOSKINS3345640588TURTLE.CRK33451 | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640226HOSKINS3345640588TURTLE.CRK33451 | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640226HOSKINS3345640588TURTLE.CRK33451 | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640226HOSKINS3345640588TURTLE.CRK33451 | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640588TURTLE.CRK3345659160GROTON__-BE33451 | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640588TURTLE.CRK3345659160GROTON__-BE33451 | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640588TURTLE.CRK3345659160GROTON__-BE33451 | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640588TURTLE.CRK3345659160GROTON__-BE33451 | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 640588TURTLE.CRK3345659160GROTON__-BE33451 | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 645458S34583345659130CHAPELLE-BE33451 | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 645458S34583345659130CHAPELLE-BE33451 | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 645458S34583345659130CHAPELLE-BE33451 | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 645458S34583345659130CHAPELLE-BE33451 | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 645458S34583345659130CHAPELLE-BE33451 | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 658174IRVSIMM7115773300G23-066-TAP1151 | [7 empty] | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 659448DAGLUM__-BE4230775180G23-160-TAP2301 | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 659448DAGLUM__-BE4230775180G23-160-TAP2301 | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 659448DAGLUM__-BE4230775180G23-160-TAP2301 | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 659448DAGLUM__-BE4230775180G23-160-TAP2301 | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | 659448DAGLUM__-BE4230775180G23-160-TAP2301 | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | 767380G22-020-PROX345773060G23-054-TAP3451 | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27WP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new OAHE to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | 767380G22-020-PROX345773060G23-054-TAP3451 | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | 767380G22-020-PROX345773060G23-054-TAP3451 | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | 767380G22-020-PROX345773060G23-054-TAP3451 | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | 767380G22-020-PROX345773060G23-054-TAP3451 | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27WP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27WP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27WP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27WP | P13:230-345:NPPD:STEGALL3:KV3A::: | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P12:230:UMZW:# 161 #:: PL IN SD. NU-PLT-OA & PLT-PL (PLT IS A TAP):HV: | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV: | [7 empty] | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P23:345:UMZB:# 7110 #:: CKE IN SD. CKE BREAKER FAULT (192):EHV | [7 empty] | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P23:345:UMZB:# 7110 #:: CKE IN SD. CKE BREAKER FAULT (192):EHV | [7 empty] | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new BELFELD3 to MAURINE 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new OAHE to SWEET W3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new Maurine 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV | [7 empty] | Build a new Oahe 345/230 kV transformer 1
01ALL | ERIS | Voltage | WAYSIDE4 | 27SP | System Intact |  |  |  |  | 0.795 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | FAITH 7 | 27SP | System Intact |  |  |  |  | 0.8355 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | ELKCRK 7 | 27SP | System Intact |  |  |  |  | 0.781 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | ELSWRTH7 | 27SP | System Intact |  |  |  |  | 0.789 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | MARTIN 7 | 27SP | System Intact |  |  |  |  | 0.8435 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | MAURINE7 | 27SP | System Intact |  |  |  |  | 0.8397 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | NEWELL 7 | 27SP | System Intact |  |  |  |  | 0.803 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | NUNDRWD4 | 27SP | System Intact |  |  |  |  | 0.8014 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | NUNDRWD7 | 27SP | System Intact |  |  |  |  | 0.8023 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | PHILIP 7 | 27SP | System Intact |  |  |  |  | 0.8848 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | SULPHUR | 27SP | System Intact |  |  |  |  | 0.8466 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | WALL 7 | 27SP | System Intact |  |  |  |  | 0.8401 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | MAURINE4 | 27SP | System Intact |  |  |  |  | 0.8463 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | G22-066-PROX | 27SP | System Intact |  |  |  |  | 0.8501 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | G23-098-TAP | 27SP | System Intact |  |  |  |  | 0.8832 | 0.9 | 1.05 | Build a new 150 MVAR cap bank at Maurine 345 kV
01ALL | ERIS | Voltage | WAYSIDE4 | 27SP | System Intact |  |  |  |  | 0.795 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | FAITH 7 | 27SP | System Intact |  |  |  |  | 0.8355 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | ELKCRK 7 | 27SP | System Intact |  |  |  |  | 0.781 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | ELSWRTH7 | 27SP | System Intact |  |  |  |  | 0.789 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | MARTIN 7 | 27SP | System Intact |  |  |  |  | 0.8435 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | MAURINE7 | 27SP | System Intact |  |  |  |  | 0.8397 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | NEWELL 7 | 27SP | System Intact |  |  |  |  | 0.803 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | NUNDRWD4 | 27SP | System Intact |  |  |  |  | 0.8014 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | NUNDRWD7 | 27SP | System Intact |  |  |  |  | 0.8023 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | PHILIP 7 | 27SP | System Intact |  |  |  |  | 0.8848 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | SULPHUR | 27SP | System Intact |  |  |  |  | 0.8466 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | WALL 7 | 27SP | System Intact |  |  |  |  | 0.8401 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | MAURINE4 | 27SP | System Intact |  |  |  |  | 0.8463 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | G22-066-PROX | 27SP | System Intact |  |  |  |  | 0.8501 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Voltage | G23-098-TAP | 27SP | System Intact |  |  |  |  | 0.8832 | 0.9 | 1.05 | Build a new 200 MVAR cap bank at Oahe 345 kV
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | System Intact | [7 empty] | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | System Intact | [7 empty] | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27WP | System Intact | [7 empty] | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 24SP | System Intact | [7 empty] | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27SP | System Intact | [7 empty] | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1
01ALL | ERIS | Non-Converge | Non-Converge | 27WP | System Intact | [7 empty] | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1
02ALL | ERIS | Thermal | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 27WP | 531451 MINGO 7 345 767280 G22-015-TAP 345 2 |  | 966 | <90% | 113.95 |  |  |  | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1
02ALL | ERIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 27L | 640076 BEATRCE7 115 640208 HARBINE7 115 2 |  | 139 | <90% | 106.27 |  |  |  | Rebuild the BEATRCE7 to HARBINE7 115kV line 1
02ALL | ERIS | Non-Converge | Non-Converge | 27WP, 24SP, 27SP | 640183 GENTLMN3 345 640252 KEYSTON3 345 1 | [7 empty] | BUILD GENTLMN3 KEYSTONE3 345kV CKT2
02ALL | ERIS | Thermal | 640183 GENTLMN3 345 640252 KEYSTON3 345 1 | 27WP, 27SP, 24SP | 640183 GENTLMN3 345 640252 KEYSTON3 345 2 |  | 956 | <90% | 121.99 |  |  |  | Rebuild the GENTLMN3 to KEYSTON3 345kV line 1
02ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 27SP, 27WP | 640252 KEYSTON3 345 763666 G21-037-TAP 345 1 |  | 320 | <90% | 101.37 |  |  |  | BUILD KEYSTON3 G21-037-TAP 345kV CKT 2
02ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 27SP, 24SP, 27WP | 640252 KEYSTON3 345 763666 G21-037-TAP 345 1 |  | 320 | 116.44 | 133.94 |  |  |  | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1
02ALL | ERIS | Thermal | 653300 CHAPPEL7 115 659817 COLTON__-TS7 115 1 | 27SP | 640252 KEYSTON3 345 763666 G21-037-TAP 345 1 |  | 109 | 95.44 | 100.29 |  |  |  | BUILD KEYSTON3 G21-037-TAP 345kV CKT 2
02ALL | ERIS | Thermal | 653312 MORRILL7 115 659821 GERINGT_-TS7 115 1 | 27SP, 24SP | 640252 KEYSTON3 345 763666 G21-037-TAP 345 1 |  | 91 | 113.14 | 120.3 |  |  |  | Rebuild the MORRILL7 to GERINGT_-TS7 115kV line 1 (non-SPP)
02ALL | ERIS | Thermal | 653572 SIDNEY 7 115 659817 COLTON__-TS7 115 1 | 27SP | 640252 KEYSTON3 345 763666 G21-037-TAP 345 1 |  | 107 | 100.26 | 105.19 |  |  |  | BUILD KEYSTON3 G21-037-TAP 345kV CKT 2
02ALL | ERIS | Thermal | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | 27WP | 640325 REDWILO3 345 767280 G22-015-TAP 345 2 |  | 966 | <90% | 114.13 |  |  |  | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1
02ALL | ERIS | Thermal | 635201 RAUN 5 161 762069 G17-105TAP 161 1 | 24SP, 27SP, 27WP | 640377 TEKAMAH5 161 762069 G17-105TAP 161 1 |  | 217 | <90% | 101.36 |  |  |  | BUILD TEKAMAH5 G17-105TAP 161kV CKT2
02ALL | ERIS | Thermal | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 27SP, 24SP, 27WP | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 256 | <90% | 133.57 |  |  |  | Rebuild the TEKAMAH5 to S1226 5 161kV line 1
02ALL | ERIS | Thermal | 640377 TEKAMAH5 161 762069 G17-105TAP 161 1 | 27SP, 24SP, 27WP | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 |  | 217 | <90% | 156.39 |  |  |  | Rebuild the TEKAMAH5 to G17-105TAP 161kV line 1
02ALL | ERIS | Thermal | 640265 MALONEY7 115 640287 N.PLATT7 115 1 | 27WP | 659807 ELSIETP_-TS7 115 773400 G23-071-TAP 115 1 |  | 156 | <90% | 101.29 |  |  |  | Rebuild the MALONEY7 to N.PLATT7 115kV line 1
02ALL | ERIS | Thermal | 640265 MALONEY7 115 640370 SUTHLND7 115 1 | 27WP, 24SP, 27SP | 659807 ELSIETP_-TS7 115 773400 G23-071-TAP 115 1 |  | 155 | <90% | 118.31 |  |  |  | Rebuild the MALONEY7 to SUTHLND7 115kV line 1
02ALL | ERIS | Thermal | 640370 SUTHLND7 115 659808 PAXTON__-TS7 115 1 | 27WP, 24SP, 27SP | 659807 ELSIETP_-TS7 115 773400 G23-071-TAP 115 1 |  | 108 | <90% | 177.14 |  |  |  | Rebuild the SUTHLND7 to PAXTON__-TS7 115kV line 1
02ALL | ERIS | Thermal | 659807 ELSIETP_-TS7 115 773400 G23-071-TAP 115 1 | 27SP, 24SP, 27WP | 659808 PAXTON__-TS7 115 773400 G23-071-TAP 115 1 |  | 131 | <90% | 148.31 |  |  |  | Rebuild the ELSIETP_-TS7 to G23-071-TAP 115kV line 1
02ALL | ERIS | Thermal | 659808 PAXTON__-TS7 115 773400 G23-071-TAP 115 1 | 27SP, 24SP, 27WP | P12:115:RMR:# 3529 #:: MC-ON-GH-CON IN NE. :HV: |  | 131 | <90% | 148.93 |  |  |  | Rebuild the PAXTON__-TS7 to G23-071-TAP 115kV line 1
02ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | 27L, 27WP, 24SP, 27SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: |  | 956.1 | <90% | 157.26 |  |  |  | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2
02ALL | ERIS | Thermal | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 27WP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 239 | <90% | 108.84 |  |  |  | Rebuild the PILE 3 to SCOTCTY3 115kV line 1
02ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 27WP, 24SP, 27SP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 252 | <90% | 120 |  |  |  | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1
02ALL | ERIS | Thermal | 531464 SETAB 3 115 997499 SETAB 115 1 | 27L, 27WP, 27SP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 298.8 | <90% | 121.32 |  |  |  | Build a new Setab 345/115 kV transformer 2
02ALL | ERIS | Thermal | 531464 SETAB 3 115 997501 SETAB 115 1 | 24SP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 298.8 | <90% | 114.19 |  |  |  | Build a new Setab 345/115 kV transformer 2
02ALL | ERIS | Thermal | 531465 SETAB 7 345 997499 SETAB 115 1 | 27WP, 27L, 27SP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 298.8 | <90% | 125.56 |  |  |  | Build a new Setab 345/115 kV transformer 2
02ALL | ERIS | Thermal | 531465 SETAB 7 345 997501 SETAB 115 1 | 24SP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 298.8 | <90% | 117.69 |  |  |  | Build a new Setab 345/115 kV transformer 2
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 27L, 27WP, 24SP, 27SP | P42:345:NPPD:BKR-HOS-3308:::: |  | 1792 | <90% | 118.15 |  |  |  | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 1
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 27L, 27WP, 24SP, 27SP | P42:345:NPPD:BKR-HOS-3308:::: |  | 1792 | <90% | 118.15 |  |  |  | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 2
03ALL | ERIS | Thermal | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 24SP, 27L, 27SP, 27WP | 300042 7HUBEN 345 300045 7MORGAN 345 1 |  | 213 | 59.58 | 126.3 |  |  |  | Rebuild the 5MANSFDMN to G23-085-TAP 161kV line 1
03ALL | ERIS | Thermal | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 24SP, 27SP, 27WP | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 |  | 254 | 15.55 | 106.46 |  |  |  | Rebuild the LBRTYST5 to BRMGHAM5 161kV line 1
03ALL | ERIS | Thermal | 300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | 24SP, 27SP, 27WP | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 |  | 1195 | 97.6 | 142.62 |  |  |  | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1
03ALL | ERIS | Thermal | 547468 AUR124 5 161 547480 MON383 5 161 1 | 27WP | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 |  | 223 | 82.24 | 116.03 |  |  |  | Rebuild the AUR124 5 to MON383 5 161kV line 1
03ALL | ERIS | Thermal | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 24SP, 27SP, 27WP | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 |  | 956 | 107.48 | 162.6 |  |  |  | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1
03ALL | ERIS | Thermal | 541241 SEDEAST5 161 768980 G22-100-TAP 161 1 | 24SP, 27SP, 27WP | 345411 5OVERTON 2 161 774280 G23-115-TAP 161 1 |  | 347 | 22.53 | 107.94 |  |  |  | Rebuild the SEDEAST5 to G22-100-TAP 161kV line 1
03ALL | ERIS | Thermal | 768980 G22-100-TAP 161 774280 G23-115-TAP 161 1 | 24SP, 27SP | 345411 5OVERTON 2 161 774280 G23-115-TAP 161 1 |  | 259 | 0.05 | 113.41 |  |  |  | Rebuild the G22-100-TAP to G23-115-TAP 161kV line 1
03ALL | ERIS | Thermal | 541209 SEDALIA5 161 541241 SEDEAST5 161 1 | 24SP, 27SP | 345411 5OVERTON 2 161 774280 G23-115-TAP 161 1 |  | 281 | 3.61 | 107.24 |  |  |  | Rebuild the SEDALIA5 to SEDEAST5 161kV line 1
03ALL | ERIS | Thermal | 505486 NEO SPA5 161 505488 CARTHAG5 161 1 | 24SP, 27SP | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 215 | 68.32 | 111.69 |  |  |  | Rebuild the NEO SPA5 to CARTHAG5 161kV line 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 24SP, 27SP, 27WP | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 322 | 37.06 | 102.19 |  |  |  | Build a new CARTHAG5 to CAR395 5 161kV line 2
03ALL | ERIS | Thermal | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | 24SP, 27SP | 505488 CARTHAG5 161 547485 CAR395 5 161 1 |  | 290 | 29.3 | 102.35 |  |  |  | Build a new CARTHAG5 to CAR395 5 161kV line 2
03ALL | ERIS | Thermal | 505492 SPRGFLD5 161 547479 LAR382 5 161 2 | 24SP, 27SP, 27WP | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 |  | 189 | 100.97 | 175.32 |  |  |  | Rebuild the SPRGFLD5 to LAR382 5 161kV line 2
03ALL | ERIS | Thermal | 547479 LAR382 5 161 547480 MON383 5 161 1 | 24SP, 27SP, 27WP | 505492 SPRGFLD5 161 547479 LAR382 5 161 2 |  | 223 | 79.85 | 131.13 |  |  |  | Rebuild the LAR382 5 to MON383 5 161kV line 1
03ALL | ERIS | Thermal | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 | 24SP, 27SP, 27WP | 505492 SPRGFLD5 161 547479 LAR382 5 161 2 |  | 167 | 83.01 | 143.93 |  |  |  | Rebuild the SPRGFLD5 to LAR382 5 161kV line 1
03ALL | ERIS | Thermal | 509790 CATOOSA4 138 509804 LLANETP4 138 1 | 27SP | 509771 LLAN ET4 138 509790 CATOOSA4 138 1 |  | 235 | 31.73 | 107.05 |  |  |  | Rebuild the CATOOSA4 to LLANETP4 138kV line 1
03ALL | ERIS | Thermal | 506934 FLINTCR5 161 547484 DEC392 5 161 1 | 24SP, 27SP | 512750 TONECE7 345 774740 G23-138-TAP 345 1 |  | 274 | 48.72 | 130.91 |  |  |  | Rebuild the FLINTCR5 to DEC392 5 161kV line 1
03ALL | ERIS | Thermal | 503997 SIBLEYRD5 161 547496 NOL435 5 161 1 | 24SP, 27SP, 27WP | 512750 TONECE7 345 774740 G23-138-TAP 345 1 |  | 223 | 43.44 | 133.27 |  |  |  | Rebuild the SIBLEYRD5 to NOL435 5 161kV line 1
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 24SP, 27L, 27SP, 27WP | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 |  | 1792 | 46.64 | 118.82 |  |  |  | Build a new FINNEY to HOLCOMB7 345kV line 3
03ALL | ERIS | Thermal | 539695 SPEARVL6 230 997353 SPEARVL 230 1 | 24SP | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 |  | 373.5 | 46.6 | 100.53 |  |  |  | Build a new Spearville 345/230 kV transformer 2
03ALL | ERIS | Thermal | 531469 SPERVIL7 345 997353 SPEARVL 230 1 | 24SP | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 |  | 373.5 | 46.43 | 100.07 |  |  |  | Build a new Spearville 345/230 kV transformer 2
03ALL | ERIS | Thermal | 539695 SPEARVL6 230 997351 SPEARVL 230 1 | 27SP, 27WP | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 |  | 373.5 | 56.57 | 107.65 |  |  |  | Build a new Spearville 345/230 kV transformer 2
03ALL | ERIS | Thermal | 531469 SPERVIL7 345 997351 SPEARVL 230 1 | 27SP, 27WP | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 |  | 373.5 | 55.93 | 107.14 |  |  |  | Build a new Spearville 345/230 kV transformer 2
03ALL | ERIS | Thermal | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | 27WP | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 |  | 398.4 | 60.07 | 103.46 |  |  |  | Rebuild the SPEARVL6 to G19-053-TAP 230kV line 1
03ALL | ERIS | Thermal | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1 | 24SP, 27SP, 27WP | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 |  | 1015 | 77.43 | 108.11 |  |  |  | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1
03ALL | ERIS | Thermal | 532938 FRANKLIN5 161 772480 G23-025-TAP 161 1 | 24SP, 27SP, 27WP | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 |  | 250 | 76.23 | 158.44 |  |  |  | Build a new G23-025-TAP to LITCH 5 161kV line 1
03ALL | ERIS | Thermal | 532938 FRANKLIN5 161 772480 G23-025-TAP 161 1 | 24SP, 27SP, 27WP | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 |  | 250 | 76.23 | 158.44 |  |  |  | Rebuild the FRANKLIN5 to G23-025-TAP 161kV line 1
03ALL | ERIS | Thermal | 532937 NEOSHO 5 161 997417 NEOSHO TX-4 138 1 | 24SP | 532937 NEOSHO 5 161 3WXFMR NEOSHO TX-5 1 |  | 123.2 | 67.17 | 102.42 |  |  |  | Replace Neosho TX-4 161/138 kV transformer 1
03ALL | ERIS | Thermal | 533021 NEOSHO 4 138 997417 NEOSHO TX-4 138 1 | 24SP | 532937 NEOSHO 5 161 3WXFMR NEOSHO TX-5 1 |  | 123.2 | 66.6 | 101.31 |  |  |  | Replace Neosho TX-4 161/138 kV transformer 1
03ALL | ERIS | Thermal | 532937 NEOSHO 5 161 997415 NEOSHO TX-4 138 1 | 27SP | 532937 NEOSHO 5 161 3WXFMR NEOSHO TX-5 1 |  | 123.2 | 68.12 | 105.49 |  |  |  | Replace Neosho TX-4 161/138 kV transformer 1
03ALL | ERIS | Thermal | 533021 NEOSHO 4 138 997415 NEOSHO TX-4 138 1 | 27SP | 532937 NEOSHO 5 161 3WXFMR NEOSHO TX-5 1 |  | 123.2 | 67.54 | 104.21 |  |  |  | Replace Neosho TX-4 161/138 kV transformer 1
03ALL | ERIS | Thermal | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1 | 24SP, 27SP, 27WP | 532938 FRANKLIN5 161 772480 G23-025-TAP 161 1 |  | 250 | 76.25 | 156.29 |  |  |  | Build a new G23-025-TAP to LITCH 5 161kV line 1
03ALL | ERIS | Thermal | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 24SP, 27SP, 27WP | 532938 FRANKLIN5 161 772480 G23-025-TAP 161 1 |  | 228 | 64.16 | 119.46 |  |  |  | Build a new G23-025-TAP to LITCH 5 161kV line 1
03ALL | ERIS | Thermal | 532991 WEAVER 4 138 533062 ROSEHIL4 138 1 | 24SP, 27SP | 533039 ELPASO 4 138 533059 ELPASOE4 138 Z1 |  | 382 | 75.83 | 105.2 |  |  |  | Rebuild the WEAVER 4 to ROSEHIL4 138kV line 1
03ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP | 533304 LANG 3 115 767120 G22-007-TAP 115 1 | [7 empty] | Build a new LANG 3 to G22-007-TAP 115kV line 2
03ALL | ERIS | Thermal | 533547 OAK 2 69.0 533563 PRAIRIJ2 69.0 1 | 27WP | 533543 CRESWLN2 69.0 533547 OAK 2 69.0 1 |  | 72 | 54.7 | 106.02 |  |  |  | Rebuild the OAK 2 to PRAIRIJ2 69kV line 1
03ALL | ERIS | Thermal | 533556 STROTHR2 69.0 533561 WINFLD 2 69.0 1 | 24SP, 27SP, 27WP | 533549 RAINBOW2 69.0 533561 WINFLD 2 69.0 1 |  | 71 | 78.53 | 139.83 |  |  |  | Rebuild the STROTHR2 to WINFLD 2 69kV line 1
03ALL | ERIS | Thermal | 533547 OAK 2 69.0 533556 STROTHR2 69.0 1 | 24SP, 27SP, 27WP | 533549 RAINBOW2 69.0 533561 WINFLD 2 69.0 1 |  | 77 | 63.99 | 120.18 |  |  |  | Rebuild the OAK 2 to STROTHR2 69kV line 1
03ALL | ERIS | Thermal | 345411 5OVERTON 2 161 774280 G23-115-TAP 161 1 | 24SP, 27SP, 27WP | 541241 SEDEAST5 161 768980 G22-100-TAP 161 1 |  | 259 | 29.98 | 143.27 |  |  |  | Rebuild the 5OVERTON 2 to G23-115-TAP 161kV line 1
03ALL | ERIS | Thermal | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 24SP, 27SP | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 |  | 211 | 18.29 | 119.66 |  |  |  | Rebuild the 5MOCITYB2 to G23-169-TAP 161kV line 1
03ALL | ERIS | Thermal | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | 24SP, 27SP, 27WP | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 |  | 1792 | 117.7 | 130.41 |  |  |  | Build a new LACYGNE7 to PHILL 7 345kV line 1
03ALL | ERIS | Thermal | 765155 G20-076-TAP 345 766141 G21-096-TAP 345 1 | 24SP, 27SP | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 956 | 86.92 | 111.21 |  |  |  | Rebuild the G20-076-TAP to G21-096-TAP 345kV line 1
03ALL | ERIS | Thermal | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | 27SP | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1792 | 70.12 | 100.92 |  |  |  | Build a new LACYGNE7 to G20-007-TAP 345kV line 2
03ALL | ERIS | Non-Converge | Non-Converge | 24SP | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | [7 empty] | Blackberry - Wolf Creek 345 kV
03ALL | ERIS | Thermal | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | 24SP, 27SP, 27WP | 543004 BLUMILS5 161 548807 BLUVLY-161 161 1 |  | 282 | 27.5 | 136.96 |  |  |  | Rebuild the SIBLEYPL to ECKLES-161 161kV line 1
03ALL | ERIS | Thermal | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | 24SP, 27SP, 27WP | 543004 BLUMILS5 161 548807 BLUVLY-161 161 1 |  | 309 | 58.3 | 121.53 |  |  |  | Rebuild the BLUMILS5 to ECKLES-161 161kV line 1
03ALL | ERIS | Thermal | 543004 BLUMILS5 161 548807 BLUVLY-161 161 1 | 24SP, 27SP, 27WP | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 |  | 309 | 58.54 | 122.05 |  |  |  | Rebuild the BLUMILS5 to BLUVLY-161 161kV line 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547469 RIV4525 161 1 | 24SP, 27SP, 27WP | 547469 RIV4525 161 547498 STL439 5 161 1 |  | 348 | 94.12 | 108.01 |  |  |  | Build a new G20-079-TAP to STL439 5 161kV line 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547469 RIV4525 161 1 | 24SP, 27SP, 27WP | 547469 RIV4525 161 547498 STL439 5 161 1 |  | 348 | 94.12 | 108.01 |  |  |  | Rebuild the ORO110 5 to RIV4525 161kV line 1
03ALL | ERIS | Thermal | 532932 LITCH 5 161 532938 FRANKLIN5 161 1 | 24SP, 27SP, 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 251 | 94.49 | 145.48 |  |  |  | Build a new G23-025-TAP to LITCH 5 161kV line 1
03ALL | ERIS | Thermal | 532932 LITCH 5 161 547476 ASB349 5 161 1 | 24SP, 27SP, 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 262 | 104.49 | 159.06 |  |  |  | Rebuild the LITCH 5 to ASB349 5 161kV line 1
03ALL | ERIS | Thermal | 532937 NEOSHO 5 161 997416 NEOSHO TX-5 138 1 | 24SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 165 | 94.42 | 144.8 |  |  |  | Build a new RIV4525 to G20-079-TAP 161kV line 2
03ALL | ERIS | Thermal | 533020 NEOSHOS4 138 997416 NEOSHO TX-5 138 1 | 24SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 165 | 93.93 | 143.98 |  |  |  | Build a new RIV4525 to G20-079-TAP 161kV line 2
03ALL | ERIS | Thermal | 532937 NEOSHO 5 161 997414 NEOSHO TX-5 138 1 | 27SP, 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 165 | 96.24 | 147.78 |  |  |  | Build a new RIV4525 to G20-079-TAP 161kV line 2
03ALL | ERIS | Thermal | 533020 NEOSHOS4 138 997414 NEOSHO TX-5 138 1 | 27SP, 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 165 | 95.73 | 146.87 |  |  |  | Build a new RIV4525 to G20-079-TAP 161kV line 2
03ALL | ERIS | Thermal | 532932 LITCH 5 161 532938 FRANKLIN5 161 1 | 24SP, 27SP, 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 251 | 94.49 | 145.48 |  |  |  | Rebuild the LITCH 5 to FRANKLIN5 161kV line 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 24SP, 27SP, 27WP | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 293 | 42.93 | 112.88 |  |  |  | Rebuild the CARTHAG5 to CAR395 5 161kV line 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 24SP, 27SP, 27WP | 547476 ASB349 5 161 547477 CJ 366 5 161 1 |  | 293 | 42.93 | 112.88 |  |  |  | Build a new CARTHAG5 to CAR395 5 161kV line 2
03ALL | ERIS | Thermal | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | 24SP, 27SP | 640325 REDWILO3 345 767280 G22-015-TAP 345 2 |  | 966 | 55.3 | 102.52 |  |  |  | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1
03ALL | ERIS | Voltage | 533008 TV1MNDV4 138 | 27SP | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 |  |  |  |  | 0.9204 | 0.93 | 1.05 | Build a new 30 MVAR cap bank at TV1MNDV4
03ALL | ERIS | Voltage | 533003 LIBERTY4 138 | 27SP | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 |  |  |  |  | 0.9236 | 0.93 | 1.05 | Build a new 30 MVAR cap bank at TV1MNDV4
03ALL | ERIS | Voltage | 533760 ERIE 2 69 | 27SP | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 |  |  |  |  | 0.9298 | 0.93 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Thermal | 531378 HICKOCK3 115 531391 PIONEER3 115 1 | 24SP, 27SP, 27WP | P12:115:SUNC:HICKOK-RUBARTSTATION:::HV: |  | 159.3 | 23.55 | 101.17 |  |  |  | Rebuild the HICKOCK3 to PIONEER3 115kV line 1
03ALL | ERIS | Thermal | 533062 ROSEHIL4 138 533068 STEARMN4 138 1 | 24SP, 27SP | P12:138:WERE:ELPA-ROSE-138:::HV: |  | 287 | 81.5 | 105.19 |  |  |  | Rebuild the ROSEHIL4 to STEARMN4 138kV line 1
03ALL | ERIS | Thermal | 533039 ELPASO 4 138 533059 ELPASOE4 138 Z1 | 24SP, 27SP | P12:138:WERE:ROSE-WEAV-138:::HV: |  | 382 | 74.69 | 113.18 |  |  |  | Rebuild the ELPASO 4 to ROSEHIL4 138kV line 1
03ALL | ERIS | Thermal | 510402 GROVE 4 138 997990 GROVE 138 1 | 24SP | P12:161:AEPW-EMDE:FLINTCR5:739952::: |  | 112 | 36.67 | 100.06 |  |  |  | Build a new Grove 161/138 kV transformer 2
03ALL | ERIS | Thermal | 510411 GROVE 5 161 997990 GROVE 138 1 | 24SP, 27SP | P12:161:AEPW-EMDE:FLINTCR5:739952::: |  | 112 | 36.59 | 104.51 |  |  |  | Build a new Grove 161/138 kV transformer 2
03ALL | ERIS | Thermal | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | 24SP, 27SP, 27WP | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: |  | 227 | 72.05 | 133.18 |  |  |  | Rebuild the 5MOCITYB1 to ECKLES-161 161kV line 1
03ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997365 FRAN TX-1 69.0 1 | 24SP | P12:161:WERE:FRAN-LITC-161:::HV: |  | 110 | 88.03 | 147.77 |  |  |  | Build a new G23-025-TAP to LITCH 5 161kV line 1
03ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997365 FRAN TX-1 69.0 1 | 24SP | P12:161:WERE:FRAN-LITC-161:::HV: |  | 110 | 87.92 | 147.4 |  |  |  | Build a new G23-025-TAP to LITCH 5 161kV line 1
03ALL | ERIS | Thermal | 533876 FRANKLIN2 69.0 997363 FRAN TX-1 69.0 1 | 27SP, 27WP | P12:161:WERE:FRAN-LITC-161:::HV: |  | 110 | 90.12 | 149.32 |  |  |  | Build a new G23-025-TAP to LITCH 5 161kV line 1
03ALL | ERIS | Thermal | 532938 FRANKLIN5 161 997363 FRAN TX-1 69.0 1 | 27SP, 27WP | P12:161:WERE:FRAN-LITC-161:::HV: |  | 110 | 90.08 | 149.01 |  |  |  | Build a new G23-025-TAP to LITCH 5 161kV line 1
03ALL | ERIS | Thermal | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 24SP, 27SP, 27WP | P12:345:OKGE:BKRBKR357_1:::: |  | 956 | 59.37 | 125.08 |  |  |  | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1
03ALL | ERIS | Thermal | 533039 ELPASO 4 138 533062 ROSEHIL4 138 1 | 24SP, 27SP | P12:345:OKGE:BKRBKR357_1:::: |  | 382 | 74.39 | 109.78 |  |  |  | Rebuild the ELPASO 4 to ROSEHIL4 138kV line 1
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | 24SP, 27L, 27SP, 27WP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: |  | 956.1 | 87.37 | 222.59 |  |  |  | Build a new FINNEY to HOLCOMB7 345kV line 3
03ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | 24SP, 27L, 27SP, 27WP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: |  | 956.1 | 87.37 | 222.59 |  |  |  | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2
03ALL | ERIS | Thermal | 531465 SETAB 7 345 997501 SETAB 115 1 | 24SP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 298.8 | 21.01 | 102.22 |  |  |  | Build a new Setab 345/115 kV transformer 2
03ALL | ERIS | Thermal | 531464 SETAB 3 115 997501 SETAB 115 1 | 24SP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 298.8 | 20.59 | 101.22 |  |  |  | Build a new Setab 345/115 kV transformer 2
03ALL | ERIS | Thermal | 531465 SETAB 7 345 997499 SETAB 115 1 | 27L, 27SP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 298.8 | 22.65 | 100.97 |  |  |  | Build a new Setab 345/115 kV transformer 2
03ALL | ERIS | Thermal | 531464 SETAB 3 115 997499 SETAB 115 1 | 27SP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 298.8 | 22.17 | 100.82 |  |  |  | Build a new Setab 345/115 kV transformer 2
03ALL | ERIS | Thermal | 531433 SCOTCTY3 115 531464 SETAB 3 115 1 | 24SP, 27L, 27SP, 27WP | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  | 252 | 12.86 | 112.06 |  |  |  | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1
03ALL | ERIS | Thermal | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | 24SP, 27SP | P12:345:WERE:N345-AECI-345:::EHV: |  | 1176 | 58.78 | 114.81 |  |  |  | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1
03ALL | ERIS | Thermal | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 24SP, 27SP, 27WP | P12:345:WERE:N345-AECI-345:::EHV: |  | 570 | 104.39 | 154.58 |  |  |  | Build a new RIV4525 to G20-079-TAP 161kV line 2
03ALL | ERIS | Thermal | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 24SP, 27SP, 27WP | P12:345:WERE:N345-AECI-345:::EHV: |  | 570 | 104.39 | 154.58 |  |  |  | Build a new G20-079-TAP to STL439 5 161kV line 1
03ALL | ERIS | Voltage | 533763 HUDSON-2 69 | 27SP | P12:69:WERE:LITC-SPIT-69::FUTURE:HV: |  |  |  |  | 0.9017 | 0.93 | 1.05 | Build a new 10 MVAR cap bank at HUDSON-2
03ALL | ERIS | Voltage | 533773 SOPITT 2 69 | 27SP | P12:69:WERE:LITC-SPIT-69::FUTURE:HV: |  |  |  |  | 0.9049 | 0.93 | 1.05 | Build a new 10 MVAR cap bank at HUDSON-2
03ALL | ERIS | Thermal | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 27WP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 |  | 418 | 24.06 | 102.64 |  |  |  | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1
03ALL | ERIS | Thermal | 541201 SIBLEY 7 345 997289 SIBLEY11 161 11 | 27WP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 |  | 440 | 23.7 | 101.93 |  |  |  | Build a new Sibley 345/161 kV transformer 2
03ALL | ERIS | Thermal | 541201 SIBLEY 7 345 997292 SIBLEY11 161 11 | 27WP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 |  | 440 | 23.16 | 100.51 |  |  |  | Build a new Sibley 345/161 kV transformer 2
03ALL | ERIS | Thermal | 541198 PECULR 7 345 542968 STILWEL7 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL:WGARDNER-R10-12:::EHV: |  | 1195 | 89.71 | 109.95 |  |  |  | Build a new LACYGNE7 to PHILL 7 345kV line 1
03ALL | ERIS | Thermal | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: |  | 956 | 90.52 | 116.62 |  |  |  | Build a new LACYGNE7 to PHILL 7 345kV line 1
03ALL | ERIS | Thermal | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  | 1015 | 95.34 | 134.86 |  |  |  | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1
03ALL | ERIS | Thermal | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  | 1015 | 95.37 | 103.06 |  |  |  | Build a new LACYGNE7 to PHILL 7 345kV line 1
03ALL | ERIS | Thermal | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  | 1015 | 95.37 | 103.06 |  |  |  | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1
03ALL | ERIS | Thermal | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  | 1792 | 130.76 | 143.51 |  |  |  | Build a new LACYGNE7 to PHILL 7 345kV line 1
03ALL | ERIS | Thermal | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  | 1792 | 130.76 | 126.9 |  |  |  | Build a new LACYGNE7 to PHILL 7 345kV line 1
03ALL | ERIS | Thermal | 531451 MINGO 7 345 531465 SETAB 7 345 1 | 24SP, 27SP, 27WP | P23:345:SUNC:HLC_BRK282:::EHV: |  | 1195.1 | 9.4 | 121.3 |  |  |  | Rebuild the MINGO 7 to SETAB 7 345kV line 1
03ALL | ERIS | Thermal | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | 27SP | P23:345:WERE:N345-345-20:::EHV: |  | 956 | 66.56 | 100.05 |  |  |  | Rebuild the ROSEHIL7 to LATHAMS7 345kV line 1
03ALL | ERIS | Voltage | 773480 G23-075-TAP 345 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9203 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 773481 GEN-2023-075 345 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9203 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 773488 G23-075XFMRH 345 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9203 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 773501 GEN-2023-076 345 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9203 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 765100 GEN-2020-052 345 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9254 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 765110 G20-052-TAP 345 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9254 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 768820 G22-092-TAP 345 | 27SP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9125 | 0.92 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 768821 GEN-2022-092 345 | 27SP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9125 | 0.92 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 510380 DELWARE7 345 | 27SP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9134 | 0.92 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 765350 GEN-2021-006 345 | 27SP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9491 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 532793 NEOSHO 7 345 | 27SP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9491 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Voltage | 772981 GEN-2023-050 345 | 27SP | P42:345:OKGE:SB_SOER7383:::: |  |  |  |  | 0.9492 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03ALL | ERIS | Thermal | 509771 LLAN ET4 138 509790 CATOOSA4 138 1 | 24SP, 27SP | System Intact | 216 |  | 55.17 | 131.28 |  |  |  | Rebuild the LLAN ET4 to CATOOSA4 138kV line 1
03ALL | ERIS | Thermal | 509771 LLAN ET4 138 509886 E41ST_W4 138 1 | 24SP, 27SP | System Intact | 221 |  | 47.76 | 121.71 |  |  |  | Rebuild the LLAN ET4 to E41ST_W4 138kV line 1
03ALL | ERIS | Thermal | 509779 MAYO--N4 138 509886 E41ST_W4 138 1 | 24SP, 27SP | System Intact | 221 |  | 40.92 | 114.3 |  |  |  | Rebuild the MAYO--N4 to E41ST_W4 138kV line 1
03ALL | ERIS | Thermal | 509760 MINGO-N4 138 509779 MAYO--N4 138 1 | 24SP, 27SP | System Intact | 221 |  | 30.23 | 103.33 |  |  |  | Rebuild the MINGO-N4 to MAYO--N4 138kV line 1
03ALL | ERIS | Thermal | 541251 MARYVLE5 161 635034 CLRNDA 5 161 1 | 24SP, 27SP | System Intact | 152 |  | 82.71 | 126.53 |  |  |  | Rebuild the MARYVLE5 to CLRNDA 5 161kV line 1
03ALL | ERIS | Thermal | 547473 RDS295 5 161 763696 G19-035-TAP 161 1 | 27WP | System Intact | 167 |  | 72.12 | 106.3 |  |  |  | Rebuild the RDS295 5 to G19-035-TAP 161kV line 1
03ALL | ERIS | Thermal | 547468 AUR124 5 161 763696 G19-035-TAP 161 1 | 27WP | System Intact | 167 |  | 68.6 | 102.66 |  |  |  | Rebuild the AUR124 5 to G19-035-TAP 161kV line 1
03ALL | ERIS | Voltage | 770500 G22-176-TAP 345 | 27SP | System Intact |  |  |  |  | 0.9491 | 0.95 | 1.05 | Build a new 300 MVAR cap bank at DELWARE7
03NR | NRIS | Non-Converge | None | 27L | None | [7 empty] | None
03NR | NRIS | Thermal | None | 27L | None | [7 empty] | None
01NR | NRIS | Non-Converge | None | 27L | [8 empty] | None
01NR | NRIS | Thermal | None | 27L | None | [7 empty] | None
01NR | NRIS | Voltage | None | 27L | [8 empty] | None
02NR | NRIS | Thermal | None | 27L | None | [7 empty] | None
02NR | NRIS | Voltage | None | 27L | [8 empty] | None
02NR | NRIS | Non-Converge | None | 27L | [8 empty] | None
02ALL | ERIS | Voltage | None | 24SP, 27SP, 27WP, 27L | None | [7 empty] | None
03NR | NRIS | Voltage | None | 27L | None | [7 empty] | None
WECC | ERIS | Thermal | None | 23SP, 28WP, 28SP | None | [7 empty] | None
WECC | ERIS | Voltage | None | 23SP, 28WP, 28SP | [8 empty] | None
WECC | ERIS | Non-Converge | None | 28SP | [8 empty] | None
WECC | ERIS | Non-Converge | Non-Converge | 23SP, 28WP | DISCONNECT BRANCH FROM BUS 623174 TO BUS 623210 CKT 1 DISCONNECT BRANCH FROM BUS 623181 TO BUS 623210 CKT 1 | [7 empty] | Columbus 230kV Subsystem Reconfiguration
04ALL | ERIS | Non-Converge | Non-Converged | 24SP | P42:345:OKGE:SB_RARD7383:::: | [7 empty] | Build a new HANNA to WELEETK 138kV line 1
04ALL | ERIS | Non-Converge | Non-Converged | 24SP,27SP,27WP,27L | 520886 DUSTIN 4 138 520932 HANNA 4 138 1 | [7 empty] | Build a new HANNA to WELEETK 138kV line 1
04ALL | ERIS | Non-Converge | Non-Converged | 24SP,27SP,27WP,27L | 520886 DUSTIN 4 138 521026 PHAROAH4 138 1 | [7 empty] | Build a new HANNA to WELEETK 138kV line 1
05ALL | ERIS | Non-Converge | Non-Converged | 24SP,27SP,27WP | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | [7 empty] | Build a new TOLK to NEEDMORE 230kV line 2
00ALL | ERIS | Thermal | 645455 S3455 3 345 645740 S3740 3 345 1 | 24SP,27SP,27WP | P12:345:OPPD:LX008::S3458.S3740.CKT1:: |  | 1195 | 103.08 | 151.93 |  |  |  | Rebuild the S3455 to S3740 345kV line 1
00ALL | ERIS | Thermal | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: |  | 140 | 27.8 | 244.28 |  |  |  | Rebuild the BPSSUB7 to CLATONA7 115kV line 1
00ALL | ERIS | Thermal | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 24SP,27SP,27WP | 640088 BPS SUB7 115 640111 CLATONA7 115 1 |  | 193 | 23.94 | 196.8 |  |  |  | Rebuild the BPSSUB7 to SHELDON7 115kV line 1
00ALL | ERIS | Thermal | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: |  | 137 | 35.18 | 240.16 |  |  |  | Rebuild the CLATONA7 to SHELDON 7 115kV line 1
00ALL | ERIS | Thermal | 645458 S3458 3 345 645740 S3740 3 345 1 | 24SP | P12:345:OPPD:S3455-S3740:::EHV: |  | 1073 | 115.26 | 169.63 |  |  |  | New Line - S3454 - S3740 345 kV
00ALL | ERIS | Thermal | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 24SP,27SP,27WP | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 |  | 193 | 37.87 | 150.87 |  |  |  | Rebuild the BPSSUB7 to BEATRCE7 115kV line 1
00ALL | ERIS | Thermal | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 24SP,27SP,27WP | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 |  | 193 | 38.06 | 151.57 |  |  |  | Rebuild the BPSSUB7 to BEATRCE7 115kV line 2
00ALL | ERIS | Thermal | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: |  | 219 | 38.81 | 105.04 |  |  |  | Rebuild the ROKHILL4 to G23-059-TAP 138kV line 1
00ALL | ERIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 24SP,27SP | 640076 BEATRCE7 115 640208 HARBINE7 115 2 |  | 139 | 13.04 | 103.58 |  |  |  | Build a new BPSSUB7 to HARBINE7 115kV line 1
04ALL | ERIS | Thermal | 300686 4WOODY 138 521026 PHAROAH4 138 1 | 24SP,27SP | P12:138:SWPA-AEPW:WELEETK4:WELETK4::: |  | 174 | 39.78 | 138.93 |  |  |  | Rebuild the 4WOODY to PHAROAH4 138kV line 1
04ALL | ERIS | Thermal | 505552 GORE 5 161 505558 MUSKTAP5 161 1 | 24SP,27SP | P12:161:OKGE-SWPA:BKRBKR2:::: |  | 201 | 32.71 | 119.34 |  |  |  | Rebuild the GORE5 to MUSKTAP5 161kV line 1
04ALL | ERIS | Thermal | 505592 WELEETK4 138 505595 GREASYC4 138 1 | 24SP,27SP,27WP,27L | P12:138:OKGE-SWPA-AEPW-WFEC:BKRBKR278:::: |  | 147 | 33.32 | 187.72 |  |  |  | Rebuild the WELEETK4 to GREASYC4 138kV line 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 521071 STNWLSW4 138 1 | 24SP,27SP,27WP | 515192 LULA 4 138 772741 GEN-2023-038 138 1 |  | 169 | 73.51 | 188.27 |  |  |  | Rebuild the TUPELO4 to STNWLSW4 138kV line 1
04ALL | ERIS | Thermal | 505602 S BROWN4 138 772380 G23-020-TAP 138 1 | 24SP,27SP,27WP | P12:138:OKGE:BKRBKR261:::: |  | 136 | 85.72 | 256.26 |  |  |  | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1
04ALL | ERIS | Thermal | 515120 RUSSET-4 138 521044 RUSSETT4 138 1 | 24SP,27SP,27WP | 515151 LTLCITY4 138 515152 BROWNTP4 138 1 |  | 222 | 87.98 | 253.53 |  |  |  | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 Build a new RUSSET-4 to RUSSETT4 138kV line 2 Build a new RUSSET-4 to RUSSETT4 138kV line 3
04ALL | ERIS | Thermal | 520969 LASALLE4 138 520971 LATTAJT4 138 1 | 24SP,27SP | P12:138:OKGE:BKRBKR277:::: |  | 169 | 44.57 | 112.51 |  |  |  | Rebuild the LASALLE4 to LATTAJT4 138kV line 1
04ALL | ERIS | Thermal | 520969 LASALLE4 138 521075 STNWLTP4 138 1 | 24SP,27SP | P12:138:OKGE:BKRBKR277:::: |  | 169 | 47.42 | 116.57 |  |  |  | Rebuild the LASALLE4 to STNWLTP4 138kV line 1
04ALL | ERIS | Thermal | 521044 RUSSETT4 138 772380 G23-020-TAP 138 1 | 24SP,27SP,27WP | P12:138:OKGE:BKRBKR261:::: |  | 136 | 86.1 | 404.65 |  |  |  | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 510881 ALLENGT4 138 1 | 24SP,27SP,27WP | 520448 BOGYDPT4 138 773360 G23-069-TAP 138 1 |  | 152 | 76.43 | 179.68 |  |  |  | Rebuild the TUPELO4 to ALLENGT4 138kV line 1
04ALL | ERIS | Thermal | 515150 CANEYCK4 138 515151 LTLCITY4 138 1 | 24SP,27SP,27WP | 521044 RUSSETT4 138 772380 G23-020-TAP 138 1 |  | 222 | 86.9 | 208.42 |  |  |  | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1
04ALL | ERIS | Thermal | 515151 LTLCITY4 138 515152 BROWNTP4 138 1 | 24SP,27SP,27WP | 521044 RUSSETT4 138 772380 G23-020-TAP 138 1 |  | 222 | 87.8 | 212.05 |  |  |  | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1
04ALL | ERIS | Thermal | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 24SP,27SP,27WP | 521044 RUSSETT4 138 772380 G23-020-TAP 138 1 |  | 153 | 8.18 | 307.15 |  |  |  | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1
04ALL | ERIS | Thermal | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 24SP,27SP,27WP | 521044 RUSSETT4 138 772380 G23-020-TAP 138 1 |  | 153 | 7.86 | 312.36 |  |  |  | Rebuild the BROWN4 to STRRDTP4 138kV line 1
04ALL | ERIS | Thermal | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 | 24SP,27SP,27WP | P12:138:OKGE:BKRBKR344:::: |  | 153 | 78.4 | 177.57 |  |  |  | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1
04ALL | ERIS | Thermal | 515172 SPRNDAL4 138 515873 DRPSPRG4 138 1 | 24SP,27SP,27WP | P12:138:OKGE:BKRBKR344:::: |  | 153 | 81.79 | 164.65 |  |  |  | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1
04ALL | ERIS | Thermal | 515189 AOCPA 2 69.0 515190 AOCPT 2 69.0 1 | 24SP,27SP,27WP | 515192 LULA 4 138 515699 EFITSTP4 138 1 |  | 56 | 9.09 | 166.52 |  |  |  | Rebuild the ACOPA2 to ACOPT2 69kV line 1
04ALL | ERIS | Thermal | 515191 LULA 2 69.0 997839 LULA1 69.0 1 | 24SP,27SP,27WP | 515192 LULA 4 138 515699 EFITSTP4 138 1 |  | 67 | 52.42 | 160.61 |  |  |  | Upgrade the LULA4 138/69 kV transformer 1
04ALL | ERIS | Thermal | 515192 LULA 4 138 997839 LULA1 69.0 1 | 24SP,27SP,27WP | 515192 LULA 4 138 515699 EFITSTP4 138 1 |  | 67 | 53.09 | 159.28 |  |  |  | Upgrade the LULA4 138/69 kV transformer 1
04ALL | ERIS | Thermal | 515873 DRPSPRG4 138 515932 STIRLNG4 138 1 | 24SP,27SP,27WP | P12:138:OKGE:BKRBKR344:::: |  | 153 | 80.28 | 169.11 |  |  |  | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1
04ALL | ERIS | Thermal | 520814 ANADARK4 138 521129 CHERRYRD 4 138 1 | 24SP,27SP,27WP | P12:138:WFEC:CHERRYRD_SNYDR_GRANDFLD:::: |  | 169 | 67.3 | 183.67 |  |  |  | Rebuild the ANADARK4 to CHERRYRD4 138kV line 1
04ALL | ERIS | Thermal | 520939 HLDTNTP4 138 520981 LOCO 4 138 1 | 24SP,27SP,27WP | System Intact | 117 |  | 27 | 148.31 |  |  |  | Rebuild the HLDTNTP4 to LOCO4 138kV line 1
04ALL | ERIS | Thermal | 510402 GROVE 4 138 775220 G23-162-TAP 138 1 | 24SP,27SP,27WP | 510419 PRY-JCT4 138 772520 G23-027-TAP 138 1 |  | 151 | 9.55 | 152.28 |  |  |  | Rebuild the GROVE4 to G23-162-TAP 138kV line 1
04ALL | ERIS | Thermal | 510402 GROVE 4 138 997990 GROVE 138 1 | 24SP,27SP,27WP | 510419 PRY-JCT4 138 772520 G23-027-TAP 138 1 |  | 112 | 4.13 | 167.23 |  |  |  | Build a new GROVE 161/138 kV transformer 2 Build a new GROVE 161/138 kV transformer 3
04ALL | ERIS | Thermal | 510411 GROVE 5 161 997990 GROVE 138 1 | 24SP,27SP,27WP | 510419 PRY-JCT4 138 772520 G23-027-TAP 138 1 |  | 112 | 4.12 | 168.77 |  |  |  | Build a new GROVE 161/138 kV transformer 2 Build a new GROVE 161/138 kV transformer 3
04ALL | ERIS | Thermal | 547471 NEO184 5 161 547496 NOL435 5 161 1 | 24SP,27SP,27WP | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: |  | 223 | 75.68 | 141.89 |  |  |  | Rebuild the NEO1845 to NOL4355 161kV line 1
04ALL | ERIS | Thermal | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 24SP,27SP,27WP | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: |  | 194 | 75.84 | 153.91 |  |  |  | Rebuild the MIAMI5 to AFTON5 161kV line 1
04ALL | ERIS | Thermal | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 24SP,27SP,27WP | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: |  | 194 | 84.09 | 166.88 |  |  |  | Rebuild the AFTON5 to KETCHUM5 161kV line 1
04ALL | ERIS | Thermal | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 24SP,27SP,27WP | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: |  | 194 | 88.92 | 173.52 |  |  |  | Rebuild the PENSA5 to KETCHUM5 161kV line 1
04ALL | ERIS | Thermal | 547467 ORO110 5 161 547469 RIV4525 161 1 | 24SP,27SP | 547469 RIV4525 161 547498 STL439 5 161 1 |  | 279 | 95.1 | 162.19 |  |  |  | Rebuild the ORO110 5 to RIV4525 161kV line 1
04ALL | ERIS | Thermal | 505552 GORE 5 161 774880 G23-145-TAP 161 1 | 24SP,27SP,27WP | 505582 RS KERR5 161 773260 G23-064-TAP 161 1 |  | 181 | 9.48 | 175.26 |  |  |  | Rebuild the GORE5 to G23-145-TAP 161kV line 1
04ALL | ERIS | Thermal | 508067 NEWBOST2 69.0 508068 NNBOSTN2 69.0 1 | 24SP,27SP,27WP | 508069 NNBOSTN4 138 508104 RIFFIN REC4 138 1 |  | 86 | 84.9 | 131.92 |  |  |  | Rebuild the NEWBOST2 to NNBOSTN2 69kV line 1
04ALL | ERIS | Thermal | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 | 24SP,27SP,27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: |  | 191 | 98.35 | 165.91 |  |  |  | Rebuild the NNBOSTN4 to G18-003-TAP 138kV line 1
04ALL | ERIS | Thermal | 505590 WELEETK5 161 998095 WLK X1 138 1 | 27WP,27L | 301551 4CHECOTA 138 505592 WELEETK4 138 1 |  | 120 | 97.53 | 129.06 |  |  |  | Upgrade the WELEETK5 161/138 kV transformer 1
04ALL | ERIS | Thermal | 505592 WELEETK4 138 998095 WLK X1 138 1 | 27WP,27L | 301551 4CHECOTA 138 505592 WELEETK4 138 1 |  | 120 | 97.27 | 128.79 |  |  |  | Upgrade the WELEETK5 161/138 kV transformer 1
04ALL | ERIS | Thermal | 515336 VBI 2 69.0 997817 VBI2 69.0 2 | 27SP | System Intact | 76 |  | 89 | 102.32 |  |  |  | Upgrade the VBI 161/69 kV transformer 2
04ALL | ERIS | Thermal | 515339 VBI 5 161 997817 VBI2 69.0 2 | 27SP | System Intact | 76 |  | 89 | 102.37 |  |  |  | Upgrade the VBI 161/69 kV transformer 2
04ALL | ERIS | Thermal | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 24SP,27SP,27WP | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 |  | 335 | 9.51 | 134.67 |  |  |  | Rebuild the VANBUR5 to VBI5 161kV line Z1
04ALL | ERIS | Thermal | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | 27WP | System Intact | 266 |  | 73 | 102.97 |  |  |  | Rebuild the AVOCA5 to EROGERS5 161kV line 1
04ALL | ERIS | Thermal | 505592 WELEETK4 138 510902 WELETK4 138 1 | 24SP,27SP | P12:138:WFEC:PHAROAH_WOODY:::: |  | 235 | 9.52 | 122.32 |  |  |  | Rebuild the WELEETK4 to WELETK4 138kV line 1
04ALL | ERIS | Thermal | 505595 GREASYC4 138 505596 EXPLOR 4 138 1 | 24SP,27SP,27L | P12:138:SWPA:WELEETKA-GREASY CREEK::505592 505595 1, 505595:: |  | 147 | 0.3 | 135.17 |  |  |  | Rebuild the GREASYC4 to EXPLOR4 138kV line 1
04ALL | ERIS | Thermal | 505596 EXPLOR 4 138 505598 ALLEN 4 138 1 | 24SP,27SP,27L | P12:138:SWPA:WELEETKA-GREASY CREEK::505592 505595 1, 505595:: |  | 147 | 7.55 | 126.64 |  |  |  | Rebuild the EXPLOR4 to ALLEN4 138kV line 1
04ALL | ERIS | Thermal | 505598 ALLEN 4 138 505600 TUPELO 4 138 1 | 24SP,27SP,27L | P12:138:SWPA:WELEETKA-GREASY CREEK::505592 505595 1, 505595:: |  | 147 | 8.34 | 118.85 |  |  |  | Rebuild the ALLEN4 to TUPELO4 138kV line 1
04ALL | ERIS | Thermal | 511435 SNYDER-4 138 521052 SNYDER 4 138 1 | 24SP,27SP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 234 | 81.01 | 117.23 |  |  |  | Rebuild the SNYDER-4 to SNYDER4 138kV line 1
04ALL | ERIS | Thermal | 520404 MDCPRK4 138 521024 PARADSE4 138 1 | 24SP,27SP,27WP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 169 | 66.31 | 178.63 |  |  |  | Rebuild the MDCPRK4 to PARADSE4 138kV line 1
04ALL | ERIS | Thermal | 520404 MDCPRK4 138 521190 CACHEJ4 138 1 | 24SP,27SP,27WP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 169 | 65.01 | 171.91 |  |  |  | Rebuild the MDCPRK4 to CACHEJ4 138kV line 1
04ALL | ERIS | Thermal | 521024 PARADSE4 138 521129 CHERRYRD 4 138 1 | 24SP,27SP,27WP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 169 | 66.81 | 182.14 |  |  |  | Rebuild the PARADSE4 to CHERRYRD4 138kV line 1
04ALL | ERIS | Thermal | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1 | 24SP,27SP,27WP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 169 | 37.81 | 125.32 |  |  |  | Rebuild the CACHEJ5 to G20-016-TAP 138kV 1
04ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515120 RUSSET-4 138 1 | 24SP,27SP,27WP | 515120 RUSSET-4 138 515932 STIRLNG4 138 1 |  | 287 | 9.47 | 117.01 |  |  |  | Rebuild the JOHNCO4 to RUSSET4 138kV line 1
04ALL | ERIS | Thermal | 515120 RUSSET-4 138 515147 GLASSES4 138 1 | 24SP,27SP,27WP | 521044 RUSSETT4 138 772380 G23-020-TAP 138 1 |  | 176 | 66.05 | 110.8 |  |  |  | Rebuild the RUSSET4 to GLASSES4 138kV line 1
04ALL | ERIS | Thermal | 515149 MADINDT4 138 515150 CANEYCK4 138 1 | 24SP,27SP,27WP | 521044 RUSSETT4 138 772380 G23-020-TAP 138 1 |  | 153 | 8.84 | 156.36 |  |  |  | Rebuild the MADINDT4 to CANEYCK4 138kV line 1
04ALL | ERIS | Thermal | 515162 FNDTION4 138 515172 SPRNDAL4 138 1 | 24SP,27SP | P12:138:OKGE:BKRBKR344:::: |  | 153 | 53.84 | 123.62 |  |  |  | Rebuild the FNDTION4 to SPRNDAL4 138kV line 1
04ALL | ERIS | Thermal | 510419 PRY-JCT4 138 772520 G23-027-TAP 138 1 | 24SP,27SP,27WP | 510402 GROVE 4 138 775220 G23-162-TAP 138 1 |  | 216 | 6.66 | 107.84 |  |  |  | Rebuild the PRY-JCT4 to G23-027-TAP 138kV line 1
04ALL | ERIS | Thermal | 512635 KERR GR5 161 512648 MAID 5 161 1 | 24SP,27SP | P12:161:GRDA:KERR GR5-MAID-2 5:::HV: |  | 198 | 8.53 | 110.37 |  |  |  | Build a new KERRGR5 to MAID5 161kV line 3
04ALL | ERIS | Thermal | 512635 KERR GR5 161 512648 MAID 5 161 2 | 24SP,27SP | P12:161:GRDA:KERR GR5-MAID 5-1:::HV: |  | 198 | 8.53 | 110.34 |  |  |  | Build a new KERRGR5 to MAID5 161kV line 3
04ALL | ERIS | Thermal | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 24SP,27SP,27WP | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 |  | 335 | 0.68 | 112.56 |  |  |  | Rebuild the DRYGULCH5 to G23-028-TAP 161kV line 1
04ALL | ERIS | Thermal | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 24SP,27SP,27WP | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: |  | 335 | 20.01 | 132.33 |  |  |  | Rebuild the PENSA5 to G23-049-TAP 161kV line 1
04ALL | ERIS | Thermal | 510387 ADAIR--2 69.0 510404 VINITA-2 69.0 1 | 24SP,27SP | P12:69:AEPW:VINITA-2:VINTAJC2::: |  | 50 | 53.51 | 103.16 |  |  |  | Rebuild the ADAIR2 to VINITA 2 line 69kV
04ALL | ERIS | Thermal | 510400 PRY-JCT2 69.0 512810 PRYORC12 69.0 1 | 24SP,27SP,27WP | 510402 GROVE 4 138 775220 G23-162-TAP 138 1 |  | 72 | 50.34 | 127.56 |  |  |  | Rebuild the PRY-JCT2 to PRYORC12 69kV line 1
04ALL | ERIS | Thermal | 511458 ELKCTY-4 138 511485 CLINTJC4 138 1 | 24SP,27SP,27WP | 511548 REDROCKRD4 138 773000 G23-051-TAP 138 1 |  | 152 | 8.53 | 126.64 |  |  |  | Build a new ELKCITY to G22-145-TAP 138kV line 1
04ALL | ERIS | Thermal | 511485 CLINTJC4 138 511534 CL-NGTP4 138 1 | 24SP,27SP,27WP | 511548 REDROCKRD4 138 773000 G23-051-TAP 138 1 |  | 173 | 9.23 | 140.4 |  |  |  | Build a new ELKCITY to G22-145-TAP 138kV line 1
04ALL | ERIS | Thermal | 511489 WTH_JCT4 138 769880 G22-145-TAP 138 1 | 24SP,27SP,27WP | 511548 REDROCKRD4 138 773000 G23-051-TAP 138 1 |  | 278 | 67.79 | 120.22 |  |  |  | Build a new ELKCITY to G22-145-TAP 138kV line 1
04ALL | ERIS | Thermal | 511497 WTH_SE 4 138 511536 WEATHTP4 138 1 | 24SP,27SP | 511548 REDROCKRD4 138 773000 G23-051-TAP 138 1 |  | 239 | 59.6 | 113.06 |  |  |  | Build a new ELKCITY to G22-145-TAP 138kV line 1
04ALL | ERIS | Thermal | 511540 CAN_GAS4 138 514821 JENSEN 4 138 1 | 24SP,27SP,27WP | 511489 WTH_JCT4 138 769880 G22-145-TAP 138 1 |  | 191 | 62.92 | 124.24 |  |  |  | Build a new ELKCITY to G22-145-TAP 138kV line 1
04ALL | ERIS | Thermal | 505582 RS KERR5 161 773260 G23-064-TAP 161 1 | 24SP,27SP,27WP | 505552 GORE 5 161 774880 G23-145-TAP 161 1 |  | 237 | 9.36 | 123.23 |  |  |  | Rebuild the RSKERR5 to G23-064-TAP 161kV line 1
04ALL | ERIS | Thermal | 515192 LULA 4 138 521071 STNWLSW4 138 1 | 24SP,27SP | 515192 LULA 4 138 772741 GEN-2023-038 138 1 |  | 234 | 9.89 | 104.64 |  |  |  | Rebuild the LULA4 to STNWLSW4 138kV line 1
04ALL | ERIS | Thermal | 510874 MCGEETP2 69.0 510915 ANTLTAP2 69.0 1 | 24SP,27SP,27WP | 510891 LANE 2 69.0 773380 G23-070-TAP 69.0 1 |  | 39 | 4.35 | 125.76 |  |  |  | Rebuild the MCGEETP2 to ANTLTAP2 69kV line 1
04ALL | ERIS | Thermal | 510874 MCGEETP2 69.0 773380 G23-070-TAP 69.0 1 | 24SP,27SP,27WP | 510891 LANE 2 69.0 773380 G23-070-TAP 69.0 1 |  | 39 | 0.29 | 130.96 |  |  |  | Rebuild the MCGEETP2 to G23-070-TAP 69kV line 1
04ALL | ERIS | Thermal | 510882 ATOKA--2 69.0 510891 LANE 2 69.0 1 | 24SP,27SP,27WP | 510874 MCGEETP2 69.0 773380 G23-070-TAP 69.0 1 |  | 39 | 4.01 | 122.77 |  |  |  | Rebuild the ATOKA-2 to LANE2 69kV line 1
04ALL | ERIS | Thermal | 510891 LANE 2 69.0 773380 G23-070-TAP 69.0 1 | 24SP,27SP,27WP | 510874 MCGEETP2 69.0 773380 G23-070-TAP 69.0 1 |  | 39 | 0.4 | 129.61 |  |  |  | Rebuild the LANE2 to G23-070-TAP 69kV line 1
04ALL | ERIS | Thermal | 510894 VALYTIM2 69.0 510915 ANTLTAP2 69.0 1 | 24SP,27SP | 510891 LANE 2 69.0 773380 G23-070-TAP 69.0 1 |  | 39 | 8.16 | 103.91 |  |  |  | Rebuild the VALYTIM2 to ANTLTAP2 69kV line 1
04ALL | ERIS | Thermal | 520886 DUSTIN 4 138 520932 HANNA 4 138 1 | 24SP | 505592 WELEETK4 138 520932 HANNA 4 138 1 |  | 286 | 34.89 | 100.42 |  |  |  | Rebuild the DUSTIN4 to HANNA4 138kV line 1
04ALL | ERIS | Thermal | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 24SP,27SP | 505418 JONESBO5 161 774620 G23-132-TAP 161 1 |  | 205 | 5.59 | 108.44 |  |  |  | Rebuild the 5HEBERN# to GREERSF5 161kV line 1
04ALL | ERIS | Thermal | 300829 2J6 69.0 512620 AFTP TP2 69.0 1 | 24SP,27SP,27WP | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: |  | 88 | 67.47 | 130.63 |  |  |  | Rebuild the 2J6 to AFTPTP2 69kV line 1
04ALL | ERIS | Thermal | 300829 2J6 69.0 512673 VINEOTP2 69.0 1 | 24SP,27SP,27WP | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: |  | 88 | 68.91 | 132.76 |  |  |  | Rebuild the 2J6 to VINEOTP2 69kV line 1
04ALL | ERIS | Thermal | 512620 AFTP TP2 69.0 512672 EXPL TP2 69.0 1 | 24SP,27SP,27WP | P13:138-161:EMDE:HOCKERVILLE_138-161_AUTO::HOC404_AUTO:: |  | 88 | 67.03 | 129.16 |  |  |  | Rebuild the AFTPTP2 to EXPLTP2 69kV line 1
04ALL | ERIS | Thermal | 547486 HOC404 4 138 547487 HOC404 5 161 1 | 24SP,27SP,27WP | 547486 HOC404 4 138 547487 HOC404 5 161 2 |  | 165 | 48.16 | 111.76 |  |  |  | Build a new HOC404 161/138 kV transformer 3
04ALL | ERIS | Thermal | 547486 HOC404 4 138 547487 HOC404 5 161 2 | 24SP,27SP,27WP | 547486 HOC404 4 138 547487 HOC404 5 161 1 |  | 165 | 48.16 | 111.76 |  |  |  | Build a new HOC404 161/138 kV transformer 3
04ALL | ERIS | Thermal | 508070 NWT-BNT4 138 762431 G18-003-TAP 138 1 | 24SP,27SP,27WP | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 286 | 52.1 | 104 |  |  |  | Rebuild the NWT-BNT4 to G18-003-TAP 138kV line 1
04ALL | ERIS | Thermal | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 | 24SP,27SP,27WP | 521043 RUSSELL4 138 774940 G23-148-TAP 138 1 |  | 107 | 1.78 | 102.2 |  |  |  | Rebuild the LAKE4WPT to G23-148-TAP 138kV line 1
04ALL | ERIS | Thermal | 521042 RUSSELL2 69.0 997733 RUSSELL 69.0 1 | 24SP | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 |  | 41.7 | 80.59 | 148.64 |  |  |  | Upgrade the RUSSELL2 138/69 kV transformer 1
04ALL | ERIS | Thermal | 521043 RUSSELL4 138 774940 G23-148-TAP 138 1 | 24SP,27SP,27WP | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 |  | 107 | 2.04 | 102.38 |  |  |  | Rebuild the RUSSEL4 to G23-148-TAP 138kV line 1
04ALL | ERIS | Thermal | 521043 RUSSELL4 138 997733 RUSSELL 69.0 1 | 24SP | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 |  | 41.7 | 80.44 | 148.17 |  |  |  | Upgrade the RUSSELL2 138/69 kV transformer 1
04ALL | ERIS | Thermal | 510887 ATOKA--4 138 510895 LEHIGH-4 138 1 | 24SP,27SP,27WP | 505600 TUPELO 4 138 510881 ALLENGT4 138 1 |  | 152 | 85.19 | 173.76 |  |  |  | Rebuild the ATOKA-4 to LEHIGH-4 138kV line 1
04ALL | ERIS | Thermal | 515163 ROCKYPT2 69.0 515676 MRIETAT2 69.0 1 | 24SP | 521038 RINGLNG4 138 775100 G23-156-TAP 138 1 |  | 43 | 2.68 | 128.42 |  |  |  | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild
04ALL | ERIS | Thermal | 520559 MRTA34_2 69.0 520987 MARIETA2 69.0 1 | 24SP | 521038 RINGLNG4 138 775100 G23-156-TAP 138 1 |  | 68 | 35.65 | 109.94 |  |  |  | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild
04ALL | ERIS | Thermal | 520987 MARIETA2 69.0 997738 MARIETTA 69.0 1 | 24SP | 521038 RINGLNG4 138 775100 G23-156-TAP 138 1 |  | 70 | 29.45 | 112.07 |  |  |  | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild
04ALL | ERIS | Thermal | 520988 MARIETA4 138 997738 MARIETTA 69.0 1 | 24SP | 521038 RINGLNG4 138 775100 G23-156-TAP 138 1 |  | 70 | 29.65 | 110.1 |  |  |  | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild
04ALL | ERIS | Thermal | 520888 PAYNESW4 138 521023 PAOLI 4 138 1 | 24SP,27SP | 520973 LEXNGTN4 138 521023 PAOLI 4 138 1 |  | 169 | 9.59 | 107.63 |  |  |  | Rebuild the PAYNESW4 to PAOLI4 138kV line 1
04ALL | ERIS | Thermal | 515152 BROWNTP4 138 515155 BODLE 4 138 1 | 24SP,27SP | 515157 BROWN 4 138 515944 STRRDTP4 138 1 |  | 153 | 60.8 | 116.04 |  |  |  | Rebuild the BROWNTP4 to BODLE4 138kV line 1
04ALL | ERIS | Thermal | 515193 COLBRT-4 138 520860 COLBERT4 138 1 | 24SP,27SP | 520446 KRSEY1_4 138 520860 COLBERT4 138 1 |  | 222 | 79.84 | 102.04 |  |  |  | Rebuild the COLBRT-4 to COLBERT4 138kV line 1
04ALL | ERIS | Thermal | 506944 CHAMSPR5 161 998082 CHAMSPR 161 1 | 24SP,27SP,27WP | P13:161-345:AEPW:TONTITN5:::: |  | 675 | 99.93 | 116.94 |  |  |  | Build a new CHAMSPR5 345/161 kV transformer 2
04ALL | ERIS | Thermal | 506945 CHAMSPR7 345 998082 CHAMSPR 161 1 | 24SP,27SP,27WP | P13:161-345:AEPW:TONTITN5:::: |  | 675 | 98.99 | 116.41 |  |  |  | Build a new CHAMSPR5 345/161 kV transformer 2
04ALL | ERIS | Thermal | 506957 TONTITN5 161 998080 TONTITN5 161 1 | 24SP,27SP,27WP | P13:161-345:AEPW:CHAMSPR5:::: |  | 675 | 99.95 | 117.21 |  |  |  | Build a new TONTITN7 345/161 kV transformer 2
04ALL | ERIS | Thermal | 506959 TONTITN7 345 998080 TONTITN5 161 1 | 24SP,27SP,27WP | P13:161-345:AEPW:CHAMSPR5:::: |  | 675 | 98.66 | 115.96 |  |  |  | Build a new TONTITN7 345/161 kV transformer 2
04ALL | ERIS | Thermal | 510408 PCP-TAP2 69.0 510416 HUNTAP-2 69.0 1 | 24SP,27SP | P12:069:GRDA:PRYORC32-PRYORC12:::HV: |  | 30 | 9.43 | 106.68 |  |  |  | Rebuild the PCP-TAP2 to HUNTAP-2 69kV line 1
04ALL | ERIS | Thermal | 510408 PCP-TAP2 69.0 512810 PRYORC12 69.0 1 | 24SP,27SP | P12:069:GRDA:PRYORC32-PRYORC12:::HV: |  | 30 | 9.99 | 122.57 |  |  |  | Rebuild the PCP-TAP2 to PRYORC12 69kV line 1
04ALL | ERIS | Thermal | 521042 RUSSELL2 69.0 997731 RUSSELL 69.0 1 | 27SP,27WP | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 |  | 41.7 | 80.38 | 149.16 |  |  |  | Upgrade the RUSSELL2 138/69 kV transformer 1
04ALL | ERIS | Thermal | 521043 RUSSELL4 138 997731 RUSSELL 69.0 1 | 27SP,27WP | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 |  | 41.7 | 80.21 | 148.69 |  |  |  | Upgrade the RUSSELL2 138/69 kV transformer 1
04ALL | ERIS | Thermal | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | 27WP | P12:138:WFEC:HUGO_VALIANT:::: |  | 478 | 8.17 | 106.8 |  |  |  | Build a new HUGOITC4 to HUGOPP4 138kV line 2
04ALL | ERIS | Thermal | 520560 HUGOITC4 138 997722 HUGO 1 138 1 | 27WP | P12:138:WFEC:HUGO_VALIANT:::: |  | 500 | 7.81 | 102.04 |  |  |  | Build a new HUGO7 345/138 kV transformer 2
04ALL | ERIS | Thermal | 521157 HUGO 7 345 997722 HUGO 1 138 1 | 27WP | P12:138:WFEC:HUGO_VALIANT:::: |  | 500 | 7.79 | 102.36 |  |  |  | Build a new HUGO7 345/138 kV transformer 2
04ALL | ERIS | Thermal | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 27WP | 507793 LEASIDE 4 138 509052 STONWAL4 138 1 |  | 219 | 57.9 | 107.5 |  |  |  | Rebuild the ROKHILL4 to G23-059-TAP 138kV line 1
04ALL | ERIS | Thermal | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | 27WP | 505522 VAN BUR5 161 505582 RS KERR5 161 1 |  | 223 | 8.17 | 117.03 |  |  |  | Rebuild the RSKERR5 to SUNSTCN5 161kV line 1
04ALL | ERIS | Thermal | 515264 TARBY 5 161 515265 SHAD-PT5 161 1 | 27WP | 505522 VAN BUR5 161 505582 RS KERR5 161 1 |  | 223 | 50.76 | 108.22 |  |  |  | Rebuild the TARBY5 to SHAD-PT5 161kV line 1
04ALL | ERIS | Thermal | 510898 OKMULGE4 138 510931 KELCO 4 138 1 | 24SP,27SP | 510902 WELETK4 138 510923 EC.HEN-4 138 1 |  | 235 | 7.91 | 104.11 |  |  |  | Rebuild the OKMULGE4 to KELCO4 138kV line 1
04ALL | ERIS | Thermal | 515190 AOCPT 2 69.0 515191 LULA 2 69.0 1 | 24SP,27SP,27WP | 515192 LULA 4 138 515699 EFITSTP4 138 1 |  | 72 | 7.5 | 142.94 |  |  |  | Rebuild the AOCPT2 to LULA2 69kV line 1
04ALL | ERIS | Thermal | 520971 LATTAJT4 138 521014 OILCRTP4 138 1 | 24SP | P12:138:OKGE:BKRBKR277:::: |  | 169 | 37.39 | 102.47 |  |  |  | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1
04ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | 24SP,27SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: |  | 956.1 | 88.26 | 131.82 |  |  |  | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2
04ALL | ERIS | Thermal | 520926 GRANFLD2 69.0 997729 GRNDFLD 69.0 1 | 24SP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 56 | 63.57 | 113.52 |  |  |  | Upgrade the GRANFLD2 138/69 kV transformer 1
04ALL | ERIS | Thermal | 521106 GRNDFLD4 138 997729 GRNDFLD 69.0 1 | 24SP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 56 | 63.21 | 111.07 |  |  |  | Upgrade the GRANFLD2 138/69 kV transformer 1
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 24SP,27WP | 532799 WAVERLY7 345 774420 G23-122-TAP 345 1 |  | 1015 | 72.96 | 114.98 |  |  |  | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1
04ALL | ERIS | Thermal | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1 | 24SP,27WP | 532799 WAVERLY7 345 774420 G23-122-TAP 345 1 |  | 1015 | 72.86 | 130.72 |  |  |  | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1
04ALL | ERIS | Thermal | 760921 G17-209-TAP 345 767240 G22-013-TAP 345 1 | 24SP,27WP | 532799 WAVERLY7 345 774420 G23-122-TAP 345 1 |  | 1015 | 72.72 | 128.85 |  |  |  | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1
04ALL | ERIS | Thermal | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 24SP,27WP | 532799 WAVERLY7 345 774420 G23-122-TAP 345 1 |  | 1015 | 72.68 | 126.22 |  |  |  | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1
04ALL | ERIS | Thermal | 547554 BAX492 2 69.0 547601 HOC404 2 69.0 1 | 24SP,27SP,27WP | 547487 HOC404 5 161 547729 BAX488 5 161 1 |  | 99 | 66.22 | 143.3 |  |  |  | Build a new RIV4525 to HOC4045 161kV line 1
04ALL | ERIS | Thermal | 512632 AFTON 5 161 997936 AFTAUTO1 69.0 1 | 24SP,27SP,27WP | P21:161:GRDA:MIAMI5-AFTON5:::HV: |  | 63 | 88.73 | 134.65 |  |  |  | Build a new AFTON5 to MIAMI5 161kV line 2
04ALL | ERIS | Thermal | 512633 AFTON 2 69.0 997936 AFTAUTO1 69.0 1 | 24SP,27SP,27WP | P21:161:GRDA:MIAMI5-AFTON5:::HV: |  | 63 | 88.27 | 132.77 |  |  |  | Build a new AFTON5 to MIAMI5 161kV line 2
04ALL | ERIS | Thermal | 300893 2CHECDST 69.0 513083 SUMMIT 2 69.0 1 | 24SP,27SP | 505552 GORE 5 161 774880 G23-145-TAP 161 1 |  | 35 | 8.8 | 118.97 |  |  |  | Rebuild the 2CHECDST to SUMMIT2 69kV line 1
04ALL | ERIS | Thermal | 510882 ATOKA--2 69.0 997987 ATOKA 69.0 1 | 24SP,27SP,27WP | 773380 G23-070-TAP 69.0 773381 GEN-2023-070 69.0 1 |  | 33 | 62.14 | 134.43 |  |  |  | Upgrade the ATOKA-4 138/69 kV transformer 1
04ALL | ERIS | Thermal | 510887 ATOKA--4 138 997987 ATOKA 69.0 1 | 24SP,27SP,27WP | 773380 G23-070-TAP 69.0 773381 GEN-2023-070 69.0 1 |  | 33 | 61.73 | 133.73 |  |  |  | Upgrade the ATOKA-4 138/69 kV transformer 1
04ALL | ERIS | Thermal | 515073 ERLSBOR2 69.0 515077 FIXICO 2 69.0 1 | 24SP | 510877 FIXCT4 138 510948 EARLSBORO 4 138 1 |  | 49 | 68.04 | 102.57 |  |  |  | Build a new FIXCT4 to MAUD4 138kV line 1
04ALL | ERIS | Thermal | 515077 FIXICO 2 69.0 997852 FIXICO4 69.0 4 | 24SP,27SP,27WP | 510877 FIXCT4 138 510948 EARLSBORO 4 138 1 |  | 67 | 6.46 | 123.63 |  |  |  | Build a new FIXCT4 to MAUD4 138kV line 1
04ALL | ERIS | Thermal | 515078 FIXICO 4 138 997852 FIXICO4 69.0 4 | 24SP,27SP,27WP | 510877 FIXCT4 138 510948 EARLSBORO 4 138 1 |  | 67 | 6.4 | 122.13 |  |  |  | Build a new FIXCT4 to MAUD4 138kV line 1
04ALL | ERIS | Thermal | 300852 2MIAETP 69.0 512630 MIAMI 2 69.0 1 | 24SP,27SP,27WP | 547487 HOC404 5 161 547729 BAX488 5 161 1 |  | 60 | 86.11 | 134.2 |  |  |  | Build a new RIV4525 to HOC4045 161kV line 1
04ALL | ERIS | Thermal | 547487 HOC404 5 161 997219 HOCK 69 69.0 1 | 24SP | 547487 HOC404 5 161 547729 BAX488 5 161 1 |  | 75 | 94.36 | 173.55 |  |  |  | Build a new RIV4525 to HOC4045 161kV line 1
04ALL | ERIS | Thermal | 547601 HOC404 2 69.0 997219 HOCK 69 69.0 1 | 24SP | 547487 HOC404 5 161 547729 BAX488 5 161 1 |  | 75 | 92.79 | 169.02 |  |  |  | Build a new RIV4525 to HOC4045 161kV line 1
04ALL | ERIS | Thermal | 511475 SNYDER-2 69.0 511495 TOMSTEED2 69.0 1 | 24SP,27SP | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1 |  | 35 | 8.81 | 101.29 |  |  |  | Rebuild the SNYDER2 to TOMSTEED2 69kV line 1
04ALL | ERIS | Thermal | 520534 DUKE 2 69.0 520929 GYPSUM 2 69.0 1 | 24SP | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 |  | 30 | 59.95 | 147.32 |  |  |  | Rebuild the DUKE2 to GYPSUM2 69kV line 1
04ALL | ERIS | Thermal | 520534 DUKE 2 69.0 521042 RUSSELL2 69.0 Z1 | 24SP | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 |  | 30 | 62.86 | 155 |  |  |  | REPLACE the breaker at DUKE
04ALL | ERIS | Thermal | 520895 ELDORDJ2 69.0 520929 GYPSUM 2 69.0 1 | 24SP | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 |  | 30 | 99.88 | 129.51 |  |  |  | Rebuild the ELDORDJ2 to GYPSUM2 69kV line 1
04ALL | ERIS | Thermal | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 27SP | P12:138:AEPW:HENRYET4:WELETK4::: |  | 286 | 7.77 | 100.35 |  |  |  | Rebuild the WELEETK4 to WELETK4 138kV line 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 520406 TUPELO 4 138 1 | 27SP | P12:138:OKGE-SWPA-AEPW-WFEC:BKRBKR278:::: |  | 143 | 6.84 | 100.04 |  |  |  | Rebuild the TUPELO4 to STNWLSW4 138kV line 1
04ALL | ERIS | Thermal | 520926 GRANFLD2 69.0 997727 GRNDFLD 69.0 1 | 27SP,27WP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 56 | 73.17 | 112.79 |  |  |  | Upgrade the GRANFLD2 138/69 kV transformer 1
04ALL | ERIS | Thermal | 521106 GRNDFLD4 138 997727 GRNDFLD 69.0 1 | 27SP,27WP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 56 | 72.06 | 110.26 |  |  |  | Upgrade the GRANFLD2 138/69 kV transformer 1
04ALL | ERIS | Thermal | 512691 FAIRNEO2 69.0 512708 FAIRTAP2 69.0 1 | 24SP,27SP,27WP | P21:161:GRDA:MIAMI5-AFTON5:::HV: |  | 122 | 84.27 | 114.14 |  |  |  | Build a new AFTON5 to MIAMI5 161kV line 2
04ALL | ERIS | Thermal | 547487 HOC404 5 161 997217 HOCK 69 69.0 1 | 27SP,27WP | 547487 HOC404 5 161 547729 BAX488 5 161 1 |  | 75 | 92.6 | 193.71 |  |  |  | Build a new RIV4525 to HOC4045 161kV line 1
04ALL | ERIS | Thermal | 547554 BAX492 2 69.0 547602 RIV406 2 69.0 1 | 27SP,27WP | 547487 HOC404 5 161 547729 BAX488 5 161 1 |  | 72 | 9.33 | 106.24 |  |  |  | Build a new RIV4525 to HOC4045 161kV line 1
04ALL | ERIS | Thermal | 547601 HOC404 2 69.0 997217 HOCK 69 69.0 1 | 27SP,27WP | 547487 HOC404 5 161 547729 BAX488 5 161 1 |  | 75 | 99.13 | 185.4 |  |  |  | Build a new RIV4525 to HOC4045 161kV line 1
04ALL | ERIS | Thermal | 512646 OKAYGR 2 69.0 513074 MUSKSW 2 69.0 1 | 27SP | P12:161:SWPA:GORE-MUSKOGEE-FT GIBSON THREE TERMINAL LINE::505558 505552 1, 505558 505560 1, 505558 515222 1:: |  | 43 | 8.25 | 104.59 |  |  |  | Rebuild the OKAYGR2 to MUSKSW2 69kV line 1
04ALL | ERIS | Thermal | 520821 BASELIN2 69.0 997744 BASELINE 69.0 1 | 27SP | P12:138:WFEC:COMACHE_LOCO:::: |  | 56 | 41.33 | 102.53 |  |  |  | Upgrade the BASELIN2 138/69 kV transformer 1
04ALL | ERIS | Thermal | 515162 FNDTION4 138 515171 CHIKSAW4 138 1 | 24SP,27SP,27WP | P12:138:OKGE:BKRBKR344:::: |  | 191 | 44.79 | 109.87 |  |  |  | Rebuild the FNDTION4 to CHIKSAW4 138kV line 1
04ALL | ERIS | Thermal | 547469 RIV4525 161 547498 STL439 5 161 1 | 24SP,27SP | 547467 ORO110 5 161 547469 RIV4525 161 1 |  | 461 | 60.98 | 105.92 |  |  |  | Rebuild the RIV4525 to STL4395 161kV line 1
04ALL | ERIS | Thermal | 505558 MUSKTAP5 161 505560 FT GIB 5 161 1 | 27SP | 505558 MUSKTAP5 161 515222 MUSKOGE5 161 1 |  | 166 | 9.64 | 104.48 |  |  |  | Rebuild the MUSKTAP5 to FTGIB5 161kV line 1
04ALL | ERIS | Thermal | 510893 HUGO---2 69.0 510894 VALYTIM2 69.0 1 | 27WP | 505600 TUPELO 4 138 510881 ALLENGT4 138 1 |  | 48 | 9.77 | 100.34 |  |  |  | Rebuild the HUGO-2 to VALYTIM2 69kV line 1
04ALL | ERIS | Thermal | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1 | 24SP | 775100 G23-156-TAP 138 775101 GEN-2023-156 138 1 |  | 136 | 88.3 | 105.62 |  |  |  | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line 1
04ALL | ERIS | Thermal | 515177 PARKLN 2 69.0 515384 ADAINDU2 69.0 1 | 24SP,27SP,27WP | P12:138:OKGE:BKRBKR276:::: |  | 96 | 50.57 | 103.68 |  |  |  | Rebuild the PARKLN2 to ADAINDU2 69kV line 1
04ALL | ERIS | Thermal | 515182 VALLYVU2 69.0 515189 AOCPA 2 69.0 1 | 24SP,27SP | P12:138:OKGE:BKRBKR276:::: |  | 111 | 9.07 | 105.69 |  |  |  | Rebuild the VALLYU2 to AOCPA2 69kV line 1
04ALL | ERIS | Thermal | 512644 GORE GR2 69.0 513068 ILLINOTP 2 69.0 1 | 24SP | P12:161:OKGE-SWPA:BKRBKR3:::: |  | 43 | 74.58 | 123.44 |  |  |  | Rebuild the GOREGR2 to ILLINOTP2 69kV line 1
04ALL | ERIS | Thermal | 513068 ILLINOTP 2 69.0 513071 GREENLF 2 69.0 1 | 24SP,27SP | P12:161:OKGE-SWPA:BKRBKR3:::: |  | 47 | 60.96 | 106.93 |  |  |  | Rebuild the ILLINOTP2 to GREENLF2 69kV line 1
04ALL | ERIS | Thermal | 520895 ELDORDJ2 69.0 520896 ELDORDO2 69.0 1 | 24SP,27SP | 512110 LAKEP4WT 138 774940 G23-148-TAP 138 1 |  | 30 | 71.84 | 127.3 |  |  |  | Rebuild the ELDORDJ2 to ELDORDO2 69kV line 1
04ALL | ERIS | Thermal | 520821 BASELIN2 69.0 521080 VELMA 2 69.0 1 | 24SP,27SP,27WP | 520864 COMANCH4 138 3WXFMR COMANCHE 1 |  | 30 | 28.09 | 107.58 |  |  |  | Rebuild the BASELIN2 to VELMA2 69kV line 1
04ALL | ERIS | Thermal | 504000 AVOCA 5 161 505480 BEAVER 5 161 1 | 27WP | P12:345:AEPW-SPRM:FLINTCR7:BROOKLINE7::: |  | 223 | 70.69 | 131.52 |  |  |  | Rebuild the AVOCA5 to BEAVER5 161kV line 1
04ALL | ERIS | Thermal | 505560 FT GIB 5 161 512640 OKAYGR 5 161 1 | 27SP | 505558 MUSKTAP5 161 515222 MUSKOGE5 161 1 |  | 223 | 6.06 | 101.12 |  |  |  | Rebuild the FTGIB5 to OKAYGR5 161kV line 1
04ALL | ERIS | Thermal | 513071 GREENLF 2 69.0 513074 MUSKSW 2 69.0 1 | 27SP | P12:161:OKGE-SWPA:BKRBKR3:::: |  | 47 | 54.21 | 102.24 |  |  |  | Rebuild the GREENLF2 to MUSKSW2 69kV line 1
04ALL | ERIS | Thermal | 520542 HRSBGSW2 69.0 520933 HARISBG2 69.0 1 | 27SP | 520864 COMANCH4 138 520981 LOCO 4 138 1 |  | 30 | 45.36 | 100.42 |  |  |  | Rebuild the HRSBGSW2 to HARISBG2 69kV line 1
04ALL | ERIS | Thermal | 520542 HRSBGSW2 69.0 521080 VELMA 2 69.0 1 | 27SP | 520864 COMANCH4 138 520981 LOCO 4 138 1 |  | 30 | 44.69 | 101.58 |  |  |  | Rebuild the HRSBGSW2 to VELMA2 69kV line 1
04ALL | ERIS | Thermal | 520883 DUNCNJT2 69.0 520933 HARISBG2 69.0 1 | 27SP | 520864 COMANCH4 138 520981 LOCO 4 138 1 |  | 30 | 8.92 | 106.44 |  |  |  | Rebuild the DUNCNJT2 to HARISBG2 69kV line 1
05ALL | ERIS | Thermal | 528413 TAYLOR 3 115 528449 W_BENDER 3 115 1 | 24SP,27SP,27WP | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1 |  | 157 | 103.98 | 127.68 |  |  |  | Rebuild the TAYLOR to W_BENDER 115kV line 1
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 997680 WAUK 90343-A 230 1 | 24SP | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A _1 2 |  | 559 | 16.76 | 101.44 |  |  |  | Build a new POTTERCO 345/230 kV transformer 4
05ALL | ERIS | Thermal | 523304 MOORE_W 3 115 523315 RB-S&S 3 115 1 | 24SP,27SP | 523309 MOORE_CNTY 6 230 3WXFMR ENRCO 136402 1 |  | 80 | 62.66 | 107.95 |  |  |  | Build a new DUMAS19ST to MOORE_W 115kV line 1
05ALL | ERIS | Thermal | 523315 RB-S&S 3 115 523318 DUMAS_19ST 3 115 1 | 24SP | 523309 MOORE_CNTY 6 230 3WXFMR ENRCO 136402 1 |  | 103 | 65.73 | 102.81 |  |  |  | Build a new DUMAS19ST to MOORE_W 115kV line 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 997699 ENRCO13617-1 115 1 | 24SP | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 |  | 193 | 3.2 | 146.31 |  |  |  | Upgrade the PRINGLE 230/115 kV transformer 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 997699 ENRCO13617-1 115 1 | 24SP | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 |  | 193 | 3.27 | 144.11 |  |  |  | Upgrade the PRINGLE 230/115 kV transformer 1
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1 | 24SP,27SP,27WP | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 |  | 547 | 66.21 | 135.29 |  |  |  | Build a new POTTER_CO to HARRNG_MID6 230kV line 1
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | 24SP,27SP,27WP | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1 |  | 796 | 48.06 | 114.51 |  |  |  | Build a new POTTER_CO to HARRNG_MID6 230kV line 1
05ALL | ERIS | Thermal | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | 24SP,27SP | 525531 TOLK 6 230 525586 NEEDMORE 6 230 2 |  | 497 | 14.51 | 104.57 |  |  |  | Rebuild the TOLK to NEEDMORE 230 kV line 1
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 997697 ENRCO13617-1 115 1 | 27SP,27WP,27L | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 |  | 193 | 3.06 | 144.89 |  |  |  | Upgrade the PRINGLE 230/115 kV transformer 1
05ALL | ERIS | Thermal | 523267 PRINGLE 6 230 997697 ENRCO13617-1 115 1 | 27SP,27WP,27L | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 |  | 193 | 3.12 | 144.2 |  |  |  | Upgrade the PRINGLE 230/115 kV transformer 1
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 997678 WAUK 90343-A 230 1 | 27SP,27WP | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A _1 2 |  | 559 | 19.78 | 117.76 |  |  |  | Build a new POTTERCO 345/230 kV transformer 4
05ALL | ERIS | Thermal | 523961 POTTER_CO 7 345 997678 WAUK 90343-A 230 1 | 27SP,27WP | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A _1 2 |  | 559 | 19.99 | 113.92 |  |  |  | Build a new POTTERCO 345/230 kV transformer 4
05ALL | ERIS | Thermal | 523318 DUMAS_19ST 3 115 523319 DEMON_TP 3 115 1 | 27SP | 523309 MOORE_CNTY 6 230 3WXFMR ENRCO 136402 1 |  | 103 | 77.72 | 115.58 |  |  |  | Build a new DUMAS19ST to MOORE_W 115kV line 1
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 997676 WAUK 90343-A 230 3 | 27WP | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A _1 2 |  | 770 | 19.88 | 107.78 |  |  |  | Build a new POTTERCO 345/230 kV transformer 4
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 997677 WAUK 90343-A 230 2 | 27WP | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A _2 3 |  | 770 | 19.88 | 107.78 |  |  |  | Build a new POTTERCO 345/230 kV transformer 4
05ALL | ERIS | Thermal | 523961 POTTER_CO 7 345 997676 WAUK 90343-A 230 3 | 27WP | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A _1 2 |  | 770 | 20.1 | 106.64 |  |  |  | Build a new POTTERCO 345/230 kV transformer 4
05ALL | ERIS | Thermal | 523961 POTTER_CO 7 345 997677 WAUK 90343-A 230 2 | 27WP | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A _2 3 |  | 770 | 20.1 | 106.64 |  |  |  | Build a new POTTERCO 345/230 kV transformer 4
05ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | 24SP,27SP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: |  | 956.1 | 57.04 | 124.32 |  |  |  | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2
05ALL | ERIS | Thermal | 531451 MINGO 7 345 531465 SETAB 7 345 1 | 24SP,27SP | 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 |  | 1195.1 | 38.48 | 110.96 |  |  |  | Rebuild the MINGO 7 to SETAB 7 345kV line 1
05ALL | ERIS | Thermal | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | 27SP | P42:345:OKGE:SB_SEOL7385:::: |  | 717 | 66.17 | 101.15 |  |  |  | Rebuild the DRAPER7 to SEMINOL7 345kV line 2
05ALL | ERIS | Thermal | 525480 PLANT_X 3 115 997631 WH ALM20171 115 1 | 27SP | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 251 | 58.15 | 103.02 |  |  |  | Upgrade the PLANTX 230/115kV transformer 1
05ALL | ERIS | Thermal | 525481 PLANT_X 6 230 997631 WH ALM20171 115 1 | 27SP | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 251 | 58.51 | 102.95 |  |  |  | Upgrade the PLANTX 230/115kV transformer 1
05ALL | ERIS | Thermal | 525531 TOLK 6 230 997629 ABBXNL844501 230 1 | 27WP | 525531 TOLK 6 230 3WXFMR TOLK 6 3 |  | 553 | 46.88 | 100.92 |  |  |  | Build a new POTTERCO 345/230 kV transformer 4
05ALL | ERIS | Thermal | 525549 TOLK 7 345 997629 ABBXNL844501 230 1 | 27WP | 525531 TOLK 6 230 3WXFMR TOLK 6 3 |  | 553 | 47.92 | 100.92 |  |  |  | Build a new POTTERCO 345/230 kV transformer 4
05ALL | ERIS | Thermal | 523266 PRINGLE 3 115 523377 RIVERVIEW 3 115 1 | 27L | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 |  | 176 | 12.69 | 100.04 |  |  |  | Rebuild the PRINGLE3 to RIVERVIEW3 115kV line 1
00NR | NRIS | Thermal | 505488 CARTHAG5 161 998100 CRG X2 69.0 1 | 24SP,27SP | 505490 CARTHG 2 69.0 3WXFMR CRG X1 1 |  | 84 | 86.24 | 103.09 |  |  |  | Build a new CARTHAG5 161/69 kV transformer 3
00NR | NRIS | Thermal | 505488 CARTHAG5 161 998101 CRG X1 69.0 1 | 24SP,27SP | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 |  | 84 | 86.79 | 103.75 |  |  |  | Build a new CARTHAG5 161/69 kV transformer 3
00NR | NRIS | Thermal | 505490 CARTHG 2 69.0 998101 CRG X1 69.0 1 | 24SP,27SP | 505490 CARTHG 2 69.0 3WXFMR CRG X2 1 |  | 84 | 83.86 | 100.58 |  |  |  | Build a new CARTHAG5 161/69 kV transformer 3
00NR | NRIS | Thermal | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 24SP,27SP,27WP | 640088 BPS SUB7 115 640111 CLATONA7 115 1 |  | 398 | 13.11 | 103.67 |  |  |  | Build a new BPSSUB7 to SHELDON7 115kV line 2
00NR | NRIS | Thermal | 512111 LAKEP2WT 69.0 520896 ELDORDO2 69.0 1 | 24SP,27SP,27WP | 521043 RUSSELL4 138 774940 G23-148-TAP 138 1 |  | 39 | 54 | 121.49 |  |  |  | Rebuild the LAKEP2WT to ELDORADO2 69kV line 1
00NR | NRIS | Thermal | 640173 FREMONT7 115 996709 FREMONT T4 69.0 1 | 24SP | P12:161:OPPD:TEKAMAH-S1226:::HV: |  | 56 | 83.33 | 100.1 |  |  |  | Build a new FREMONT7 115/69 kV transformer 3
00NR | NRIS | Thermal | 647976 S976 8 69.0 996709 FREMONT T4 69.0 1 | 24SP | P12:161:OPPD:TEKAMAH-S1226:::HV: |  | 56 | 83.2 | 100.51 |  |  |  | Build a new FREMONT7 115/69 kV transformer 3
00NR | NRIS | Thermal | 640227 HOSKINS4 230 996866 HOSKINS T1 115 1 | 24SP | P13:115-345:NPPD:NUCOR-2 |  | 187 | 112.69 | 106.11 |  |  |  | Build a new HOSKINST1 230/115 kV transformer 2
00NR | NRIS | Thermal | 640228 HOSKINS7 115 996866 HOSKINS T1 115 1 | 24SP | P13:115-345:NPPD:NUCOR-2 |  | 187 | 111.77 | 105.32 |  |  |  | Build a new HOSKINST1 230/115 kV transformer 2
00NR | NRIS | Thermal | 528018 RED_BLUFF 3 115 528025 RDRUNNER 3 115 1 | 27SP | 528027 RDRUNNER 7 345 3WXFMR SMIT 3230943 1 |  | 175 | 100.08 | 105.44 |  |  |  | Rebuild the RED_BLUFF3 to RDRUNNER3 115kV line 1
00NR | NRIS | Thermal | 640173 FREMONT7 115 996707 FREMONT T4 69.0 1 | 27SP | P12:161:OPPD:TEKAMAH-S1226:::HV: |  | 56 | 84.94 | 103.58 |  |  |  | Build a new FREMONT7 115/69 kV transformer 3
00NR | NRIS | Thermal | 647976 S976 8 69.0 996707 FREMONT T4 69.0 1 | 27SP | P12:161:OPPD:TEKAMAH-S1226:::HV: |  | 56 | 83.88 | 101.79 |  |  |  | Build a new FREMONT7 115/69 kV transformer 3
00NR | NRIS | Thermal | 640227 HOSKINS4 230 996864 HOSKINS T1 115 1 | 27SP | P13:115-345:NPPD:NUCOR-2 |  | 187 | 112.55 | 106.82 |  |  |  | Build a new HOSKINST1 230/115 kV transformer 2
00NR | NRIS | Thermal | 640228 HOSKINS7 115 996864 HOSKINS T1 115 1 | 27SP | P13:115-345:NPPD:NUCOR-2 |  | 187 | 112.53 | 106.61 |  |  |  | Build a new HOSKINST1 230/115 kV transformer 2
00NR | NRIS | Thermal | 542976 LEVEE 5 161 543666 NEASTN5 161 1 | 27SP | 543011 CHOUTEU5 161 543665 HAWTHN5 161 1 |  | 334 | 84.84 | 100.01 |  |  |  | Rebuild the LEVEE5 to NEASTN 161kV line 1
01ALL | ERIS | Thermal | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 27SP, 24SP | 589324 G17-094-TAP 230 652507 FTTHOMP4 230 1 | 352 | 352 | 55.77 | 113.23 |  |  |  | Rebuild the G17-094-TAP to HURON 4 230kV line 1
01ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 27L, 27SP, 27WP, 24SP | 640183 GENTLMN3 345 640252 KEYSTON3 345 1 | 320 | 320 | 87.29 | 133.41 |  |  |  | Rebuild the GENTLMN4 to OGALALA4 230kV line 1
01ALL | ERIS | Thermal | 589324 G17-094-TAP 230 652507 FTTHOMP4 230 1 | 24SP, 27SP | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 352 | 352 | 48.15 | 113.99 |  |  |  | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1
01ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 996528 BD KU2A 230 1 | 27SP | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 471 | 478 | 77.36 | 112.26 |  |  |  | Build a new Broadland 345/230 kV transformer 2
01ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 996529 BD KU2A 230 1 | 27SP | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 471 | 478 | 69.62 | 122.17 |  |  |  | Build a new Broadland 345/230 kV transformer 2
01ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 996531 BD KU2A 230 1 | 24SP | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 471 | 478 | 69.62 | 115.87 |  |  |  | Build a new Broadland 345/230 kV transformer 2
01ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 996532 BD KU2A 230 1 | 24SP | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 471 | 478 | 77.36 | 125.98 |  |  |  | Build a new Broadland 345/230 kV transformer 2
01ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 996528 BD KU2A 230 1 | 27SP | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 471 | 478 | 76.03 | 111.46 |  |  |  | Build a new Broadland 345/230 kV transformer 2
01ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 996529 BD KU2A 230 1 | 27SP | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 471 | 478 | 68.26 | 121.49 |  |  |  | Build a new Broadland 345/230 kV transformer 2
01ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 996531 BD KU2A 230 1 | 24SP | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 471 | 478 | 68.26 | 115.38 |  |  |  | Build a new Broadland 345/230 kV transformer 2
01ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 996532 BD KU2A 230 1 | 24SP | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 471 | 478 | 76.03 | 125.67 |  |  |  | Build a new Broadland 345/230 kV transformer 2
01ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 27SP, 24SP, 27WP | 640252 KEYSTON3 345 763666 G21-037-TAP 345 1 | 320 | 320 | 121.42 | 131.72 |  |  |  | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1
01ALL | ERIS | Thermal | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | 24SP | 652424 BELFELD3 345 999222 MAURINE 345 1 | 319 | 383 | 104.95 | 104.95 |  |  |  | Rebuild the BISON___-GE4 to HETINGR4 230kV line 1
01ALL | ERIS | Thermal | 659351 BISON___-GE4 230 773940 G23-098-TAP 230 1 | 24SP | 652424 BELFELD3 345 999222 MAURINE 345 1 | 384 | 384 | 100.18 | 100.18 |  |  |  | Rebuild the BISON___-GE4 to G23-098-TAP 230kV line 1
01ALL | ERIS | Thermal | 768300 G22-066-PROX 230 773940 G23-098-TAP 230 1 | 24SP, 27SP | 652424 BELFELD3 345 999222 MAURINE 345 1 | 384 | 384 | 63.42 | 141.37 |  |  |  | Rebuild the G22-066-PROX to G23-098-TAP 230kV line 1
01ALL | ERIS | Thermal | 652444 JAMESTN4 230 774860 G23-144-TAP 230 1 | 24SP, 27SP | 652444 JAMESTN4 230 765520 GEN-2021-024 230 1 | 345 | 345 | 51.85 | 110.21 |  |  |  | Rebuild the JAMESTN4 to G23-144-TAP 230kV line 1
01ALL | ERIS | Thermal | 652473 ELKCRK 7 115 652483 NEWELL 7 115 1 | 27SP, 24SP, 27L | 652480 MAURINE7 115 652491 SULPHUR 115 1 | 134 | 134 | 71.65 | 115.07 |  |  |  | Rebuild the ELKCRK 7 to NEWELL 7 115kV line 1
01ALL | ERIS | Thermal | 652473 ELKCRK 7 115 652490 RAPIDCY7 115 1 | 27SP, 24SP | 652480 MAURINE7 115 652491 SULPHUR 115 1 | 134 | 134 | 67.9 | 110.25 |  |  |  | Rebuild the ELKCRK 7 to RAPIDCY7 115kV line 1
01ALL | ERIS | Thermal | 652483 NEWELL 7 115 652491 SULPHUR 115 1 | 27SP, 24SP, 27L | 652480 MAURINE7 115 652491 SULPHUR 115 1 | 134 | 134 | 77.26 | 121.67 |  |  |  | Rebuild the NEWELL 7 to SULPHUR 115kV line 1
01ALL | ERIS | Thermal | 652480 MAURINE7 115 652491 SULPHUR 115 1 | 27SP, 24SP, 27L | 652483 NEWELL 7 115 652491 SULPHUR 115 1 | 134 | 134 | 77.07 | 118.73 |  |  |  | Rebuild the MAURINE7 to SULPHUR 115kV line 1
01ALL | ERIS | Thermal | 652490 RAPIDCY7 115 655763 RUSHMORE-RM7 115 1 | 27SP, 24SP, 27WP | 652484 NUNDRWD4 230 659376 DRYCREEK-BE4 230 1 | 80 | 88 | 86.16 | 119.33 |  |  |  | Rebuild the RAPIDCY7 to RUSHMORE-RM7 115kV line 1
01ALL | ERIS | Thermal | 640109 CHADRON7 115 640405 WAYSIDE7 115 1 | 24SP, 27SP | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | 160 | 160 | 74.61 | 111.66 |  |  |  | Rebuild the CHADRON7 to WAYSIDE7 115kV line 1
01ALL | ERIS | Thermal | 640404 WAYSIDE4 230 996783 WAYSIDE T1 115 1 | 27SP | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | 187 | 187 | 66.14 | 110.62 |  |  |  | Build a new Wayside 230/115 kV transformer 2
01ALL | ERIS | Thermal | 640404 WAYSIDE4 230 996785 WAYSIDE T1 115 1 | 24SP | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | 187 | 187 | 61.42 | 116.51 |  |  |  | Build a new Wayside 230/115 kV transformer 2
01ALL | ERIS | Thermal | 640405 WAYSIDE7 115 996783 WAYSIDE T1 115 1 | 27SP | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | 187 | 187 | 66.13 | 108.26 |  |  |  | Build a new Wayside 230/115 kV transformer 2
01ALL | ERIS | Thermal | 640405 WAYSIDE7 115 996785 WAYSIDE T1 115 1 | 24SP | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | 187 | 187 | 61.59 | 114.31 |  |  |  | Build a new Wayside 230/115 kV transformer 2
01ALL | ERIS | Thermal | 640338 SCOTBLF7 115 640397 VICTRYH7 115 1 | 24SP | 652573 STEGALL4 230 659206 STEGALL_-MB4 230 1 | 155 | 155 | 63.55 | 123.38 |  |  |  | Rebuild the SCOTBLF7 to VICTRYH7 115kV line 1
01ALL | ERIS | Thermal | 652437 GRNDFKS4 230 657759 PICKERT4 230 1 | 27WP, 24SP, 27SP | 657110 MPC4300 POI 345 657946 PRAIRIE3 345 1 | 423 | 423 | 67.72 | 109.77 |  |  |  | Rebuild the GRNDFKS4 to PICKERT4 230kV line 1
01ALL | ERIS | Thermal | 652444 JAMESTN4 230 657759 PICKERT4 230 1 | 24SP, 27SP | 657110 MPC4300 POI 345 657946 PRAIRIE3 345 1 | 345 | 345 | 72.08 | 101.02 |  |  |  | Rebuild the JAMESTN4 to PICKERT4 230kV line 1
01ALL | ERIS | Thermal | 659134 SIDNEY___TS4 230 659210 SIDNEY__-MB4 230 1 | 24SP | 659425 SD.LS-KS-MB3 345 763666 G21-037-TAP 345 1 | 478 | 478 | 87.57 | 100.01 |  |  |  | Rebuild the SIDNEY___TS4 to SIDNEY__-MB4 230kV line 1
01ALL | ERIS | Thermal | 659339 BOWMAN__-BE4 230 661047 HETINGR4 230 1 | 24SP | 659448 DAGLUM__-BE4 230 775180 G23-160-TAP 230 1 | 319 | 351 | < 40 | 102.2 |  |  |  | Build a new BOWMAN__-BE4 to HETINGR4 230 kV line 2
01ALL | ERIS | Thermal | 764220 G20-021-TAP 345 767380 G22-020-PROX 345 2 | 24SP, 27SP | 764220 G20-021-TAP 345 767380 G22-020-PROX 345 1 | 717 | 717 | 60.49 | 108.04 |  |  |  | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2
01ALL | ERIS | Thermal | 764220 G20-021-TAP 345 767380 G22-020-PROX 345 1 | 24SP, 27SP | 764220 G20-021-TAP 345 767380 G22-020-PROX 345 2 | 717 | 717 | 60.49 | 108.03 |  |  |  | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1
01ALL | ERIS | Thermal | 652499 CAMPBELL 4 230 661038 GLENHAM4 230 1 | 24SP, 27SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 319 | 319 | 84.47 | 118.58 |  |  |  | Rebuild the CAMPBELL 4 to GLENHAM4 230kV line 1
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996616 FT2 KU1C 230 1 | 27SP, 27WP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 81.7 | 117.81 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996617 FT2 KU1B 230 1 | 27SP, 27WP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 81.7 | 117.81 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996618 FT2 KU1A 230 1 | 27SP, 27WP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 83.47 | 120.36 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996619 FT2 KU1C 230 1 | 24SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 86.94 | 117.12 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 24SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 239 | 239 | 83.53 | 166.92 |  |  |  | Oahe 230 kV Terminal Upgrades (WAPA)
01ALL | ERIS | Thermal | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 | 24SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 239 | 239 | 88.82 | 173.64 |  |  |  | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1
01ALL | ERIS | Thermal | 655765 WHITLOCK_-RM 230 661038 GLENHAM4 230 1 | 24SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 271 | 271 | 80.73 | 119.11 |  |  |  | Whitlock - Glenham 230 kV Clearance Increase
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996620 FT2 KU1B 230 1 | 24SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 86.94 | 117.12 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996621 FT2 KU1A 230 1 | 24SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 88.82 | 119.66 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652497 MAURINE4 230 652884 NUNDRWD-LNX3 230 1 | 24SP, 27SP | 999222 MAURINE 345 999224 OAHE 345 1 | 320 | 342 | 51.01 | 110.44 |  |  |  | Rebuild the MAURINE4 to NUNDRWD-LNX3 230kV line 1
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996616 FT2 KU1C 230 1 | 27SP, 27WP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 81.44 | 116.69 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996617 FT2 KU1B 230 1 | 27SP, 27WP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 81.44 | 116.69 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996618 FT2 KU1A 230 1 | 27SP, 27WP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 83.2 | 119.22 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 24SP, 27SP, 27WP | 999222 MAURINE 345 999224 OAHE 345 1 | 717 | 717 | 68.87 | 121.9 |  |  |  | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1
01ALL | ERIS | Thermal | 541202 SIBLEY 5 161 541250 SIBLEYPL 161 1 | 24SP, 27SP, 27WP | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | 418 | 418 | 76.11 | 123.08 |  |  |  | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996619 FT2 KU1C 230 1 | 24SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 86.47 | 115.92 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996620 FT2 KU1B 230 1 | 24SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 86.47 | 115.92 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996621 FT2 KU1A 230 1 | 24SP | 767380 G22-020-PROX 345 773060 G23-054-TAP 345 1 | 250 | 313 | 88.34 | 118.43 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 2 | 27L, 27WP | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | 956.1 | 956.1 | 81.68 | 138.6 |  |  |  | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2
01ALL | ERIS | Thermal | 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | 24SP, 27SP | 999222 MAURINE 345 999224 OAHE 345 1 | 320 | 342 | 51.88 | 126.96 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 24SP, 27SP | 999222 MAURINE 345 999224 OAHE 345 1 | 239 | 239 | 98.89 | 179.9 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 652520 OAHE 7 115 658174 IRVSIMM7 115 1 | 24SP | P12:115:UMZS:# 4014 #:: SIMPLE N-1 FOR PIERRE-IRV SIMMONS BRANCH FAULT:HV: | 114 | 114 | 44.92 | 102.46 |  |  |  | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2
01ALL | ERIS | Thermal | 645458 S3458 3 345 659130 CHAPELLE-BE3 345 1 | 27SP, 24SP, 27WP | P23:345:UMZW:# 2411 #:: FT2 IN SD. FT2 3392 BKR FAULT:EHV | 1792 | 1792 | < 40 | 118.88 |  |  |  | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1
01ALL | ERIS | Thermal | 659120 BROADLND-BE3 345 996532 BD KU2A 230 1 | 24SP | 999222 MAURINE 345 999224 OAHE 345 1 | 471 | 478 | 62.33 | 101.49 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 659205 BROADLND-BE4 230 996532 BD KU2A 230 1 | 24SP | 999222 MAURINE 345 999224 OAHE 345 1 | 471 | 478 | 62.25 | 103.59 |  |  |  | Build a new OAHE to MAURINE 345 kV line 2
01ALL | ERIS | Thermal | 635200 RAUN 3 345 762779 G18-043 TAP 345 1 | 27SP, 24SP, 27WP | P55:345:OPPD:S3458 3::FN13:EHV | 956 | 956 | 90.98 | 133.09 |  |  |  | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1
01ALL | ERIS | Thermal | 652203 FARGO 8 69.0 652436 FARGO 7 115 2 | 27WP, 27SP, 24SP | P12:230:XEL-WAPA:AUTO-SINGLE:SHEYNNE4:FARGO4:1 | 100 | 125 | 132 | 178.84 |  |  |  | Build a new Fargo 115/69 kV transformer 2
01ALL | ERIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 27WP, 24SP, 27SP, 27L | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1: | 796 | 796 | 76.17 | 116.48 |  |  |  | Build a new SHEYNNE4 to FARGO 4 230 kV line 2
01ALL | ERIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 27WP, 24SP, 27SP, 27L | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1: | 458 | 505 | 118.17 | 186.71 |  |  |  | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1
01ALL | ERIS | Thermal | 652474 AURORA 7 115 652504 BROOKNG7 115 1 | 24SP, 27SP | P23:345:XEL:192 BKR SPK AS | 121 | 121 | 63.51 | 130.31 |  |  |  | Rebuild the AURORA 7 to BROOKNG7 115kV line 1
01ALL | ERIS | Thermal | 652474 AURORA 7 115 652505 FLANDRU7 115 1 | 24SP, 27SP | P23:345:XEL:196 BKR SPK AS | 114 | 114 | 57.29 | 123.94 |  |  |  | Rebuild the AURORA 7 to FLANDRU7 115kV line 1
01ALL | ERIS | Thermal | 652203 FARGO 8 69.0 657802 DELVO 8 69.0 1 | 27WP, 24SP, 27SP, 27L | P21:230:XEL-WAPA:AUTO-SINGLE:SHEYNNE4:FARGO4:1 | 71 | 71 | 172.59 | 291.98 |  |  |  | Rebuild the FARGO 8 to DELVO 8 69kV line 1

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2023-012 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 2360799.2262 | 0.8636% | 273358902 | 0.02815
GEN-2023-012 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 5370176.139 | 1.492% | 359902800 | 0.06382
GEN-2023-012 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 6775920.3861 | 2.054% | 329910900 | 0.08107
GEN-2023-012 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 927136.825 | 0.6183% | 149959500 | 0.01309
GEN-2023-012 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 871915.8767 | 0.5814% | 149959500 | 0.01209
GEN-2023-012 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 5375093.3433 | 1.379% | 389894700 | 0.07196
GEN-2023-012 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 9323.7841 | 0.1123% | 8302968 | 0.00197
GEN-2023-012 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 138632.6505 | 1.67% | 8302968 | 0.04895
GEN-2023-012 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 1.462% | 0 | 0.05954
GEN-2023-012 | 01 NORTH | 158697 | ERIS | Kingsbury County 115kV Substation GEN-2023-012 Interconnection (Non-Shared NU) (EREP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-012 (98.6MW/Wind), into Kingsbury County 115kV Substation | 0 | 100% | 0 | 1
GEN-2023-012 | 01 NORTH | 158696 | ERIS | Kingsbury County 115kV Substation GEN-2023-012 Interconnection (TOIF) (EREP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-012 (98.6MW/Wind), into Kingsbury County 115kV Substation | 5135000 | 100% | 5135000 | 1
GEN-2023-012 | 01 NORTH | TBD | ERIS | Rebuild the AURORA 7 to BROOKNG7 115kV line 1 | Current Study | Rebuild the existing AURORA 7 to BROOKNG7 115 kV line 1 (11 miles) to a standard rating of 239 MVA | 3267171.2549 | 41.78% | 7819240 | 0.13103
GEN-2023-012 | 01 NORTH | TBD | ERIS | Rebuild the AURORA 7 to FLANDRU7 115kV line 1 | Current Study | Rebuild the existing AURORA 7 to FLANDRU7 115 kV line 1 (17.05 miles) to a standard rating of 239 MVA | 5064115.445 | 41.78% | 12119822 | 0.13103
GEN-2023-012 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2820.6136 | 0.3286% | 858333 | 0.05666
GEN-2023-012 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 1264692.0658 | 3.83% | 33016731.33 | 0.08521
GEN-2023-012 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 592600.4087 | 0.5156% | 114925066.48 | 0.02464
GEN-2023-012 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 1466958.9016 | 2.562% | 57267977.76 | 0.09995
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 8721617.8417 | 3.191% | 273358902 | 0.05127
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 34308492.5938 | 22.88% | 149959500 | 0.18604
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 12162717.775 | 3.379% | 359902800 | 0.07126
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 32745823.3592 | 9.926% | 329910900 | 0.19315
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 3591677.0038 | 2.395% | 149959500 | 0.025
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 3512315.5442 | 2.342% | 149959500 | 0.02401
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 12728549.661 | 3.265% | 389894700 | 0.08401
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 981966.9986 | 11.83% | 8302968 | 0.08044
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 12192.2198 | 0.1468% | 8302968 | 0.00127
GEN-2023-013 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 213587.2365 | 2.572% | 8302968 | 0.03718
GEN-2023-013 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 3.335% | 0 | 0.06697
GEN-2023-013 | 01 NORTH | 158698 | ERIS | Leland Olds to Groton 345 kV Line GEN-2023-013 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-013 (200MW/Wind), into Leland Olds to Groton 345 kV Line | 3685159 | 100% | 3685159 | 1
GEN-2023-013 | 01 NORTH | 158668 | ERIS | Leland Olds to Groton 345 kV Line Interconnection (DISIS-2023-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-013/014 (200MW/Wind), into Leland Olds to Groton 345 kV Line | 9951802 | 50% | 19903604 | 1
GEN-2023-013 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5998.0013 | 0.6988% | 858333 | 0.0594
GEN-2023-013 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 2941317.2712 | 8.909% | 33016731.33 | 0.0977
GEN-2023-013 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 27385.5263 | 3.323% | 823999.68 | 0.03809
GEN-2023-013 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 27007.5533 | 3.324% | 812555.24 | 0.03863
GEN-2023-013 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 3742681.9098 | 3.257% | 114925066.48 | 0.07672
GEN-2023-013 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 2788913.9276 | 4.87% | 57267977.76 | 0.09368
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 8721617.8417 | 3.191% | 273358902 | 0.05127
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 34308492.5938 | 22.88% | 149959500 | 0.18604
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 12162717.775 | 3.379% | 359902800 | 0.07126
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 32745823.3592 | 9.926% | 329910900 | 0.19315
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 3591677.0038 | 2.395% | 149959500 | 0.025
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 3512315.5442 | 2.342% | 149959500 | 0.02401
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 12728549.661 | 3.265% | 389894700 | 0.08401
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 981966.9986 | 11.83% | 8302968 | 0.08044
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 12192.2198 | 0.1468% | 8302968 | 0.00127
GEN-2023-014 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 213587.2365 | 2.572% | 8302968 | 0.03718
GEN-2023-014 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 3.335% | 0 | 0.06697
GEN-2023-014 | 01 NORTH | 158668 | ERIS | Leland Olds to Groton 345 kV Line Interconnection (DISIS-2023-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-013/014 (200MW/Wind), into Leland Olds to Groton 345 kV Line | 9951802 | 50% | 19903604 | 1
GEN-2023-014 | 01 NORTH | 158699 | ERIS | Leland Olds to Groton 345 kV Line GEN-2023-014 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-014 (200MW/Wind), into Leland Olds to Groton 345 kV Line | 120000 | 100% | 120000 | 1
GEN-2023-014 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5998.0013 | 0.6988% | 858333 | 0.0594
GEN-2023-014 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 2941317.2712 | 8.909% | 33016731.33 | 0.0977
GEN-2023-014 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 27385.5263 | 3.323% | 823999.68 | 0.03809
GEN-2023-014 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 27007.5533 | 3.324% | 812555.24 | 0.03863
GEN-2023-014 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 3742681.9098 | 3.257% | 114925066.48 | 0.07672
GEN-2023-014 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 2788913.9276 | 4.87% | 57267977.76 | 0.09368
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 211968.5428 | 5.677% | 3733650 | 0.05116
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 334446.0274 | 6.718% | 4978200 | 0.11601
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 17033266.9103 | 6.231% | 273358902 | 0.10013
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 1080669.5689 | 0.7206% | 149959500 | 0.00586
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 13697138.6675 | 3.806% | 359902800 | 0.08025
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 13869716.8471 | 4.204% | 329910900 | 0.08181
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 7350007.8205 | 4.901% | 149959500 | 0.05116
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 7339144.9752 | 4.894% | 149959500 | 0.05017
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 17098164.8524 | 4.385% | 389894700 | 0.11285
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 | Current Study | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 (4.2 miles) to a standard rating of 796 MVA | 225782.0406 | 4.644% | 4862281.2 | 0.02746
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 505144.1373 | 6.084% | 8302968 | 0.04138
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 21120.3807 | 0.2544% | 8302968 | 0.0022
GEN-2023-031 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 78644.6818 | 0.9472% | 8302968 | 0.01369
GEN-2023-031 | 01 NORTH | 143614 | ERIS | Whitlock - Glenham 230 kV Clearance Increase | Contingent | Increase ground clearance of the Whitlock - Glenham 230 kV. (NTC 210648) | 0 | 13.9% | 5845900 | 0.07405
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 3.782% | 0 | 0.07596
GEN-2023-031 | 01 NORTH | 158731 | ERIS | Washburn 230 kV Substation GEN-2023-031 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-031 (200MW/Solar), into Washburn 230 kV Substation | 28097000 | 100% | 28097000 | 1
GEN-2023-031 | 01 NORTH | 158730 | ERIS | Washburn 230 kV Substation GEN-2023-031 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-031 (200MW/Solar), into Washburn 230 kV Substation | 598000 | 100% | 598000 | 1
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to G23-098-TAP 230 kV line 1 (19.76 miles) to a standard rating of 796 MVA | 1023790.2342 | 5.864% | 17458137.84 | 0.04764
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to HETINGR4 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to HETINGR4 230 kV line 1 (37.09 miles) to a standard rating of 796 MVA | 1921679.1391 | 5.864% | 32769348.81 | 0.04764
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the CAMPBELL 4 to GLENHAM4 230kV line 1 | Current Study | Rebuild the existing CAMPBELL 4 to GLENHAM4 230 kV line 1 (14 miles) to a standard rating of 796 MVA | 1717969.4493 | 13.89% | 12369126 | 0.07439
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 6085.8508 | 0.709% | 858333 | 0.06027
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 1220481.0867 | 3.697% | 33016731.33 | 0.04054
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 62363.3645 | 7.568% | 823999.68 | 0.08674
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 61502.8336 | 7.569% | 812555.24 | 0.08797
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 8522992.1332 | 7.416% | 114925066.48 | 0.17471
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the G22-066-PROX to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing G22-066-PROX to G23-098-TAP 230 kV line 1 (15.35 miles) to a standard rating of 796 MVA | 433234.9369 | 3.195% | 13561863.15 | 0.04764
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the JAMESTN4 to G23-144-TAP 230kV line 1 | Current Study | Rebuild the existing JAMESTN4 to G23-144-TAP 230 kV line 1 (30.2 miles) to a standard rating of 796 MVA | 1227036.3084 | 4.599% | 26681971.8 | 0.04651
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the MAURINE4 to NUNDRWD-LNX3 230kV line 1 | Current Study | Rebuild the existing MAURINE4 to NUNDRWD-LNX3 230 kV line 1 (71.98 miles) to a standard rating of 796 MVA | 4516004.0421 | 7.101% | 63594977.82 | 0.03827
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 2431666.1999 | 4.246% | 57267977.76 | 0.08168
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1 | Current Study | Rebuild the existing SB.LS-WK-ER4 to WHITLOCK_-RM 230 kV line 1 (21.56 miles) to a standard rating of 796 MVA | 1494685.0535 | 7.847% | 19048454.04 | 0.07405
GEN-2023-031 | 01 NORTH | TBD | ERIS | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Current Study | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line 1 (4.2 miles) to a standard rating of 796 MVA | 170194.6425 | 4.587% | 3710737.8 | 0.02746
GEN-2023-031 | 01 NORTH | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation (NTC 210648) | 0 | 7.851% | 561800 | 0.0743
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 327813.7432 | 8.78% | 3733650 | 0.03956
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 620401.561 | 12.46% | 4978200 | 0.1076
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 27108972.4841 | 9.917% | 273358902 | 0.07968
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 1313031.9677 | 0.8756% | 149959500 | 0.00356
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 35812257.1366 | 9.951% | 359902800 | 0.10491
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 23572245.8186 | 7.145% | 329910900 | 0.06952
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 11366939.3815 | 7.58% | 149959500 | 0.03956
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 11281539.9738 | 7.523% | 149959500 | 0.03856
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 31644862.3045 | 8.116% | 389894700 | 0.10443
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 | Current Study | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 (4.2 miles) to a standard rating of 796 MVA | 253079.7964 | 5.205% | 4862281.2 | 0.01539
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 748804.77 | 9.019% | 8302968 | 0.03067
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 10944.1973 | 0.1318% | 8302968 | 0.00057
GEN-2023-054 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 327217.025 | 3.941% | 8302968 | 0.02848
GEN-2023-054 | 01 NORTH | 143614 | ERIS | Whitlock - Glenham 230 kV Clearance Increase | Contingent | Increase ground clearance of the Whitlock - Glenham 230 kV. (NTC 210648) | 0 | 11.08% | 5845900 | 0.02951
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 10.02% | 0 | 0.10062
GEN-2023-054 | 01 NORTH | 158767 | ERIS | LeLand Olds-Fort Thompson 345kV line GEN-2023-054 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-054 (400MW/Solar), into LeLand Olds-Fort Thompson 345kV line | 19903604 | 100% | 19903604 | 1
GEN-2023-054 | 01 NORTH | 158766 | ERIS | LeLand Olds-Fort Thompson 345kV line GEN-2023-054 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-054 (400MW/Solar), into LeLand Olds-Fort Thompson 345kV line | 3685159 | 100% | 3685159 | 1
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to G23-098-TAP 230 kV line 1 (19.76 miles) to a standard rating of 796 MVA | 1540842.9848 | 8.826% | 17458137.84 | 0.03585
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to HETINGR4 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to HETINGR4 230 kV line 1 (37.09 miles) to a standard rating of 796 MVA | 2892199.7118 | 8.826% | 32769348.81 | 0.03585
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the CAMPBELL 4 to GLENHAM4 230kV line 1 | Current Study | Rebuild the existing CAMPBELL 4 to GLENHAM4 230 kV line 1 (14 miles) to a standard rating of 796 MVA | 1378255.3668 | 11.14% | 12369126 | 0.02984
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 12369.6155 | 1.441% | 858333 | 0.06125
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 1026601.0128 | 3.109% | 33016731.33 | 0.01705
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 288795.4377 | 35.05% | 823999.68 | 0.20084
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 284785.316 | 35.05% | 812555.24 | 0.20367
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 39466951.4947 | 34.34% | 114925066.48 | 0.40451
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the G22-066-PROX to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing G22-066-PROX to G23-098-TAP 230 kV line 1 (15.35 miles) to a standard rating of 796 MVA | 652034.9491 | 4.808% | 13561863.15 | 0.03585
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 4733532.3921 | 8.266% | 57267977.76 | 0.0795
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1 | Current Study | Rebuild the existing SB.LS-WK-ER4 to WHITLOCK_-RM 230 kV line 1 (21.56 miles) to a standard rating of 796 MVA | 1191307.3849 | 6.254% | 19048454.04 | 0.02951
GEN-2023-054 | 01 NORTH | TBD | ERIS | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Current Study | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line 1 (4.2 miles) to a standard rating of 796 MVA | 190771.7078 | 5.141% | 3710737.8 | 0.01539
GEN-2023-054 | 01 NORTH | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation (NTC 210648) | 0 | 6.287% | 561800 | 0.02975
GEN-2023-062 | 01 NORTH | 158780 | ERIS | REN 115 kV Substation GEN-2023-062 Interconnection (Non-Shared NU) (LYREC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-062 (98MW/Thermal), into REN 115 kV Substation | 4940802 | 100% | 4940802 | 1
GEN-2023-062 | 01 NORTH | 158779 | ERIS | REN 115 kV Substation GEN-2023-062 Interconnection (TOIF) (LYREC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-062 (98MW/Thermal), into REN 115 kV Substation | 407172 | 100% | 407172 | 1
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 38322.9679 | 1.026% | 3733650 | 0.01423
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 351860.2264 | 7.068% | 4978200 | 0.18777
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 7131925.6488 | 2.609% | 273358902 | 0.0645
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 9734099.8797 | 2.705% | 359902800 | 0.08774
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 3728005.6058 | 1.13% | 329910900 | 0.03383
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2 | Current Study | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2 (5.25 miles) to a standard rating of 239 MVA | 4560633.8174 | 96.65% | 4718526.75 | 0.45196
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 1328848.6578 | 0.8861% | 149959500 | 0.01423
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 1448153.5914 | 0.9657% | 149959500 | 0.01523
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 18179962.7881 | 4.663% | 389894700 | 0.1846
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 224893.6538 | 2.709% | 8302968 | 0.03604
GEN-2023-066 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 807412.0306 | 9.724% | 8302968 | 0.21623
GEN-2023-066 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 2.701% | 0 | 0.08346
GEN-2023-066 | 01 NORTH | 158788 | ERIS | Tap Pierre - Midland 115 kV line GEN-2023-066 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-066 (130MW/Hybrid), into Tap Pierre - Midland 115 kV line | 16835000 | 100% | 16835000 | 1
GEN-2023-066 | 01 NORTH | 158787 | ERIS | Tap Pierre - Midland 115 kV line GEN-2023-066 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-066 (130MW/Hybrid), into Tap Pierre - Midland 115 kV line | 355000 | 100% | 355000 | 1
GEN-2023-066 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 4566.862 | 0.5321% | 858333 | 0.06958
GEN-2023-066 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 1391331.0462 | 2.43% | 57267977.76 | 0.0719
GEN-2023-066 | 01 NORTH | TBD | ERIS | Rebuild the SIDNEY___TS4 to SIDNEY__-MB4 230kV line 1 | Current Study | Rebuild the existing SIDNEY___TS4 to SIDNEY__-MB4 230 kV line 1 (4 miles) to a standard rating of 796 MVA | 904461.9955 | 25.59% | 3534036 | 0.02325
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 134751.8747 | 3.609% | 3733650 | 0.15865
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 118246.4618 | 2.375% | 4978200 | 0.20008
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 4427109.8874 | 1.62% | 273358902 | 0.12695
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 2524147.9702 | 0.7013% | 359902800 | 0.07214
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 1262295.1199 | 0.3826% | 329910900 | 0.03632
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2 | Current Study | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2 (5.25 miles) to a standard rating of 239 MVA | 46273.2618 | 0.9807% | 4718526.75 | 0.01454
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 4672520.3645 | 3.116% | 149959500 | 0.15865
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 4727692.2881 | 3.153% | 149959500 | 0.15765
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 6116340.0767 | 1.569% | 389894700 | 0.19692
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 874299.7596 | 10.53% | 8302968 | 0.44425
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 138045.2569 | 1.663% | 8302968 | 0.11722
GEN-2023-067 | 01 NORTH | TBD | ERIS | Build a new Wayside 230/115 kV transformer 2 | Current Study | Build Wayside 230/115kV Transformer Ckt 2 | 1515603.2731 | 22.89% | 6621188 | 0.0276
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 0.6927% | 0 | 0.06786
GEN-2023-067 | 01 NORTH | 158790 | ERIS | Sulphur 115 kV Substation GEN-2023-067 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-067 (41MW/Wind), into Sulphur 115 kV Substation | 2137600 | 100% | 2137600 | 1
GEN-2023-067 | 01 NORTH | 158789 | ERIS | Sulphur 115 kV Substation GEN-2023-067 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-067 (41MW/Wind), into Sulphur 115 kV Substation | 232000 | 100% | 232000 | 1
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the CHADRON7 to WAYSIDE7 115kV line 1 | Current Study | Rebuild the existing CHADRON7 to WAYSIDE7 115 kV line 1 (16.2 miles) to a standard rating of 239 MVA | 2636314.0764 | 22.89% | 11515608 | 0.05521
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the ELKCRK 7 to NEWELL 7 115kV line 1 | Current Study | Rebuild the existing ELKCRK 7 to NEWELL 7 115 kV line 1 (26 miles) to a standard rating of 239 MVA | 14091146.6295 | 76.24% | 18481840 | 0.39686
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the ELKCRK 7 to RAPIDCY7 115kV line 1 | Current Study | Rebuild the existing ELKCRK 7 to RAPIDCY7 115 kV line 1 (10 miles) to a standard rating of 239 MVA | 7108400 | 100% | 7108400 | 0.15028
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 1553.548 | 0.181% | 858333 | 0.07505
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 374724.3181 | 0.3261% | 114925066.48 | 0.03747
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the GENTLMN4 to OGALALA4 230kV line 1 | Current Study | Rebuild the existing GENTLMN4 to OGALALA4 230 kV line 1 (30.09 miles) to a standard rating of 796 MVA | 6119813.7579 | 23.02% | 26584785.81 | 0.04665
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the MAURINE4 to NUNDRWD-LNX3 230kV line 1 | Current Study | Rebuild the existing MAURINE4 to NUNDRWD-LNX3 230 kV line 1 (71.98 miles) to a standard rating of 796 MVA | 792489.6772 | 1.246% | 63594977.82 | 0.03276
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the MAURINE7 to SULPHUR 115kV line 1 | Current Study | Rebuild the existing MAURINE7 to SULPHUR 115 kV line 1 (34.16 miles) to a standard rating of 239 MVA | 24282294.4 | 100% | 24282294.4 | 0.60314
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the NEWELL 7 to SULPHUR 115kV line 1 | Current Study | Rebuild the existing NEWELL 7 to SULPHUR 115 kV line 1 (17.52 miles) to a standard rating of 239 MVA | 9495264.9596 | 76.24% | 12453916.8 | 0.39686
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1 | Current Study | Rebuild the existing OGALALA4 to SIDNEY___TS4 230 kV line 1 (68.85 miles) to a standard rating of 796 MVA | 1908382.7588 | 3.137% | 60829594.65 | 0.04675
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the RAPIDCY7 to RUSHMORE-RM7 115kV line 1 | Current Study | Rebuild the existing RAPIDCY7 to RUSHMORE-RM7 115 kV line 1 (4.99 miles) to a standard rating of 239 MVA | 3547091.6 | 100% | 3547091.6 | 0.15028
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 388943.0438 | 0.6792% | 57267977.76 | 0.06373
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the SCOTBLF7 to VICTRYH7 115kV line 1 | Current Study | Rebuild the existing SCOTBLF7 to VICTRYH7 115 kV line 1 (8.09 miles) to a standard rating of 239 MVA | 1290339.9828 | 22.44% | 5750695.6 | 0.00985
GEN-2023-067 | 01 NORTH | TBD | ERIS | Rebuild the SIDNEY___TS4 to SIDNEY__-MB4 230kV line 1 | Current Study | Rebuild the existing SIDNEY___TS4 to SIDNEY__-MB4 230 kV line 1 (4 miles) to a standard rating of 796 MVA | 596516.9995 | 16.88% | 3534036 | 0.04862
GEN-2023-082 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 3989115.2407 | 1.459% | 273358902 | 0.0268
GEN-2023-082 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 9011522.4772 | 2.504% | 359902800 | 0.06034
GEN-2023-082 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 10496803.7965 | 3.182% | 329910900 | 0.07076
GEN-2023-082 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 1567587.4283 | 1.045% | 149959500 | 0.01247
GEN-2023-082 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 1468158.1375 | 0.979% | 149959500 | 0.01147
GEN-2023-082 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 9017634.2632 | 2.313% | 389894700 | 0.06802
GEN-2023-082 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 15540.2801 | 0.1872% | 8302968 | 0.00185
GEN-2023-082 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 232480.0559 | 2.8% | 8302968 | 0.04625
GEN-2023-082 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 2.443% | 0 | 0.05606
GEN-2023-082 | 01 NORTH | 158811 | ERIS | White 115 kV Substation GEN-2023-082 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-082 (175MW/Battery/Storage), into White 115 kV Substation | 0 | 100% | 0 | 1
GEN-2023-082 | 01 NORTH | 158810 | ERIS | White 115 kV Substation GEN-2023-082 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-082 (175MW/Battery/Storage), into White 115 kV Substation | 4105000 | 100% | 4105000 | 1
GEN-2023-082 | 01 NORTH | TBD | ERIS | Rebuild the AURORA 7 to BROOKNG7 115kV line 1 | Current Study | Rebuild the existing AURORA 7 to BROOKNG7 115 kV line 1 (11 miles) to a standard rating of 239 MVA | 4552068.7451 | 58.22% | 7819240 | 0.10286
GEN-2023-082 | 01 NORTH | TBD | ERIS | Rebuild the AURORA 7 to FLANDRU7 115kV line 1 | Current Study | Rebuild the existing AURORA 7 to FLANDRU7 115 kV line 1 (17.05 miles) to a standard rating of 239 MVA | 7055706.555 | 58.22% | 12119822 | 0.10286
GEN-2023-082 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 4939.8943 | 0.5755% | 858333 | 0.05591
GEN-2023-082 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 1648244.0527 | 4.992% | 33016731.33 | 0.06257
GEN-2023-082 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 924572.1962 | 0.8045% | 114925066.48 | 0.02166
GEN-2023-082 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 2676566.9599 | 4.674% | 57267977.76 | 0.10275
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 3602962.0809 | 1.318% | 273358902 | 0.04236
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 16876702.3206 | 11.25% | 149959500 | 0.18303
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 5945667.6073 | 1.652% | 359902800 | 0.06967
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 16455136.5014 | 4.988% | 329910900 | 0.19412
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 1463967.5467 | 0.9762% | 149959500 | 0.02038
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 1417506.7732 | 0.9453% | 149959500 | 0.01938
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 6087764.8539 | 1.561% | 389894700 | 0.08036
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 435988.9527 | 5.251% | 8302968 | 0.07143
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 7632.1376 | 0.09192% | 8302968 | 0.00159
GEN-2023-084 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 122850.0014 | 1.48% | 8302968 | 0.04277
GEN-2023-084 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 1.628% | 0 | 0.06538
GEN-2023-084 | 01 NORTH | 158815 | ERIS | Groton South 115 kV Substation GEN-2023-084 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-084 (100MW/Hybrid), into Groton South 115 kV Substation | 3255000 | 100% | 3255000 | 1
GEN-2023-084 | 01 NORTH | 158814 | ERIS | Groton South 115 kV Substation GEN-2023-084 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-084 (100MW/Hybrid), into Groton South 115 kV Substation | 260000 | 100% | 260000 | 1
GEN-2023-084 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2981.3298 | 0.3473% | 858333 | 0.05905
GEN-2023-084 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 1624799.3155 | 4.921% | 33016731.33 | 0.10794
GEN-2023-084 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 9993.6681 | 1.213% | 823999.68 | 0.0278
GEN-2023-084 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 9854.2962 | 1.213% | 812555.24 | 0.02819
GEN-2023-084 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 1365454.4663 | 1.188% | 114925066.48 | 0.05598
GEN-2023-084 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 1413510.1759 | 2.468% | 57267977.76 | 0.09496
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 422248.7122 | 11.31% | 3733650 | 0.08153
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 479463.4508 | 9.631% | 4978200 | 0.13305
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 33830929.3597 | 12.38% | 273358902 | 0.1591
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 1242493.3823 | 0.8286% | 149959500 | 0.00539
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 16820598.3263 | 4.674% | 359902800 | 0.07884
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 16266951.8577 | 4.931% | 329910900 | 0.07676
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 14641471.3058 | 9.764% | 149959500 | 0.08153
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 14729124.1716 | 9.822% | 149959500 | 0.08055
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 24601812.2987 | 6.31% | 389894700 | 0.1299
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 | Current Study | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 (4.2 miles) to a standard rating of 796 MVA | 169069.3084 | 3.477% | 4862281.2 | 0.01645
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 665763.615 | 8.018% | 8302968 | 0.04363
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 47640.8587 | 0.5738% | 8302968 | 0.00397
GEN-2023-097 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 215497.3429 | 2.595% | 8302968 | 0.03001
GEN-2023-097 | 01 NORTH | 143614 | ERIS | Whitlock - Glenham 230 kV Clearance Increase | Contingent | Increase ground clearance of the Whitlock - Glenham 230 kV. (NTC 210648) | 0 | 9.333% | 5845900 | 0.03977
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 4.64% | 0 | 0.07454
GEN-2023-097 | 01 NORTH | 158834 | ERIS | Judson 345 kV Substation GEN-2023-097 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-097 (250MW/Battery/Storage), into Judson 345 kV Substation | 3039889 | 100% | 3039889 | 1
GEN-2023-097 | 01 NORTH | 158833 | ERIS | Judson 345 kV Substation GEN-2023-097 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-097 (250MW/Battery/Storage), into Judson 345 kV Substation | 2909909 | 100% | 2909909 | 1
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to G23-098-TAP 230 kV line 1 (19.76 miles) to a standard rating of 796 MVA | 1907249.8591 | 10.92% | 17458137.84 | 0.071
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to HETINGR4 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to HETINGR4 230 kV line 1 (37.09 miles) to a standard rating of 796 MVA | 3579954.3155 | 10.92% | 32769348.81 | 0.071
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the CAMPBELL 4 to GLENHAM4 230kV line 1 | Current Study | Rebuild the existing CAMPBELL 4 to GLENHAM4 230 kV line 1 (14 miles) to a standard rating of 796 MVA | 1157591.3247 | 9.359% | 12369126 | 0.0401
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7790.3334 | 0.9076% | 858333 | 0.06172
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 70647.684 | 8.574% | 823999.68 | 0.07861
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 69659.9817 | 8.573% | 812555.24 | 0.07971
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 9654285.0619 | 8.401% | 114925066.48 | 0.15832
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the G22-066-PROX to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing G22-066-PROX to G23-098-TAP 230 kV line 1 (15.35 miles) to a standard rating of 796 MVA | 807086.4955 | 5.951% | 13561863.15 | 0.071
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the MAURINE4 to NUNDRWD-LNX3 230kV line 1 | Current Study | Rebuild the existing MAURINE4 to NUNDRWD-LNX3 230 kV line 1 (71.98 miles) to a standard rating of 796 MVA | 8095058.1993 | 12.73% | 63594977.82 | 0.05488
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 2946921.6205 | 5.146% | 57267977.76 | 0.07919
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1 | Current Study | Rebuild the existing SB.LS-WK-ER4 to WHITLOCK_-RM 230 kV line 1 (21.56 miles) to a standard rating of 796 MVA | 1003437.2818 | 5.268% | 19048454.04 | 0.03977
GEN-2023-097 | 01 NORTH | TBD | ERIS | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Current Study | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line 1 (4.2 miles) to a standard rating of 796 MVA | 127444.5498 | 3.434% | 3710737.8 | 0.01645
GEN-2023-097 | 01 NORTH | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation (NTC 210648) | 0 | 5.285% | 561800 | 0.04001
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 803499.9902 | 21.52% | 3733650 | 0.19393
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 620661.0226 | 12.47% | 4978200 | 0.21529
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 18780312.2631 | 6.87% | 273358902 | 0.1104
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 12575765.4458 | 3.494% | 359902800 | 0.07368
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 7423968.9614 | 2.25% | 329910900 | 0.04379
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2 | Current Study | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2 (5.25 miles) to a standard rating of 239 MVA | 111619.6707 | 2.366% | 4718526.75 | 0.00719
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 27861356.8535 | 18.58% | 149959500 | 0.19393
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 28222867.0534 | 18.82% | 149959500 | 0.19293
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 32140307.5776 | 8.243% | 389894700 | 0.21213
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 4783286.2205 | 57.61% | 8302968 | 0.49825
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 991302.1391 | 11.94% | 8302968 | 0.17256
GEN-2023-098 | 01 NORTH | TBD | ERIS | Build a new Wayside 230/115 kV transformer 2 | Current Study | Build Wayside 230/115kV Transformer Ckt 2 | 5105584.7269 | 77.11% | 6621188 | 0.01906
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 3.456% | 0 | 0.0694
GEN-2023-098 | 01 NORTH | 158836 | ERIS | Bison - Maurine 230 kV Line GEN-2023-098 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-098 (200MW/Hybrid), into Bison - Maurine 230 kV Line | 21760000 | 100% | 21760000 | 1
GEN-2023-098 | 01 NORTH | 158835 | ERIS | Bison - Maurine 230 kV Line GEN-2023-098 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-098 (200MW/Hybrid), into Bison - Maurine 230 kV Line | 595000 | 100% | 595000 | 1
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the CHADRON7 to WAYSIDE7 115kV line 1 | Current Study | Rebuild the existing CHADRON7 to WAYSIDE7 115 kV line 1 (16.2 miles) to a standard rating of 239 MVA | 8879293.9236 | 77.11% | 11515608 | 0.03812
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the ELKCRK 7 to NEWELL 7 115kV line 1 | Current Study | Rebuild the existing ELKCRK 7 to NEWELL 7 115 kV line 1 (26 miles) to a standard rating of 239 MVA | 4390693.3705 | 23.76% | 18481840 | 0.02535
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7272.3242 | 0.8473% | 858333 | 0.07202
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 20691.9257 | 2.511% | 823999.68 | 0.02878
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 20400.7353 | 2.511% | 812555.24 | 0.02918
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 2827500.5669 | 2.46% | 114925066.48 | 0.05796
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the G22-066-PROX to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing G22-066-PROX to G23-098-TAP 230 kV line 1 (15.35 miles) to a standard rating of 796 MVA | 6877559.1531 | 50.71% | 13561863.15 | 0.75628
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the GENTLMN4 to OGALALA4 230kV line 1 | Current Study | Rebuild the existing GENTLMN4 to OGALALA4 230 kV line 1 (30.09 miles) to a standard rating of 796 MVA | 20464972.0521 | 76.98% | 26584785.81 | 0.03198
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the MAURINE4 to NUNDRWD-LNX3 230kV line 1 | Current Study | Rebuild the existing MAURINE4 to NUNDRWD-LNX3 230 kV line 1 (71.98 miles) to a standard rating of 796 MVA | 23863901.161 | 37.52% | 63594977.82 | 0.20223
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the NEWELL 7 to SULPHUR 115kV line 1 | Current Study | Rebuild the existing NEWELL 7 to SULPHUR 115 kV line 1 (17.52 miles) to a standard rating of 239 MVA | 2958651.8404 | 23.76% | 12453916.8 | 0.02535
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1 | Current Study | Rebuild the existing OGALALA4 to SIDNEY___TS4 230 kV line 1 (68.85 miles) to a standard rating of 796 MVA | 6505476.951 | 10.69% | 60829594.65 | 0.03267
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 1982129.4759 | 3.461% | 57267977.76 | 0.06658
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the SCOTBLF7 to VICTRYH7 115kV line 1 | Current Study | Rebuild the existing SCOTBLF7 to VICTRYH7 115 kV line 1 (8.09 miles) to a standard rating of 239 MVA | 4460355.6172 | 77.56% | 5750695.6 | 0.00698
GEN-2023-098 | 01 NORTH | TBD | ERIS | Rebuild the SIDNEY___TS4 to SIDNEY__-MB4 230kV line 1 | Current Study | Rebuild the existing SIDNEY___TS4 to SIDNEY__-MB4 230 kV line 1 (4 miles) to a standard rating of 796 MVA | 2033057.005 | 57.53% | 3534036 | 0.03397
GEN-2023-105 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 1198724.877 | 0.4385% | 273358902 | 0.00566
GEN-2023-105 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 33213385.0878 | 9.228% | 359902800 | 0.1563
GEN-2023-105 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 5249359.775 | 1.591% | 329910900 | 0.02487
GEN-2023-105 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 66180.2405 | 0.04413% | 149959500 | 0.00037
GEN-2023-105 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 15565981.4063 | 3.992% | 389894700 | 0.08252
GEN-2023-105 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 58804.9 | 0.7082% | 8302968 | 0.00492
GEN-2023-105 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 607573.2517 | 7.318% | 8302968 | 0.08495
GEN-2023-105 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 9.424% | 0 | 0.15202
GEN-2023-105 | 01 NORTH | 158847 | ERIS | Chappelle Creek 345 kV Substation GEN-2023-105 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-105 (249MW/Wind), into Chappelle Creek 345 Kv Substation | 1673527 | 100% | 1673527 | 1
GEN-2023-105 | 01 NORTH | 158661 | ERIS | Chappelle Creek 345 kV Substation Interconnection (DISIS-2023-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-105/106 (249/504MW/Wind), into Chappelle Creek 345 kV Substation | 3187046.2351 | 33.07% | 9637935 | 1
GEN-2023-105 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7835.8586 | 0.9129% | 858333 | 0.06233
GEN-2023-105 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 2747217.1636 | 4.797% | 57267977.76 | 0.07412
GEN-2023-105 | 01 NORTH | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 10680.8826 | 0.9175% | 1164086.56 | 0.01115
GEN-2023-106 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 2426334.6909 | 0.8876% | 273358902 | 0.00566
GEN-2023-106 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 67227092.7078 | 18.68% | 359902800 | 0.1563
GEN-2023-106 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 10625210.147 | 3.221% | 329910900 | 0.02487
GEN-2023-106 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 133955.1855 | 0.08933% | 149959500 | 0.00037
GEN-2023-106 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 31507046.702 | 8.081% | 389894700 | 0.08252
GEN-2023-106 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 119026.7855 | 1.434% | 8302968 | 0.00492
GEN-2023-106 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 1229786.8227 | 14.81% | 8302968 | 0.08495
GEN-2023-106 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 19.08% | 0 | 0.15202
GEN-2023-106 | 01 NORTH | 158661 | ERIS | Chappelle Creek 345 kV Substation Interconnection (DISIS-2023-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-105/106 (249/504MW/Wind), into Chappelle Creek 345 kV Substation | 6450888.7649 | 66.93% | 9637935 | 1
GEN-2023-106 | 01 NORTH | 158848 | ERIS | Chappelle Creek 345 kV Substation GEN-2023-106 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-106 (504MW/Wind), into Chappelle Creek 345 kV Substation | 120000 | 100% | 120000 | 1
GEN-2023-106 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 15860.5331 | 1.848% | 858333 | 0.06233
GEN-2023-106 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 5560632.3312 | 9.71% | 57267977.76 | 0.07412
GEN-2023-106 | 01 NORTH | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 21619.1359 | 1.857% | 1164086.56 | 0.01115
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 319599.755 | 8.56% | 3733650 | 0.0363
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 602448.2584 | 12.1% | 4978200 | 0.09834
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 25473988.0979 | 9.319% | 273358902 | 0.07047
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 24039545.1168 | 6.679% | 359902800 | 0.06628
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 26036235.517 | 7.892% | 329910900 | 0.07227
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 11082119.3951 | 7.39% | 149959500 | 0.0363
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 10973243.2221 | 7.317% | 149959500 | 0.0353
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 30641282.6019 | 7.859% | 389894700 | 0.09517
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 | Current Study | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 (4.2 miles) to a standard rating of 796 MVA | 2486120.5002 | 51.13% | 4862281.2 | 0.14229
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 643851.2484 | 7.754% | 8302968 | 0.02482
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new Fargo 115/69 kV transformer 2 | Current Study | Build Fargo 115/69kV Transformer Ckt 2 | 1823573.6519 | 65.65% | 2777743 | 0.00429
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 43656.7869 | 0.5258% | 8302968 | 0.00214
GEN-2023-114 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 314097.61 | 3.783% | 8302968 | 0.02573
GEN-2023-114 | 01 NORTH | 143614 | ERIS | Whitlock - Glenham 230 kV Clearance Increase | Contingent | Increase ground clearance of the Whitlock - Glenham 230 kV. (NTC 210648) | 0 | 29.27% | 5845900 | 0.07337
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 6.56% | 0 | 0.062
GEN-2023-114 | 01 NORTH | 158856 | ERIS | Jamestown 230 kV Substation GEN-2023-114 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-114 (425MW/Wind), into Jamestown 230 kV Substation | 0 | 100% | 0 | 1
GEN-2023-114 | 01 NORTH | 158855 | ERIS | Jamestown 230 kV Substation GEN-2023-114 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-114 (425MW/Wind), into Jamestown 230 kV Substation | 100000 | 100% | 100000 | 1
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to G23-098-TAP 230 kV line 1 (19.76 miles) to a standard rating of 796 MVA | 1662262.2716 | 9.521% | 17458137.84 | 0.0364
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to HETINGR4 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to HETINGR4 230 kV line 1 (37.09 miles) to a standard rating of 796 MVA | 3120106.6626 | 9.521% | 32769348.81 | 0.0364
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the CAMPBELL 4 to GLENHAM4 230kV line 1 | Current Study | Rebuild the existing CAMPBELL 4 to GLENHAM4 230 kV line 1 (14 miles) to a standard rating of 796 MVA | 3616823.3685 | 29.24% | 12369126 | 0.0737
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the FARGO 8 to DELVO 8 69kV line 1 | Current Study | Rebuild the existing FARGO 8 to DELVO 8 69 kV line 1 (0.01 miles) to a standard rating of 71 MVA | 5964.3568 | 65.62% | 9089.49 | 0.00858
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 12177.1291 | 1.419% | 858333 | 0.05675
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 75947.3837 | 9.217% | 823999.68 | 0.04971
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 74892.1271 | 9.217% | 812555.24 | 0.05041
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 10377929.5846 | 9.03% | 114925066.48 | 0.10011
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the GRNDFKS4 to PICKERT4 230kV line 1 | Current Study | Rebuild the existing GRNDFKS4 to PICKERT4 230 kV line 1 (49 miles) to a standard rating of 796 MVA | 28518050.0993 | 65.87% | 43291941 | 0.14714
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the JAMESTN4 to PICKERT4 230kV line 1 | Current Study | Rebuild the existing JAMESTN4 to PICKERT4 230 kV line 1 (61.36 miles) to a standard rating of 796 MVA | 35711582.7366 | 65.87% | 54212112.24 | 0.14714
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 5264715.1072 | 9.193% | 57267977.76 | 0.08322
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1 | Current Study | Rebuild the existing SB.LS-WK-ER4 to WHITLOCK_-RM 230 kV line 1 (21.56 miles) to a standard rating of 796 MVA | 3147038.6906 | 16.52% | 19048454.04 | 0.07337
GEN-2023-114 | 01 NORTH | TBD | ERIS | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Current Study | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line 1 (4.2 miles) to a standard rating of 796 MVA | 1874039.1779 | 50.5% | 3710737.8 | 0.14229
GEN-2023-114 | 01 NORTH | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation (NTC 210648) | 0 | 16.53% | 561800 | 0.07361
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 43633.3682 | 1.169% | 3733650 | 0.02194
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 244544.306 | 4.912% | 4978200 | 0.17672
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 2523094.1258 | 0.923% | 273358902 | 0.0309
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 7196451.0538 | 2% | 359902800 | 0.08784
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 3398309.5008 | 1.03% | 329910900 | 0.04176
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 1512986.7545 | 1.009% | 149959500 | 0.02194
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 1610779.2137 | 1.074% | 149959500 | 0.02294
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 12621581.966 | 3.237% | 389894700 | 0.17355
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 59812.9181 | 0.7204% | 8302968 | 0.01298
GEN-2023-130 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 608292.773 | 7.326% | 8302968 | 0.2206
GEN-2023-130 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 1.997% | 0 | 0.08355
GEN-2023-130 | 01 NORTH | 158873 | ERIS | Whitlock 230 kV Substation GEN-2023-130 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-130 (96MW/Hybrid), into Whitlock 230 kV Substation | 2498712 | 100% | 2498712 | 1
GEN-2023-130 | 01 NORTH | 158872 | ERIS | Whitlock 230 kV Substation GEN-2023-130 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-130 (96MW/Hybrid), into Whitlock 230 kV Substation | 2112076 | 100% | 2112076 | 1
GEN-2023-130 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3230.9234 | 0.3764% | 858333 | 0.06666
GEN-2023-130 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 426642.3216 | 0.3712% | 114925066.48 | 0.01822
GEN-2023-130 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 1072171.8804 | 1.872% | 57267977.76 | 0.07503
GEN-2023-130 | 01 NORTH | TBD | ERIS | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1 | Current Study | Rebuild the existing SB.LS-WK-ER4 to WHITLOCK_-RM 230 kV line 1 (21.56 miles) to a standard rating of 796 MVA | 7526188.3562 | 39.51% | 19048454.04 | 0.7768
GEN-2023-130 | 01 NORTH | TBD | ERIS | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Current Study | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line 1 (4.2 miles) to a standard rating of 796 MVA | 45547.2101 | 1.227% | 3710737.8 | 0.01531
GEN-2023-130 | 01 NORTH | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation (NTC 210648) | 0 | 39.41% | 561800 | 0.77704
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 208392.9202 | 5.581% | 3733650 | 0.03796
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 390961.8132 | 7.853% | 4978200 | 0.10235
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 16562228.1 | 6.059% | 273358902 | 0.07348
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 15414529.4373 | 4.283% | 359902800 | 0.06816
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 16301749.0632 | 4.941% | 329910900 | 0.07257
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 7226023.1303 | 4.819% | 149959500 | 0.03796
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 7163894.9118 | 4.777% | 149959500 | 0.03696
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 19908756.1909 | 5.106% | 389894700 | 0.09917
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 | Current Study | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 (4.2 miles) to a standard rating of 796 MVA | 1308094.8922 | 26.9% | 4862281.2 | 0.12007
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 418605.5489 | 5.042% | 8302968 | 0.02588
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new Fargo 115/69 kV transformer 2 | Current Study | Build Fargo 115/69kV Transformer Ckt 2 | 954169.3481 | 34.35% | 2777743 | 0.0036
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 31037.3595 | 0.3738% | 8302968 | 0.00244
GEN-2023-144 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 201177.2896 | 2.423% | 8302968 | 0.02643
GEN-2023-144 | 01 NORTH | 143614 | ERIS | Whitlock - Glenham 230 kV Clearance Increase | Contingent | Increase ground clearance of the Whitlock - Glenham 230 kV. (NTC 210648) | 0 | 21.15% | 5845900 | 0.08503
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 4.215% | 0 | 0.06388
GEN-2023-144 | 01 NORTH | 158891 | ERIS | Bismarck - Jamestown 230 kV GEN-2023-144 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-144 (265MW/Solar), into Bismarck - Jamestown 230 kV | 21800000 | 100% | 21800000 | 1
GEN-2023-144 | 01 NORTH | 158890 | ERIS | Bismarck - Jamestown 230 kV GEN-2023-144 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-144 (265MW/Solar), into Bismarck - Jamestown 230 kV | 595000 | 100% | 595000 | 1
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to G23-098-TAP 230 kV line 1 (19.76 miles) to a standard rating of 796 MVA | 1088292.8872 | 6.234% | 17458137.84 | 0.03822
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to HETINGR4 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to HETINGR4 230 kV line 1 (37.09 miles) to a standard rating of 796 MVA | 2042752.1856 | 6.234% | 32769348.81 | 0.03822
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the CAMPBELL 4 to GLENHAM4 230kV line 1 | Current Study | Rebuild the existing CAMPBELL 4 to GLENHAM4 230 kV line 1 (14 miles) to a standard rating of 796 MVA | 2611987.9104 | 21.12% | 12369126 | 0.08536
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the FARGO 8 to DELVO 8 69kV line 1 | Current Study | Rebuild the existing FARGO 8 to DELVO 8 69 kV line 1 (0.01 miles) to a standard rating of 71 MVA | 3125.1332 | 34.38% | 9089.49 | 0.00721
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7677.0883 | 0.8944% | 858333 | 0.05738
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 50032.3285 | 6.072% | 823999.68 | 0.05252
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 49337.5494 | 6.072% | 812555.24 | 0.05326
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 6836797.3399 | 5.949% | 114925066.48 | 0.10577
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the G22-066-PROX to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing G22-066-PROX to G23-098-TAP 230 kV line 1 (15.35 miles) to a standard rating of 796 MVA | 460530.3748 | 3.396% | 13561863.15 | 0.03822
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the GRNDFKS4 to PICKERT4 230kV line 1 | Current Study | Rebuild the existing GRNDFKS4 to PICKERT4 230 kV line 1 (49 miles) to a standard rating of 796 MVA | 14773890.9007 | 34.13% | 43291941 | 0.12225
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the JAMESTN4 to G23-144-TAP 230kV line 1 | Current Study | Rebuild the existing JAMESTN4 to G23-144-TAP 230 kV line 1 (30.2 miles) to a standard rating of 796 MVA | 23969617.406 | 89.83% | 26681971.8 | 0.6857
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the JAMESTN4 to PICKERT4 230kV line 1 | Current Study | Rebuild the existing JAMESTN4 to PICKERT4 230 kV line 1 (61.36 miles) to a standard rating of 796 MVA | 18500529.5034 | 34.13% | 54212112.24 | 0.12225
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 3269687.4998 | 5.709% | 57267977.76 | 0.08289
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1 | Current Study | Rebuild the existing SB.LS-WK-ER4 to WHITLOCK_-RM 230 kV line 1 (21.56 miles) to a standard rating of 796 MVA | 2274116.3792 | 11.94% | 19048454.04 | 0.08503
GEN-2023-144 | 01 NORTH | TBD | ERIS | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Current Study | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line 1 (4.2 miles) to a standard rating of 796 MVA | 986042.7426 | 26.57% | 3710737.8 | 0.12007
GEN-2023-144 | 01 NORTH | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation (NTC 210648) | 0 | 11.94% | 561800 | 0.08527
GEN-2023-154 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 2058349.4419 | 0.753% | 273358902 | 0.0121
GEN-2023-154 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 16050827.6672 | 4.46% | 359902800 | 0.09404
GEN-2023-154 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 11869195.4097 | 3.598% | 329910900 | 0.07001
GEN-2023-154 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 515764.8177 | 0.3439% | 149959500 | 0.00359
GEN-2023-154 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 378879.5193 | 0.2527% | 149959500 | 0.00259
GEN-2023-154 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 14445184.2005 | 3.705% | 389894700 | 0.09534
GEN-2023-154 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 47232.8514 | 0.5689% | 8302968 | 0.00492
GEN-2023-154 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 524661.7082 | 6.319% | 8302968 | 0.09133
GEN-2023-154 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 4.469% | 0 | 0.08976
GEN-2023-154 | 01 NORTH | 158911 | ERIS | Fort Thompson - Huron 230 kV Tap GEN-2023-154 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-154 (200MW/Solar), into Fort Thompson - Huron 230 kV Tap | 592000 | 100% | 592000 | 1
GEN-2023-154 | 01 NORTH | 158910 | ERIS | Fort Thompson - Huron 230 kV Tap GEN-2023-154 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-154 (200MW/Solar), into Fort Thompson - Huron 230 kV Tap | 8683000 | 100% | 8683000 | 1
GEN-2023-154 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 6212.0714 | 0.7237% | 858333 | 0.06152
GEN-2023-154 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 15011556.0997 | 45.47% | 33016731.33 | 0.49863
GEN-2023-154 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to HURON 4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to HURON 4 230 kV line 1 (21.91 miles) to a standard rating of 796 MVA | 19357682.19 | 100% | 19357682.19 | 0.50137
GEN-2023-154 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 2603145.1092 | 4.546% | 57267977.76 | 0.08744
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 791277.41 | 21.19% | 3733650 | 0.12732
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 719703.2885 | 14.46% | 4978200 | 0.16643
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 35718316.7199 | 13.07% | 273358902 | 0.13998
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new BOWMAN__-BE4 to HETINGR4 230 kV line 2 | Current Study | Build a new BOWMAN__-BE4 to HETINGR4 230 kV line 2 (36.35 miles) to a standard rating of 796 MVA | 42081886.1 | 100% | 42081886.1 | 0.15326
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 2857504.2611 | 1.906% | 149959500 | 0.01033
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 19711078.617 | 5.477% | 359902800 | 0.07699
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 16496672.7516 | 5% | 329910900 | 0.06487
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 27437538.967 | 18.3% | 149959500 | 0.12732
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 27720376.2622 | 18.49% | 149959500 | 0.12633
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 37106123.7321 | 9.517% | 389894700 | 0.16327
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 | Current Study | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 (4.2 miles) to a standard rating of 796 MVA | 194126.5105 | 3.992% | 4862281.2 | 0.01574
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 581928.9759 | 7.009% | 8302968 | 0.03178
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 1651133.7623 | 19.89% | 8302968 | 0.11466
GEN-2023-160 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 760107.4556 | 9.155% | 8302968 | 0.08821
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 5.43% | 0 | 0.0727
GEN-2023-160 | 01 NORTH | 158921 | ERIS | Belfield - Rhame 230 kV Line GEN-2023-160 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-160 (300MW/Hybrid), into Belfield - Rhame 230 kV Line | 16601046 | 100% | 16601046 | 1
GEN-2023-160 | 01 NORTH | 158920 | ERIS | Belfield - Rhame 230 kV Line GEN-2023-160 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-160 (300MW/Hybrid), into Belfield - Rhame 230 kV Line | 3311556 | 100% | 3311556 | 1
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to G23-098-TAP 230 kV line 1 (19.76 miles) to a standard rating of 796 MVA | 7710339.6136 | 44.16% | 17458137.84 | 0.23919
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to HETINGR4 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to HETINGR4 230 kV line 1 (37.09 miles) to a standard rating of 796 MVA | 14472494.7504 | 44.16% | 32769348.81 | 0.23919
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 9911.8486 | 1.155% | 858333 | 0.06544
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 63542.4736 | 7.711% | 823999.68 | 0.05892
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 62659.9007 | 7.711% | 812555.24 | 0.05975
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 8683734.2721 | 7.556% | 114925066.48 | 0.11867
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the G22-066-PROX to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing G22-066-PROX to G23-098-TAP 230 kV line 1 (15.35 miles) to a standard rating of 796 MVA | 3262766.516 | 24.06% | 13561863.15 | 0.23919
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the MAURINE4 to NUNDRWD-LNX3 230kV line 1 | Current Study | Rebuild the existing MAURINE4 to NUNDRWD-LNX3 230 kV line 1 (71.98 miles) to a standard rating of 796 MVA | 17581970.793 | 27.65% | 63594977.82 | 0.09933
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 3341159.3733 | 5.834% | 57267977.76 | 0.07482
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1 | Current Study | Rebuild the existing SB.LS-WK-ER4 to WHITLOCK_-RM 230 kV line 1 (21.56 miles) to a standard rating of 796 MVA | 771160.6005 | 4.048% | 19048454.04 | 0.02547
GEN-2023-160 | 01 NORTH | TBD | ERIS | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Current Study | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line 1 (4.2 miles) to a standard rating of 796 MVA | 146332.6843 | 3.943% | 3710737.8 | 0.01574
GEN-2023-160 | 01 NORTH | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation (NTC 210648) | 0 | 4.075% | 561800 | 0.02571
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 5187550.9281 | 1.898% | 273358902 | 0.06099
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 14376040.3147 | 9.587% | 149959500 | 0.15591
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 6267401.0202 | 1.741% | 359902800 | 0.07344
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 14872520.6015 | 4.508% | 329910900 | 0.17545
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 2159316.2147 | 1.44% | 149959500 | 0.03006
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 2126260.1597 | 1.418% | 149959500 | 0.02907
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 6734722.443 | 1.727% | 389894700 | 0.0889
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 458999.9894 | 5.528% | 8302968 | 0.0752
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 4128.0744 | 0.04972% | 8302968 | 0.00086
GEN-2023-181 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 91742.5542 | 1.105% | 8302968 | 0.03194
GEN-2023-181 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 1.722% | 0 | 0.06916
GEN-2023-181 | 01 NORTH | 158955 | ERIS | Groton - Leland Olds 345 kV Line GEN-2023-181 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-181 (100MW/Battery/Storage), into Groton - Leland Olds 345 kV Line | 3685159 | 100% | 3685159 | 1
GEN-2023-181 | 01 NORTH | 158665 | ERIS | Groton - Leland Olds 345 kV Line Interconnection (DISIS-2023-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-181/182 (100/300MW/Battery/Storage/Wind), into Groton - Leland Olds 345 kV Line | 4975901 | 25% | 19903604 | 1
GEN-2023-181 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3010.613 | 0.3508% | 858333 | 0.05963
GEN-2023-181 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 1334430.7886 | 4.042% | 33016731.33 | 0.08865
GEN-2023-181 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 17603.9541 | 2.136% | 823999.68 | 0.04897
GEN-2023-181 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 17359.5016 | 2.136% | 812555.24 | 0.04966
GEN-2023-181 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 2406009.7992 | 2.094% | 114925066.48 | 0.09864
GEN-2023-181 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 1364537.4666 | 2.383% | 57267977.76 | 0.09167
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 15562652.7843 | 5.693% | 273358902 | 0.06099
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 43128120.9441 | 28.76% | 149959500 | 0.15591
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 18802203.0606 | 5.224% | 359902800 | 0.07344
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 44617561.8046 | 13.52% | 329910900 | 0.17545
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 6477948.644 | 4.32% | 149959500 | 0.03006
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 6378780.4792 | 4.254% | 149959500 | 0.02907
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 20204167.3289 | 5.182% | 389894700 | 0.0889
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 1376999.9682 | 16.58% | 8302968 | 0.0752
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 12384.2232 | 0.1492% | 8302968 | 0.00086
GEN-2023-182 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 275227.6627 | 3.315% | 8302968 | 0.03194
GEN-2023-182 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 5.166% | 0 | 0.06916
GEN-2023-182 | 01 NORTH | 158665 | ERIS | Groton - Leland Olds 345 kV Line Interconnection (DISIS-2023-001) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-181/182 (100/300MW/Battery/Storage/Wind), into Groton - Leland Olds 345 kV Line | 14927703 | 75% | 19903604 | 1
GEN-2023-182 | 01 NORTH | 158956 | ERIS | Groton - Leland Olds 345 kV Line GEN-2023-182 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-182 (300MW/Wind), into Groton - Leland Olds 345 kV Line | 120000 | 100% | 120000 | 1
GEN-2023-182 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 9031.8389 | 1.052% | 858333 | 0.05963
GEN-2023-182 | 01 NORTH | TBD | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | Current Study | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | 4003292.3658 | 12.13% | 33016731.33 | 0.08865
GEN-2023-182 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 52811.8624 | 6.409% | 823999.68 | 0.04897
GEN-2023-182 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 52078.5049 | 6.409% | 812555.24 | 0.04966
GEN-2023-182 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 7218029.3975 | 6.281% | 114925066.48 | 0.09864
GEN-2023-182 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 4093612.3998 | 7.148% | 57267977.76 | 0.09167
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | Current Study | Build 150Mvar Reactive Support at Maurine 345kV | 432140.7156 | 11.57% | 3733650 | 0.08344
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | Current Study | Build 200Mvar Reactive Support at Oahe 345kV | 495463.584 | 9.953% | 4978200 | 0.13749
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | Current Study | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | 30939033.4497 | 11.32% | 273358902 | 0.1455
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | Current Study | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 467952.0531 | 0.3121% | 149959500 | 0.00203
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | 16163477.0319 | 4.491% | 359902800 | 0.07576
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | Current Study | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | 15101393.8168 | 4.577% | 329910900 | 0.07126
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | Current Study | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | 14984476.4596 | 9.992% | 149959500 | 0.08344
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | Current Study | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | 15076552.3023 | 10.05% | 149959500 | 0.08245
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | Current Study | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | 25440811.7481 | 6.525% | 389894700 | 0.13433
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 | Current Study | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 (4.2 miles) to a standard rating of 796 MVA | 226008.1515 | 4.648% | 4862281.2 | 0.02199
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new Broadland 345/230 kV transformer 2 | Current Study | Build Broadland 345/230kV Transformer Ckt 2 | 502946.7969 | 6.057% | 8302968 | 0.03296
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new Maurine 345/230 kV transformer 1 | Current Study | Build Maurine 345/230kV Transformer Ckt 1 | 256684.6268 | 3.091% | 8302968 | 0.02139
GEN-2023-198 | 01 NORTH | TBD | ERIS | Build a new Oahe 345/230 kV transformer 1 | Current Study | Build Oahe 345/230kV Transformer Ckt 1 | 211045.2152 | 2.542% | 8302968 | 0.02939
GEN-2023-198 | 01 NORTH | 143614 | ERIS | Whitlock - Glenham 230 kV Clearance Increase | Contingent | Increase ground clearance of the Whitlock - Glenham 230 kV. (NTC 210648) | 0 | 15.26% | 5845900 | 0.06502
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | Current Study | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. at 0 cost. | 0 | 4.448% | 0 | 0.07147
GEN-2023-198 | 01 NORTH | 158980 | ERIS | Hebron 230 kV Substation GEN-2023-198 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-198 (250MW/Solar), into Hebron 230 kV Substation | 6989000 | 100% | 6989000 | 1
GEN-2023-198 | 01 NORTH | 158979 | ERIS | Hebron 230 kV Substation GEN-2023-198 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-198 (250MW/Solar), into Hebron 230 kV Substation | 416000 | 100% | 416000 | 1
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to G23-098-TAP 230 kV line 1 (19.76 miles) to a standard rating of 796 MVA | 2525359.9895 | 14.47% | 17458137.84 | 0.09401
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the BISON___-GE4 to HETINGR4 230kV line 1 | Current Study | Rebuild the existing BISON___-GE4 to HETINGR4 230 kV line 1 (37.09 miles) to a standard rating of 796 MVA | 4740162.0451 | 14.47% | 32769348.81 | 0.09401
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the CAMPBELL 4 to GLENHAM4 230kV line 1 | Current Study | Rebuild the existing CAMPBELL 4 to GLENHAM4 230 kV line 1 (14 miles) to a standard rating of 796 MVA | 1886498.5803 | 15.25% | 12369126 | 0.06535
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7818.1019 | 0.9108% | 858333 | 0.06194
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | 56798.5451 | 6.893% | 823999.68 | 0.0632
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | Current Study | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | 56009.3868 | 6.893% | 812555.24 | 0.06409
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | Current Study | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | 7761479.2994 | 6.754% | 114925066.48 | 0.12728
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the G22-066-PROX to G23-098-TAP 230kV line 1 | Current Study | Rebuild the existing G22-066-PROX to G23-098-TAP 230 kV line 1 (15.35 miles) to a standard rating of 796 MVA | 1068650.7246 | 7.88% | 13561863.15 | 0.09401
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the JAMESTN4 to G23-144-TAP 230kV line 1 | Current Study | Rebuild the existing JAMESTN4 to G23-144-TAP 230 kV line 1 (30.2 miles) to a standard rating of 796 MVA | 1485318.0856 | 5.567% | 26681971.8 | 0.04504
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the MAURINE4 to NUNDRWD-LNX3 230kV line 1 | Current Study | Rebuild the existing MAURINE4 to NUNDRWD-LNX3 230 kV line 1 (71.98 miles) to a standard rating of 796 MVA | 8745553.9474 | 13.75% | 63594977.82 | 0.05929
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | Current Study | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | 2941711.7578 | 5.137% | 57267977.76 | 0.07905
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1 | Current Study | Rebuild the existing SB.LS-WK-ER4 to WHITLOCK_-RM 230 kV line 1 (21.56 miles) to a standard rating of 796 MVA | 1640520.2933 | 8.612% | 19048454.04 | 0.06502
GEN-2023-198 | 01 NORTH | TBD | ERIS | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Current Study | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line 1 (4.2 miles) to a standard rating of 796 MVA | 170365.0851 | 4.591% | 3710737.8 | 0.02199
GEN-2023-198 | 01 NORTH | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation (NTC 210648) | 0 | 8.62% | 561800 | 0.06526
GEN-2023-011 | 02 NEBRASKA | TBD | NRIS | Build a new BPSSUB7 to SHELDON7 115kV line 2 | Current Study | Build a new BPSSUB7 to SHELDON7 138kV line CKT2 (16.8504 miles) to a standard rating of 398 MVA | 2372635.153 | 16.89% | 14049256.91 | 0.2189
GEN-2023-011 | 02 NEBRASKA | 158695 | ERIS | Harbine 115 kV Substation GEN-2023-011 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-011 (190MW/Wind), into Harbine 115 kV Substation | 1500000 | 100% | 1500000 | 1
GEN-2023-011 | 02 NEBRASKA | 158694 | ERIS | Harbine 115 kV Substation GEN-2023-011 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-011 (190MW/Wind), into Harbine 115 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-011 | 02 NEBRASKA | TBD | ERIS | Rebuild the BEATRCE7 to HARBINE7 115kV line 1 | Current Study | Rebuild the existing BEATRCE7 to HARBINE7 115 kV line 1 (14.08 miles) to a standard ratings of 239 MVA | 10008627.2 | 100% | 10008627.2 | 0.31444
GEN-2023-011 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5367.1509 | 0.6253% | 858333 | 0.05595
GEN-2023-011 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 1260113.3312 | 2.944% | 42802205.6 | 0.05525
GEN-2023-011 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 761180.0291 | 1.738% | 43786427.44 | 0.05525
GEN-2023-040 | 02 NEBRASKA | TBD | NRIS | Build a new BPSSUB7 to SHELDON7 115kV line 2 | Current Study | Build a new BPSSUB7 to SHELDON7 138kV line CKT2 (16.8504 miles) to a standard rating of 398 MVA | 459905.9253 | 3.274% | 14049256.91 | 0.07678
GEN-2023-040 | 02 NEBRASKA | 158748 | ERIS | Carleton Junction 115 kV Substation GEN-2023-040 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-040 (105MW/Solar), into Carleton Junction 115 kV Substation | 1500000 | 100% | 1500000 | 1
GEN-2023-040 | 02 NEBRASKA | 158747 | ERIS | Carleton Junction 115 kV Substation GEN-2023-040 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-040 (105MW/Solar), into Carleton Junction 115 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-040 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3483.4604 | 0.4058% | 858333 | 0.06571
GEN-2023-040 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 759777.2154 | 1.775% | 42802205.6 | 0.06028
GEN-2023-040 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 458948.595 | 1.048% | 43786427.44 | 0.06028
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | BUILD GENTLMN3 KEYSTONE3 345kV CKT2 | Current Study | Build a new line from GENTLMN3 to KEYSTONE3 345kV line 1 (29.84 miles) to a standard rating of 1792 MVA | 2936086.1679 | 6.561% | 44747914.8 | 0.15806
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | BUILD KEYSTON3 G21-037-TAP 345kV CKT 2 | Current Study | Build a new line from KEYSTON3 to G21-037-TAP 345kV line 2 (19.54 miles) to a standard rating of 1792 MVA | 1485717.9924 | 5.078% | 29257098.45 | 0.02239
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 147322.2779 | 1.774% | 8302968 | 0.00803
GEN-2023-071 | 02 NEBRASKA | 158797 | ERIS | Elsie Tap - Paxton 115 kV Line GEN-2023-071 Interconnection (Non-Shared NU) (Tri-State) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-071 (200MW/Hybrid), into Elsie Tap - Paxton 115 kV Line | 6500000 | 100% | 6500000 | 1
GEN-2023-071 | 02 NEBRASKA | 158796 | ERIS | Elsie Tap - Paxton 115 kV Line GEN-2023-071 Interconnection (TOIF) (Tri-State) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-071 (200MW/Hybrid), into Elsie Tap - Paxton 115 kV Line | 1500000 | 100% | 1500000 | 1
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the ELSIETP_-TS7 to G23-071-TAP 115kV line 1 | Current Study | Rebuild the existing ELSIETP_-TS7 to G23-071-TAP 115 kV line 1 (3.08 miles) to a standard ratings of 239 MVA | 2189387.2 | 100% | 2189387.2 | 0.58755
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 11412.3587 | 1.33% | 858333 | 0.11302
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the GENTLMN3 to KEYSTON3 345kV line 1 | Current Study | Rebuild the existing GENTLMN3 to KEYSTON3 345 kV line 1 (29.84 miles) to a standard ratings of 1792 MVA | 2240729.1291 | 6.561% | 34150208.96 | 0.15806
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the MALONEY7 to N.PLATT7 115kV line 1 | Current Study | Rebuild the existing MALONEY7 to N.PLATT7 115 kV line 1 (3.47 miles) to a standard ratings of 239 MVA | 2466614.8 | 100% | 2466614.8 | 0.41245
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the MALONEY7 to SUTHLND7 115kV line 1 | Current Study | Rebuild the existing MALONEY7 to SUTHLND7 115 kV line 1 (15.46 miles) to a standard ratings of 239 MVA | 10989586.4 | 100% | 10989586.4 | 0.41245
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 3745948.7129 | 8.752% | 42802205.6 | 0.15603
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the PAXTON__-TS7 to G23-071-TAP 115kV line 1 | Current Study | Rebuild the existing PAXTON__-TS7 to G23-071-TAP 115 kV line 1 (3.92 miles) to a standard ratings of 239 MVA | 2488812.8064 | 89.32% | 2786492.8 | 0.41245
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the PILE 3 to SCOTCTY3 115kV line 1 | Current Study | Rebuild the existing PILE 3 to SCOTCTY3 115 kV line 1 (11.88 miles) to a standard ratings of 398 MVA | 1297065.927 | 15.36% | 8444779.2 | 0.01695
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 2262765.8003 | 5.168% | 43786427.44 | 0.15603
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 43863.3391 | 2.228% | 1969026.8 | 0.01455
GEN-2023-071 | 02 NEBRASKA | TBD | ERIS | Rebuild the SUTHLND7 to PAXTON__-TS7 115kV line 1 | Current Study | Rebuild the existing SUTHLND7 to PAXTON__-TS7 115 kV line 1 (10.21 miles) to a standard ratings of 239 MVA | 6482341.5187 | 89.32% | 7257676.4 | 0.41245
GEN-2023-077 | 02 NEBRASKA | 143660 /143661 /143662 | ERIS | New Line - S3454 - S3740 345 kV | Contingent | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1 (NTC 210680) | 0 | 33.33% | 64071687 | 0.33071
GEN-2023-077 | 02 NEBRASKA | 158803 | ERIS | Substation 3740 345 kV GEN-2023-077 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077 (303MW/Thermal), into Substation 3740 345 kV | 2644098 | 100% | 2644098 | 1
GEN-2023-077 | 02 NEBRASKA | 158676 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (303MW/Thermal), into Substation 3740 345 kV | 6651879 | 33.33% | 19955637 | 1
GEN-2023-077 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3455 to S3740 345kV line 1 | Current Study | Rebuild the S3455 to S3740 345kV line CKT1 (20.15 miles) to a standard rating of 1792 MVA | 7686848.8667 | 33.33% | 23060546.6 | 0.37018
GEN-2023-078 | 02 NEBRASKA | 143660 /143661 /143662 | ERIS | New Line - S3454 - S3740 345 kV | Contingent | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1 (NTC 210680) | 0 | 33.33% | 64071687 | 0.33071
GEN-2023-078 | 02 NEBRASKA | 158676 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (303MW/Thermal), into Substation 3740 345 kV | 6651879 | 33.33% | 19955637 | 1
GEN-2023-078 | 02 NEBRASKA | 158804 | ERIS | Substation 3740 345 kV GEN-2023-078 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-078 (303MW/Thermal), into Substation 3740 345 kV | 2775000 | 100% | 2775000 | 1
GEN-2023-078 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3455 to S3740 345kV line 1 | Current Study | Rebuild the S3455 to S3740 345kV line CKT1 (20.15 miles) to a standard rating of 1792 MVA | 7686848.8667 | 33.33% | 23060546.6 | 0.37018
GEN-2023-079 | 02 NEBRASKA | 143660 /143661 /143662 | ERIS | New Line - S3454 - S3740 345 kV | Contingent | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1 (NTC 210680) | 0 | 33.33% | 64071687 | 0.33071
GEN-2023-079 | 02 NEBRASKA | 158676 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (303MW/Thermal), into Substation 3740 345 kV | 6651879 | 33.33% | 19955637 | 1
GEN-2023-079 | 02 NEBRASKA | 158805 | ERIS | Substation 3740 345 kV GEN-2023-079 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-079 (303MW/Thermal), into Substation 3740 345 kV | 2775000 | 100% | 2775000 | 1
GEN-2023-079 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3455 to S3740 345kV line 1 | Current Study | Rebuild the S3455 to S3740 345kV line CKT1 (20.15 miles) to a standard rating of 1792 MVA | 7686848.8667 | 33.33% | 23060546.6 | 0.37018
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | BUILD GENTLMN3 KEYSTONE3 345kV CKT2 | Current Study | Build a new line from GENTLMN3 to KEYSTONE3 345kV line 1 (29.84 miles) to a standard rating of 1792 MVA | 5800469.8645 | 12.96% | 44747914.8 | 0.31226
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | BUILD KEYSTON3 G21-037-TAP 345kV CKT 2 | Current Study | Build a new line from KEYSTON3 to G21-037-TAP 345kV line 2 (19.54 miles) to a standard rating of 1792 MVA | 20269864.9007 | 69.28% | 29257098.45 | 0.30547
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 140534.0783 | 1.693% | 8302968 | 0.00766
GEN-2023-083 | 02 NEBRASKA | 158813 | ERIS | Laramie River -Sidney 345 kV Line GEN-2023-083 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-083 (200MW/Hybrid), into Laramie River -Sidney 345 kV Line | 19903604 | 100% | 19903604 | 1
GEN-2023-083 | 02 NEBRASKA | 158812 | ERIS | Laramie River -Sidney 345 kV Line GEN-2023-083 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-083 (200MW/Hybrid), into Laramie River -Sidney 345 kV Line | 3685159 | 100% | 3685159 | 1
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 10914.5448 | 1.272% | 858333 | 0.10809
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | Rebuild the GENTLMN3 to KEYSTON3 345kV line 1 | Current Study | Rebuild the existing GENTLMN3 to KEYSTON3 345 kV line 1 (29.84 miles) to a standard ratings of 1792 MVA | 4426737.1748 | 12.96% | 34150208.96 | 0.31226
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 3544282.5641 | 8.281% | 42802205.6 | 0.14763
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | Rebuild the MORRILL7 to GERINGT_-TS7 115kV line 1 (non-SPP) | Contingent | Rebuild the existing MORRILL7 to GERINGT_-TS7 115 kV line 1 (24.19 miles) to a standard ratings of 239 MVA (non-SPP) (Facility Owner to address) | 0 | 76.38% | 17195219.6 | 0.03066
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1 | Current Study | Rebuild the existing OGALALA4 to SIDNEY___TS4 230 kV line 1 (68.85 miles) to a standard rating of 796 MVA | 40277405.047 | 66.21% | 60829594.65 | 0.20227
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | Rebuild the PILE 3 to SCOTCTY3 115kV line 1 | Current Study | Rebuild the existing PILE 3 to SCOTCTY3 115 kV line 1 (11.88 miles) to a standard ratings of 398 MVA | 1241204.0906 | 14.7% | 8444779.2 | 0.01622
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 2140947.9914 | 4.89% | 43786427.44 | 0.14763
GEN-2023-083 | 02 NEBRASKA | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 41692.7821 | 2.117% | 1969026.8 | 0.01383
GEN-2023-116 | 02 NEBRASKA | TBD | ERIS | BUILD GENTLMN3 KEYSTONE3 345kV CKT2 | Current Study | Build a new line from GENTLMN3 to KEYSTONE3 345kV line 1 (29.84 miles) to a standard rating of 1792 MVA | 19881646.3716 | 44.43% | 44747914.8 | 0.42812
GEN-2023-116 | 02 NEBRASKA | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 424262.4753 | 5.11% | 8302968 | 0.00925
GEN-2023-116 | 02 NEBRASKA | 158859 | ERIS | Keystone 345 kV Substation GEN-2023-116 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116 (500MW/Wind), into Keystone 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-116 | 02 NEBRASKA | 158667 | ERIS | Keystone 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116/117 (500/300MW/Wind), into Keystone 345 kV Substation | 6250000 | 62.5% | 10000000 | 1
GEN-2023-116 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 29121.6091 | 3.393% | 858333 | 0.11536
GEN-2023-116 | 02 NEBRASKA | TBD | ERIS | Rebuild the GENTLMN3 to KEYSTON3 345kV line 1 | Current Study | Rebuild the existing GENTLMN3 to KEYSTON3 345 kV line 1 (29.84 miles) to a standard ratings of 1792 MVA | 15173050.6571 | 44.43% | 34150208.96 | 0.42812
GEN-2023-116 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 9985475.3471 | 23.33% | 42802205.6 | 0.16637
GEN-2023-116 | 02 NEBRASKA | TBD | ERIS | Rebuild the PILE 3 to SCOTCTY3 115kV line 1 | Current Study | Rebuild the existing PILE 3 to SCOTCTY3 115 kV line 1 (11.88 miles) to a standard ratings of 398 MVA | 3183359.4433 | 37.7% | 8444779.2 | 0.01664
GEN-2023-116 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 6031794.3055 | 13.78% | 43786427.44 | 0.16637
GEN-2023-116 | 02 NEBRASKA | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 105965.3862 | 5.382% | 1969026.8 | 0.01406
GEN-2023-117 | 02 NEBRASKA | TBD | ERIS | BUILD GENTLMN3 KEYSTONE3 345kV CKT2 | Current Study | Build a new line from GENTLMN3 to KEYSTONE3 345kV line 1 (29.84 miles) to a standard rating of 1792 MVA | 11928987.823 | 26.66% | 44747914.8 | 0.42812
GEN-2023-117 | 02 NEBRASKA | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 254557.4852 | 3.066% | 8302968 | 0.00925
GEN-2023-117 | 02 NEBRASKA | 158667 | ERIS | Keystone 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116/117 (500/300MW/Wind), into Keystone 345 kV Substation | 3750000 | 37.5% | 10000000 | 1
GEN-2023-117 | 02 NEBRASKA | 158860 | ERIS | Keystone 345 kV Substation GEN-2023-117 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-117 (300MW/Wind), into Keystone 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-117 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 17472.9655 | 2.036% | 858333 | 0.11536
GEN-2023-117 | 02 NEBRASKA | TBD | ERIS | Rebuild the GENTLMN3 to KEYSTON3 345kV line 1 | Current Study | Rebuild the existing GENTLMN3 to KEYSTON3 345 kV line 1 (29.84 miles) to a standard ratings of 1792 MVA | 9103830.3943 | 26.66% | 34150208.96 | 0.42812
GEN-2023-117 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 5991285.2083 | 14% | 42802205.6 | 0.16637
GEN-2023-117 | 02 NEBRASKA | TBD | ERIS | Rebuild the PILE 3 to SCOTCTY3 115kV line 1 | Current Study | Rebuild the existing PILE 3 to SCOTCTY3 115 kV line 1 (11.88 miles) to a standard ratings of 398 MVA | 1910015.666 | 22.62% | 8444779.2 | 0.01664
GEN-2023-117 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 3619076.5833 | 8.265% | 43786427.44 | 0.16637
GEN-2023-117 | 02 NEBRASKA | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 63579.2317 | 3.229% | 1969026.8 | 0.01406
GEN-2023-133 | 02 NEBRASKA | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 161678.4027 | 1.947% | 8302968 | 0.00705
GEN-2023-133 | 02 NEBRASKA | 158877 | ERIS | Sweetwater 345 kV Substation GEN-2023-133 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-133 (250MW/Wind), into Sweetwater 345 kV Substation | 7000000 | 100% | 7000000 | 1
GEN-2023-133 | 02 NEBRASKA | 158876 | ERIS | Sweetwater 345 kV Substation GEN-2023-133 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-133 (250MW/Wind), into Sweetwater 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-133 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 12522.3424 | 1.459% | 858333 | 0.09921
GEN-2023-133 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 3146231.9991 | 7.351% | 42802205.6 | 0.10484
GEN-2023-133 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1900502.84 | 4.34% | 43786427.44 | 0.10484
GEN-2023-146 | 02 NEBRASKA | 158895 | ERIS | Seward 115 kV Substation GEN-2023-146 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-146 (125MW/Solar), into Seward 115 kV Substation | 3500000 | 100% | 3500000 | 1
GEN-2023-146 | 02 NEBRASKA | 158894 | ERIS | Seward 115 kV Substation GEN-2023-146 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-146 (125MW/Solar), into Seward 115 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-146 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3854.7761 | 0.4491% | 858333 | 0.06108
GEN-2023-146 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 888441.4187 | 2.076% | 42802205.6 | 0.05921
GEN-2023-146 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 536669.0822 | 1.226% | 43786427.44 | 0.05921
GEN-2023-147 | 02 NEBRASKA | TBD | ERIS | BUILD GENTLMN3 KEYSTONE3 345kV CKT2 | Current Study | Build a new line from GENTLMN3 to KEYSTONE3 345kV line 1 (29.84 miles) to a standard rating of 1792 MVA | 1871991.7731 | 4.183% | 44747914.8 | 0.23712
GEN-2023-147 | 02 NEBRASKA | TBD | ERIS | BUILD KEYSTON3 G21-037-TAP 345kV CKT 2 | Current Study | Build a new line from KEYSTON3 to G21-037-TAP 345kV line 2 (19.54 miles) to a standard rating of 1792 MVA | 6270871.2565 | 21.43% | 29257098.45 | 0.22236
GEN-2023-147 | 02 NEBRASKA | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 61442.3797 | 0.74% | 8302968 | 0.00788
GEN-2023-147 | 02 NEBRASKA | 158897 | ERIS | Victory Hill - Crawford 115 kV Line GEN-2023-147 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-147 (85MW/Wind), into Victory Hill - Crawford 115 kV Line | 16000000 | 100% | 16000000 | 1
GEN-2023-147 | 02 NEBRASKA | 158896 | ERIS | Victory Hill - Crawford 115 kV Line GEN-2023-147 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-147 (85MW/Wind), into Victory Hill - Crawford 115 kV Line | 500000 | 100% | 500000 | 1
GEN-2023-147 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 4156.7462 | 0.4843% | 858333 | 0.09686
GEN-2023-147 | 02 NEBRASKA | TBD | ERIS | Rebuild the GENTLMN3 to KEYSTON3 345kV line 1 | Current Study | Rebuild the existing GENTLMN3 to KEYSTON3 345 kV line 1 (29.84 miles) to a standard ratings of 1792 MVA | 1428645.5695 | 4.183% | 34150208.96 | 0.23712
GEN-2023-147 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 1381941.2921 | 3.229% | 42802205.6 | 0.13544
GEN-2023-147 | 02 NEBRASKA | TBD | ERIS | Rebuild the MORRILL7 to GERINGT_-TS7 115kV line 1 (non-SPP) | Contingent | Rebuild the existing MORRILL7 to GERINGT_-TS7 115 kV line 1 (24.19 miles) to a standard ratings of 239 MVA (non-SPP) (Facility Owner to address) | 0 | 23.62% | 17195219.6 | 0.02231
GEN-2023-147 | 02 NEBRASKA | TBD | ERIS | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1 | Current Study | Rebuild the existing OGALALA4 to SIDNEY___TS4 230 kV line 1 (68.85 miles) to a standard rating of 796 MVA | 12138329.8932 | 19.95% | 60829594.65 | 0.14343
GEN-2023-147 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 834771.0376 | 1.906% | 43786427.44 | 0.13544
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | BUILD GENTLMN3 KEYSTONE3 345kV CKT2 | Current Study | Build a new line from GENTLMN3 to KEYSTONE3 345kV line 1 (29.84 miles) to a standard rating of 1792 MVA | 2328732.7999 | 5.204% | 44747914.8 | 0.20894
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | BUILD KEYSTON3 G21-037-TAP 345kV CKT 2 | Current Study | Build a new line from KEYSTON3 to G21-037-TAP 345kV line 2 (19.54 miles) to a standard rating of 1792 MVA | 1230644.3004 | 4.206% | 29257098.45 | 0.03091
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 93346.9178 | 1.124% | 8302968 | 0.00848
GEN-2023-153 | 02 NEBRASKA | 158909 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (Non-Shared NU) (Tri-State) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | 5250000 | 100% | 5250000 | 1
GEN-2023-153 | 02 NEBRASKA | 158908 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (TOIF) (Tri-State) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | 1250000 | 100% | 1250000 | 1
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7093.9997 | 0.8265% | 858333 | 0.11709
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | Rebuild the GENTLMN3 to KEYSTON3 345kV line 1 | Current Study | Rebuild the existing GENTLMN3 to KEYSTON3 345 kV line 1 (29.84 miles) to a standard ratings of 1792 MVA | 1777216.0353 | 5.204% | 34150208.96 | 0.20894
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 2416392.6037 | 5.645% | 42802205.6 | 0.16775
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | Rebuild the PAXTON__-TS7 to G23-071-TAP 115kV line 1 | Current Study | Rebuild the existing PAXTON__-TS7 to G23-071-TAP 115 kV line 1 (3.92 miles) to a standard ratings of 239 MVA | 297679.9936 | 10.68% | 2786492.8 | 0.08222
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | Rebuild the PILE 3 to SCOTCTY3 115kV line 1 | Current Study | Rebuild the existing PILE 3 to SCOTCTY3 115 kV line 1 (11.88 miles) to a standard ratings of 398 MVA | 813134.0732 | 9.629% | 8444779.2 | 0.01771
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1459638.3888 | 3.334% | 43786427.44 | 0.16775
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 27855.4813 | 1.415% | 1969026.8 | 0.0154
GEN-2023-153 | 02 NEBRASKA | TBD | ERIS | Rebuild the SUTHLND7 to PAXTON__-TS7 115kV line 1 | Current Study | Rebuild the existing SUTHLND7 to PAXTON__-TS7 115 kV line 1 (10.21 miles) to a standard ratings of 239 MVA | 775334.8813 | 10.68% | 7257676.4 | 0.08222
GEN-2023-189 | 02 NEBRASKA | 158968 | ERIS | NW 68th - Holdrege 345 kV Substation GEN-2023-189 Interconnection (Non-Shared NU) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-189 (200MW/Battery/Storage), into NW 68th - Holdrege 345 kV Substation | 0 | 100% | 0 | 1
GEN-2023-189 | 02 NEBRASKA | 158967 | ERIS | NW 68th - Holdrege 345 kV Substation GEN-2023-189 Interconnection (TOIF) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-189 (200MW/Battery/Storage), into NW 68th - Holdrege 345 kV Substation | 2768522 | 100% | 2768522 | 1
GEN-2023-189 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5675.8864 | 0.6613% | 858333 | 0.05621
GEN-2023-189 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 1276018.5483 | 2.981% | 42802205.6 | 0.05315
GEN-2023-189 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 770787.6837 | 1.76% | 43786427.44 | 0.05315
GEN-2023-197 | 02 NEBRASKA | 158978 | ERIS | Sub 1366 - Sub 1258 161 kV GEN-2023-197 Interconnection (Non-Shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-197 (150MW/Solar), into Sub 1366 - Sub 1258 161 kV | 21200000 | 100% | 21200000 | 1
GEN-2023-197 | 02 NEBRASKA | 158977 | ERIS | Sub 1366 - Sub 1258 161 kV GEN-2023-197 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-197 (150MW/Solar), into Sub 1366 - Sub 1258 161 kV | 18111000 | 100% | 18111000 | 1
GEN-2023-197 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3470.8131 | 0.4044% | 858333 | 0.04583
GEN-2023-197 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 757868.5893 | 1.771% | 42802205.6 | 0.04209
GEN-2023-197 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 457795.6765 | 1.046% | 43786427.44 | 0.04209
GEN-2023-199 | 02 NEBRASKA | 158982 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | 2500000 | 100% | 2500000 | 1
GEN-2023-199 | 02 NEBRASKA | 158981 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-199 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 6940.8689 | 0.8086% | 858333 | 0.05499
GEN-2023-199 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 1701258.0316 | 3.975% | 42802205.6 | 0.05669
GEN-2023-199 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1027656.4861 | 2.347% | 43786427.44 | 0.05669
GEN-2023-199 | 02 NEBRASKA | TBD | ERIS | Rebuild the TEKAMAH5 to S1226 5 161kV line 1 | Current Study | Rebuild the existing TEKAMAH5 to S1226 5 161 kV line 1 (20.87 miles) to a standard ratings of 557 MVA | 3214653.4779 | 15.75% | 20415534.88 | 0.06338
GEN-2023-202 | 02 NEBRASKA | TBD | NRIS | Build a new FREMONT7 115/69 kV transformer 3 | Current Study | Build a new FREMONT7 115/69 kV transformer 3 to a standard rating of 33 MVA | 2777743 | 100% | 2777743 | 0.00332
GEN-2023-202 | 02 NEBRASKA | TBD | ERIS | BUILD TEKAMAH5 G17-105TAP 161kV CKT2 | Current Study | Build a new line from TEKAMAH5 to G17-105TAP 161kV line (3.71 miles) to a standard rating of 557 MVA | 3879706.53 | 100% | 3879706.53 | 0.35287
GEN-2023-202 | 02 NEBRASKA | 158988 | ERIS | Tekamah - Raun 161 kV Line GEN-2023-202 Interconnection (Non-Shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-202 (150MW/Solar), into Tekamah - Raun 161 kV Line | 5450000 | 100% | 5450000 | 1
GEN-2023-202 | 02 NEBRASKA | 158987 | ERIS | Tekamah - Raun 161 kV Line GEN-2023-202 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-202 (150MW/Solar), into Tekamah - Raun 161 kV Line | 3089434 | 100% | 3089434 | 1
GEN-2023-202 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3847.9602 | 0.4483% | 858333 | 0.05081
GEN-2023-202 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 900475.3659 | 2.104% | 42802205.6 | 0.05001
GEN-2023-202 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 543938.2699 | 1.242% | 43786427.44 | 0.05001
GEN-2023-202 | 02 NEBRASKA | TBD | ERIS | Rebuild the TEKAMAH5 to G17-105TAP 161kV line 1 | Current Study | Rebuild the existing TEKAMAH5 to G17-105TAP 161 kV line 1 (3.71 miles) to a standard ratings of 557 MVA | 3629211.04 | 100% | 3629211.04 | 0.35287
GEN-2023-202 | 02 NEBRASKA | TBD | ERIS | Rebuild the TEKAMAH5 to S1226 5 161kV line 1 | Current Study | Rebuild the existing TEKAMAH5 to S1226 5 161 kV line 1 (20.87 miles) to a standard ratings of 557 MVA | 17200881.4021 | 84.25% | 20415534.88 | 0.56522
GEN-2023-216 | 02 NEBRASKA | TBD | NRIS | Build a new HOSKINST1 230/115 kV transformer 2 | Current Study | Build a new HOSKINST1 230/115 kV transformer 2 to a standard rating of 229 MVA | 2207062.6667 | 33.33% | 6621188 | 0.01782
GEN-2023-216 | 02 NEBRASKA | TBD | ERIS | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 1 | Current Study | Build a new line from TURTLE.CRK 3 to G19-069TAP 345kV line 1 (20.2 miles) to a standard rating of 1792 MVA | 10097273 | 33.33% | 30291819 | 0.17023
GEN-2023-216 | 02 NEBRASKA | TBD | ERIS | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 2 | Current Study | Build a new line from TURTLE.CRK 3 to G19-069TAP 345kV line 2 (20.2 miles) to a standard rating of 1792 MVA | 10097273 | 33.33% | 30291819 | 0.17023
GEN-2023-216 | 02 NEBRASKA | 159013 | ERIS | Turtle Creek 345 kV Substation GEN-2023-216 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216 (200MW/Wind), into Turtle Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-216 | 02 NEBRASKA | 158678 | ERIS | Turtle Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216/217/218 (200MW/Wind), into Turtle Creek 345 kV Substation | 2333333.3333 | 33.33% | 7000000 | 1
GEN-2023-216 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 6123.2121 | 0.7134% | 858333 | 0.06064
GEN-2023-216 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 1682231.7908 | 3.93% | 42802205.6 | 0.07007
GEN-2023-216 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1016163.5559 | 2.321% | 43786427.44 | 0.07007
GEN-2023-217 | 02 NEBRASKA | TBD | NRIS | Build a new HOSKINST1 230/115 kV transformer 2 | Current Study | Build a new HOSKINST1 230/115 kV transformer 2 to a standard rating of 229 MVA | 2207062.6667 | 33.33% | 6621188 | 0.01782
GEN-2023-217 | 02 NEBRASKA | TBD | ERIS | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 1 | Current Study | Build a new line from TURTLE.CRK 3 to G19-069TAP 345kV line 1 (20.2 miles) to a standard rating of 1792 MVA | 10097273 | 33.33% | 30291819 | 0.17023
GEN-2023-217 | 02 NEBRASKA | TBD | ERIS | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 2 | Current Study | Build a new line from TURTLE.CRK 3 to G19-069TAP 345kV line 2 (20.2 miles) to a standard rating of 1792 MVA | 10097273 | 33.33% | 30291819 | 0.17023
GEN-2023-217 | 02 NEBRASKA | 158678 | ERIS | Turtle Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216/217/218 (200MW/Wind), into Turtle Creek 345 kV Substation | 2333333.3333 | 33.33% | 7000000 | 1
GEN-2023-217 | 02 NEBRASKA | 159014 | ERIS | Turtle Creek 345 kV Substation GEN-2023-217 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-217 (200MW/Wind), into Turtle Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-217 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 6123.2121 | 0.7134% | 858333 | 0.06064
GEN-2023-217 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 1682231.7908 | 3.93% | 42802205.6 | 0.07007
GEN-2023-217 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1016163.5559 | 2.321% | 43786427.44 | 0.07007
GEN-2023-218 | 02 NEBRASKA | TBD | NRIS | Build a new HOSKINST1 230/115 kV transformer 2 | Current Study | Build a new HOSKINST1 230/115 kV transformer 2 to a standard rating of 229 MVA | 2207062.6667 | 33.33% | 6621188 | 0.01782
GEN-2023-218 | 02 NEBRASKA | TBD | ERIS | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 1 | Current Study | Build a new line from TURTLE.CRK 3 to G19-069TAP 345kV line 1 (20.2 miles) to a standard rating of 1792 MVA | 10097273 | 33.33% | 30291819 | 0.17023
GEN-2023-218 | 02 NEBRASKA | TBD | ERIS | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 2 | Current Study | Build a new line from TURTLE.CRK 3 to G19-069TAP 345kV line 2 (20.2 miles) to a standard rating of 1792 MVA | 10097273 | 33.33% | 30291819 | 0.17023
GEN-2023-218 | 02 NEBRASKA | 158678 | ERIS | Turtle Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216/217/218 (200MW/Wind), into Turtle Creek 345 kV Substation | 2333333.3333 | 33.33% | 7000000 | 1
GEN-2023-218 | 02 NEBRASKA | 159015 | ERIS | Turtle Creek 345 kV Substation GEN-2023-218 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-218 (200MW/Wind), into Turtle Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-218 | 02 NEBRASKA | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 6123.2121 | 0.7134% | 858333 | 0.06064
GEN-2023-218 | 02 NEBRASKA | TBD | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | 1682231.7908 | 3.93% | 42802205.6 | 0.07007
GEN-2023-218 | 02 NEBRASKA | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1016163.5559 | 2.321% | 43786427.44 | 0.07007
GEN-2023-222 | 02 NEBRASKA | TBD | ERIS | Build a new BPSSUB7 to HARBINE7 115kV line 1 | Current Study | Build a new BPSSUB7 to HARBINE7 115kV line CKT1 (14.58 miles) to a standard rating of 239 MVA | 8736015.24 | 66.67% | 13104022.86 | 0.08686
GEN-2023-222 | 02 NEBRASKA | TBD | NRIS | Build a new BPSSUB7 to SHELDON7 115kV line 2 | Current Study | Build a new BPSSUB7 to SHELDON7 138kV line CKT2 (16.8504 miles) to a standard rating of 398 MVA | 7477810.5544 | 53.23% | 14049256.91 | 0.27423
GEN-2023-222 | 02 NEBRASKA | 159022 | ERIS | New Beatrice Power Station 345 kV GEN-2023-222 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222 (478MW/Thermal), into New Beatrice Power Station 345 kV | 1000000 | 100% | 1000000 | 1
GEN-2023-222 | 02 NEBRASKA | 158670 | ERIS | New Beatrice Power Station 345 kV Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222/223 (478/239MW/Thermal), into New Beatrice Power Station 345 kV | 50666666.6667 | 66.67% | 76000000 | 1
GEN-2023-222 | 02 NEBRASKA | TBD | ERIS | Rebuild the BPSSUB7 to BEATRCE7 115kV line 1 | Current Study | Rebuild the BPSSUB7 to BEATRCE7 115kV line CKT1 (4.18 miles) to a standard rating of 398 MVA | 1980874.1333 | 66.67% | 2971311.2 | 0.10552
GEN-2023-222 | 02 NEBRASKA | TBD | ERIS | Rebuild the BPSSUB7 to BEATRCE7 115kV line 2 | Current Study | Rebuild the BPSSUB7 to BEATRCE7 115kV line CKT2 (4.18 miles) to a standard rating of 398 MVA | 1980874.1333 | 66.67% | 2971311.2 | 0.10552
GEN-2023-222 | 02 NEBRASKA | TBD | ERIS | Rebuild the BPSSUB7 to CLATONA7 115kV line 1 | Current Study | Rebuild the BPSSUB7 to CLATONA7 115kV line CKT1 (8.96 miles) to a standard rating of 398 MVA | 4246084.2667 | 66.67% | 6369126.4 | 0.30953
GEN-2023-222 | 02 NEBRASKA | TBD | ERIS | Rebuild the BPSSUB7 to SHELDON7 115kV line 1 | Current Study | Rebuild the BPSSUB7 to SHELDON7 115kV line CKT1 (16.85 miles) to a standard rating of 398 MVA | 7985102.6667 | 66.67% | 11977654 | 0.39256
GEN-2023-222 | 02 NEBRASKA | TBD | ERIS | Rebuild the CLATONA7 to SHELDON 7 115kV line 1 | Current Study | Rebuild the CLATONA7 to SHELDON 7 115kV line CKT1 (12.41 miles) to a standard rating of 398 MVA | 5881016.2667 | 66.67% | 8821524.4 | 0.30953
GEN-2023-223 | 02 NEBRASKA | TBD | ERIS | Build a new BPSSUB7 to HARBINE7 115kV line 1 | Current Study | Build a new BPSSUB7 to HARBINE7 115kV line CKT1 (14.58 miles) to a standard rating of 239 MVA | 4368007.62 | 33.33% | 13104022.86 | 0.08686
GEN-2023-223 | 02 NEBRASKA | TBD | NRIS | Build a new BPSSUB7 to SHELDON7 115kV line 2 | Current Study | Build a new BPSSUB7 to SHELDON7 138kV line CKT2 (16.8504 miles) to a standard rating of 398 MVA | 3738905.2772 | 26.61% | 14049256.91 | 0.27423
GEN-2023-223 | 02 NEBRASKA | 158670 | ERIS | New Beatrice Power Station 345 kV Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222/223 (478/239MW/Thermal), into New Beatrice Power Station 345 kV | 25333333.3333 | 33.33% | 76000000 | 1
GEN-2023-223 | 02 NEBRASKA | 159023 | ERIS | New Beatrice Power Station 345 kV GEN-2023-223 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-223 (239MW/Thermal), into New Beatrice Power Station 345 kV | 1000000 | 100% | 1000000 | 1
GEN-2023-223 | 02 NEBRASKA | TBD | ERIS | Rebuild the BPSSUB7 to BEATRCE7 115kV line 1 | Current Study | Rebuild the BPSSUB7 to BEATRCE7 115kV line CKT1 (4.18 miles) to a standard rating of 398 MVA | 990437.0667 | 33.33% | 2971311.2 | 0.10552
GEN-2023-223 | 02 NEBRASKA | TBD | ERIS | Rebuild the BPSSUB7 to BEATRCE7 115kV line 2 | Current Study | Rebuild the BPSSUB7 to BEATRCE7 115kV line CKT2 (4.18 miles) to a standard rating of 398 MVA | 990437.0667 | 33.33% | 2971311.2 | 0.10552
GEN-2023-223 | 02 NEBRASKA | TBD | ERIS | Rebuild the BPSSUB7 to CLATONA7 115kV line 1 | Current Study | Rebuild the BPSSUB7 to CLATONA7 115kV line CKT1 (8.96 miles) to a standard rating of 398 MVA | 2123042.1333 | 33.33% | 6369126.4 | 0.30953
GEN-2023-223 | 02 NEBRASKA | TBD | ERIS | Rebuild the BPSSUB7 to SHELDON7 115kV line 1 | Current Study | Rebuild the BPSSUB7 to SHELDON7 115kV line CKT1 (16.85 miles) to a standard rating of 398 MVA | 3992551.3333 | 33.33% | 11977654 | 0.39256
GEN-2023-223 | 02 NEBRASKA | TBD | ERIS | Rebuild the CLATONA7 to SHELDON 7 115kV line 1 | Current Study | Rebuild the CLATONA7 to SHELDON 7 115kV line CKT1 (12.41 miles) to a standard rating of 398 MVA | 2940508.1333 | 33.33% | 8821524.4 | 0.30953
GEN-2023-224 | 02 NEBRASKA | 159024 | ERIS | Olive Creek 345 kV Substation GEN-2023-224 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224 (478MW/Thermal), into Olive Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-224 | 02 NEBRASKA | 158671 | ERIS | Olive Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224/225 (478/217MW/Thermal), into Olive Creek 345 kV Substation | 3438848.9209 | 68.78% | 5000000 | 1
GEN-2023-225 | 02 NEBRASKA | 158671 | ERIS | Olive Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224/225 (478/217MW/Thermal), into Olive Creek 345 kV Substation | 1561151.0791 | 31.22% | 5000000 | 1
GEN-2023-225 | 02 NEBRASKA | 159025 | ERIS | Olive Creek 345 kV Substation GEN-2023-225 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-225 (217MW/Thermal), into Olive Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 28132.2208 | 3.131% | 898410 | 0.00935
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 239930.2071 | 3.213% | 7467300 | 0.08102
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to G20-007-TAP 345kV line 2 | Current Study | Build a new LACYGNE7 to G20-007-TAP 345 kV line 2 (0.59 miles) to a standard rating of 1792 MVA | 74614.9042 | 8.433% | 884761.05 | 0.04774
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 2247434.5699 | 3.469% | 64782504 | 0.04557
GEN-2023-006 | 03 CENTRAL | 158686 | ERIS | Wolf Creek- Blackberry 345 kV Line Break GEN-2023-006 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-006 (202MW/Wind), into Wolf Creek- Blackberry 345 kV Line Break | 4001600 | 100% | 4001600 | 1
GEN-2023-006 | 03 CENTRAL | 158687 | ERIS | Wolf Creek- Blackberry 345 kV Line Break GEN-2023-006 Interconnection (Non-Shared NU) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-006 (202MW/Wind), into Wolf Creek- Blackberry 345 kV Line Break | 20081200 | 100% | 20081200 | 1
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 5424848.6943 | 15.07% | 36004208.24 | 0.28251
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 364194.604 | 9.852% | 3696554.12 | 0.17465
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 513853.9314 | 2.901% | 17715993.12 | 0.10346
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 615448.0894 | 3.522% | 17475659.88 | 0.07854
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Rebuild the G20-076-TAP to G21-096-TAP 345kV line 1 | Current Study | Rebuild the existing G20-076-TAP to G21-096-TAP 345 kV line 1 (61.1 miles) to a standard rating of 1792 MVA | 12539212.8093 | 17.93% | 69925528.4 | 0.13077
GEN-2023-006 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 313614.7169 | 1.791% | 17509993.2 | 0.06543
GEN-2023-015 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 6676.277 | 0.08941% | 7467300 | 0.00138
GEN-2023-015 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 2.528% | 87298154 | 0.01742
GEN-2023-015 | 03 CENTRAL | 158701 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | 16806895 | 100% | 16806895 | 1
GEN-2023-015 | 03 CENTRAL | 158700 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | 1900000 | 100% | 1900000 | 1
GEN-2023-015 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 2424349.742 | 3.656% | 66320529.8 | 0.13874
GEN-2023-015 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1374213.6503 | 3.138% | 43786427.44 | 0.05743
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 32240.2668 | 3.589% | 898410 | 0.01443
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 116746.8859 | 1.563% | 7467300 | 0.05309
GEN-2023-017 | 03 CENTRAL | TBD | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | Current Study | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | 280718.2269 | 7.784% | 3606166 | 0.01465
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Build a new CARTHAG5 to CAR395 5 161kV line 2 | Current Study | Build a new CARTHAG5 to CAR395 5 161 kV line 2 (4.14 miles) to a standard rating of 557 MVA | 3085414.3693 | 71.27% | 4329376.02 | 0.41828
GEN-2023-017 | 03 CENTRAL | 158705 | ERIS | Carl Junction Northeast 161 kV Substation GEN-2023-017 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-017 (150MW/Battery/Storage), into Carl Junction Northeast 161 kV Substation | 21509480.76 | 100% | 21509480.76 | 1
GEN-2023-017 | 03 CENTRAL | 158704 | ERIS | Carl Junction Northeast 161 kV Substation GEN-2023-017 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-017 (150MW/Battery/Storage), into Carl Junction Northeast 161 kV Substation | 1871112 | 100% | 1871112 | 1
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the AUR124 5 to G19-035-TAP 161kV line 1 | Current Study | Rebuild the existing AUR124 5 to G19-035-TAP 161 kV line 1 (8.3 miles) to a standard rating of 557 MVA | 2306924.9274 | 28.41% | 8119259.2 | 0.05124
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the AUR124 5 to MON383 5 161kV line 1 | Current Study | Rebuild the existing AUR124 5 to MON383 5 161 kV line 1 (11.51 miles) to a standard rating of 557 MVA | 1935688.2534 | 17.19% | 11259358.24 | 0.09903
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 257985.2153 | 1.456% | 17715993.12 | 0.06995
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the CARTHAG5 to CAR395 5 161kV line 1 | Current Study | Rebuild the existing CARTHAG5 to CAR395 5 161 kV line 1 (4.14 miles) to a standard rating of 557 MVA | 2886202.8108 | 71.27% | 4049847.36 | 0.41828
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 308925.0643 | 1.768% | 17475659.88 | 0.05309
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the FLINTCR5 to DEC392 5 161kV line 1 | Current Study | Rebuild the existing FLINTCR5 to DEC392 5 161 kV line 1 (6.03 miles) to a standard rating of 557 MVA | 468278.4438 | 7.939% | 5898690.72 | 0.09848
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the LAR382 5 to MON383 5 161kV line 1 | Current Study | Rebuild the existing LAR382 5 to MON383 5 161 kV line 1 (15.56 miles) to a standard rating of 557 MVA | 3142474.538 | 20.65% | 15221165.44 | 0.10543
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the NEO SPA5 to CARTHAG5 161kV line 1 | Current Study | Rebuild the existing NEO SPA5 to CARTHAG5 161 kV line 1 (22.9 miles) to a standard rating of 557 MVA | 7585214.6934 | 33.86% | 22401329.6 | 0.20509
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the RDS295 5 to G19-035-TAP 161kV line 1 | Current Study | Rebuild the existing RDS295 5 to G19-035-TAP 161 kV line 1 (15.41 miles) to a standard rating of 557 MVA | 4283097.9676 | 28.41% | 15074431.84 | 0.05124
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYRD5 to NOL435 5 161kV line 1 | Current Study | Rebuild the existing SIBLEYRD5 to NOL435 5 161 kV line 1 (3.93 miles) to a standard rating of 557 MVA | 296625.6552 | 7.716% | 3844420.32 | 0.09
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 1 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 1 (43.1 miles) to a standard rating of 557 MVA | 7470891.8824 | 17.72% | 42161454.4 | 0.10566
GEN-2023-017 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 2 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 2 (43.1 miles) to a standard rating of 557 MVA | 7043150.0698 | 16.71% | 42161454.4 | 0.10566
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 17486.7513 | 1.946% | 898410 | 0.00587
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 148273.7495 | 1.986% | 7467300 | 0.05057
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 1548949.2528 | 18.66% | 8302968 | 0.13721
GEN-2023-021 | 03 CENTRAL | 158711 | ERIS | Blue Mills 161kV Substation GEN-2023-021 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-021 (200MW/Battery/Storage), into Blue Mills 161kV Substation | 12224014 | 100% | 12224014 | 1
GEN-2023-021 | 03 CENTRAL | 158710 | ERIS | Blue Mills 161kV Substation GEN-2023-021 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-021 (200MW/Battery/Storage), into Blue Mills 161kV Substation | 848027 | 100% | 848027 | 1
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MOCITYB1 to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing 5MOCITYB1 to ECKLES-161 161 kV line 1 (6.07 miles) to a standard rating of 557 MVA | 1824902.2045 | 30.73% | 5937819.68 | 0.15765
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 95861.06 | 2.593% | 3696554.12 | 0.04643
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Rebuild the BLUMILS5 to BLUVLY-161 161kV line 1 | Current Study | Rebuild the existing BLUMILS5 to BLUVLY-161 161 kV line 1 (4.7 miles) to a standard rating of 557 MVA | 2861025.9012 | 62.23% | 4597652.8 | 0.36343
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Rebuild the BLUMILS5 to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing BLUMILS5 to ECKLES-161 161 kV line 1 (6.5 miles) to a standard rating of 557 MVA | 6358456 | 100% | 6358456 | 0.63657
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 384667.6635 | 2.201% | 17475659.88 | 0.04958
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161kV line 1 | Current Study | Rebuild the existing LBRTYST5 to BRMGHAM5 161 kV line 1 (4.03 miles) to a standard rating of 557 MVA | 286447.9051 | 7.266% | 3942242.72 | 0.08362
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 438120.8648 | 2.502% | 17509993.2 | 0.09232
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 211136.2763 | 18.14% | 1164086.56 | 0.27441
GEN-2023-021 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYPL to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing SIBLEYPL to ECKLES-161 161 kV line 1 (3.09 miles) to a standard rating of 557 MVA | 804935.7989 | 26.63% | 3022712.16 | 0.43355
GEN-2023-021 | 03 CENTRAL | TBD | NRIS | Rebuild the LEVEE5 to NEASTN 161kV line 1 | Current Study | Rebuild the LEVEE5 to NEASTN 161kV line CKT1 (5.19 miles) to a standard rating of 557 MVA | 1889196.0379 | 37.21% | 5076982.56 | 0.05094
GEN-2023-023 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 17546.3314 | 1.953% | 898410 | 0.00589
GEN-2023-023 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 152261.3369 | 2.039% | 7467300 | 0.05193
GEN-2023-023 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 254225.9105 | 3.062% | 8302968 | 0.02252
GEN-2023-023 | 03 CENTRAL | 158715 | ERIS | Center City 161 kV Substation GEN-2023-023 Interconnection (Non-Shared NU) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-023 (200MW/Battery/Storage), into Center City 161 kV Substation | 4998381 | 100% | 4998381 | 1
GEN-2023-023 | 03 CENTRAL | 158714 | ERIS | Center City 161 kV Substation GEN-2023-023 Interconnection (TOIF) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-023 (200MW/Battery/Storage), into Center City 161 kV Substation | 0 | 100% | 0 | 1
GEN-2023-023 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 97161.7808 | 2.628% | 3696554.12 | 0.04706
GEN-2023-023 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 395917.5245 | 2.266% | 17475659.88 | 0.05103
GEN-2023-023 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 469110.1331 | 2.679% | 17509993.2 | 0.09885
GEN-2023-023 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 34662.3273 | 2.978% | 1164086.56 | 0.04505
GEN-2023-024 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 79751.7498 | 1.068% | 7467300 | 0.0272
GEN-2023-024 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 4.076% | 87298154 | 0.04634
GEN-2023-024 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 1931714.4896 | 2.982% | 64782504 | 0.03956
GEN-2023-024 | 03 CENTRAL | 158717 | ERIS | Rose Hill 138 kV Substation GEN-2023-024 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-024 (200MW/Battery/Storage), into Rose Hill 138 kV Substation | 792459 | 100% | 792459 | 1
GEN-2023-024 | 03 CENTRAL | 158716 | ERIS | Rose Hill 138 kV Substation GEN-2023-024 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-024 (200MW/Battery/Storage), into Rose Hill 138 kV Substation | 737196 | 100% | 737196 | 1
GEN-2023-024 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 571506.8064 | 1.587% | 36004208.24 | 0.03006
GEN-2023-024 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 57293.6553 | 1.55% | 3696554.12 | 0.02775
GEN-2023-024 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 1501760.3983 | 8.477% | 17715993.12 | 0.30539
GEN-2023-024 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 211031.8767 | 1.208% | 17475659.88 | 0.0272
GEN-2023-024 | 03 CENTRAL | TBD | ERIS | Rebuild the ELPASO 4 to ROSEHIL4 138kV line 1 | Current Study | Rebuild the existing ELPASO 4 to ROSEHIL4 138 kV line 1 (8.37 miles) to a standard rating of 478 MVA | 2216812.0673 | 27.47% | 8070010.83 | 0.13112
GEN-2023-024 | 03 CENTRAL | TBD | ERIS | Rebuild the ROSEHIL4 to STEARMN4 138kV line 1 | Current Study | Rebuild the existing ROSEHIL4 to STEARMN4 138 kV line 1 (11.64 miles) to a standard rating of 478 MVA | 4739410.8193 | 42.23% | 11222810.76 | 0.08809
GEN-2023-024 | 03 CENTRAL | TBD | ERIS | Rebuild the WEAVER 4 to ROSEHIL4 138kV line 1 | Current Study | Rebuild the existing WEAVER 4 to ROSEHIL4 138 kV line 1 (7.51 miles) to a standard rating of 478 MVA | 3212798.5407 | 44.37% | 7240834.09 | 0.13612
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Build a new 10 MVAR cap bank at HUDSON-2 | Current Study | Build a new 10 MVAR cap bank at HUDSON-2 69 kV | 340100 | 100% | 340100 | 0.04381
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 60801.4641 | 6.768% | 898410 | 0.02041
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 233185.9065 | 3.123% | 7467300 | 0.07953
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Build a new CARTHAG5 to CAR395 5 161kV line 2 | Current Study | Build a new CARTHAG5 to CAR395 5 161 kV line 2 (4.14 miles) to a standard rating of 557 MVA | 1243961.6507 | 28.73% | 4329376.02 | 0.12648
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Build a new G23-025-TAP to LITCH 5 161kV line 1 | Current Study | Build a new G23-025-TAP to LITCH 5 161 kV line 1 (24 miles) to a standard rating of 557 MVA | 25097832 | 100% | 25097832 | 0.31172
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 1201706.1069 | 1.855% | 64782504 | 0.02461
GEN-2023-025 | 03 CENTRAL | 158719 | ERIS | Franklin - Jayhawk 161 kV Line GEN-2023-025 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-025 (200MW/Battery/Storage), into Franklin - Jayhawk 161 kV Line | 12481952 | 100% | 12481952 | 1
GEN-2023-025 | 03 CENTRAL | 158718 | ERIS | Franklin - Jayhawk 161 kV Line GEN-2023-025 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-025 (200MW/Battery/Storage), into Franklin - Jayhawk 161 kV Line | 751752 | 100% | 751752 | 1
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 1239215.3573 | 3.442% | 36004208.24 | 0.06518
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 70115.0462 | 1.897% | 3696554.12 | 0.03396
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the AUR124 5 to MON383 5 161kV line 1 | Current Study | Rebuild the existing AUR124 5 to MON383 5 161 kV line 1 (11.51 miles) to a standard rating of 557 MVA | 1572319.1266 | 13.96% | 11259358.24 | 0.06033
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 359322.9389 | 2.028% | 17715993.12 | 0.07307
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the CARTHAG5 to CAR395 5 161kV line 1 | Current Study | Rebuild the existing CARTHAG5 to CAR395 5 161 kV line 1 (4.14 miles) to a standard rating of 557 MVA | 1163644.5492 | 28.73% | 4049847.36 | 0.12648
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 617035.4836 | 3.531% | 17475659.88 | 0.07953
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the FLINTCR5 to DEC392 5 161kV line 1 | Current Study | Rebuild the existing FLINTCR5 to DEC392 5 161 kV line 1 (6.03 miles) to a standard rating of 557 MVA | 419713.417 | 7.115% | 5898690.72 | 0.0662
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the FRANKLIN5 to G23-025-TAP 161kV line 1 | Current Study | Rebuild the existing FRANKLIN5 to G23-025-TAP 161 kV line 1 (14.57 miles) to a standard rating of 557 MVA | 14252723.68 | 100% | 14252723.68 | 0.33019
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the LITCH 5 to ASB349 5 161kV line 1 | Current Study | Rebuild the existing LITCH 5 to ASB349 5 161 kV line 1 (6.8 miles) to a standard rating of 557 MVA | 6651923.2 | 100% | 6651923.2 | 0.53255
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the LITCH 5 to FRANKLIN5 161kV line 1 | Current Study | Rebuild the existing LITCH 5 to FRANKLIN5 161 kV line 1 (6.22 miles) to a standard rating of 557 MVA | 6084553.28 | 100% | 6084553.28 | 0.26843
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the NEO SPA5 to CARTHAG5 161kV line 1 | Current Study | Rebuild the existing NEO SPA5 to CARTHAG5 161 kV line 1 (22.9 miles) to a standard rating of 557 MVA | 3830146.9289 | 17.1% | 22401329.6 | 0.07767
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYRD5 to NOL435 5 161kV line 1 | Current Study | Rebuild the existing SIBLEYRD5 to NOL435 5 161 kV line 1 (3.93 miles) to a standard rating of 557 MVA | 264985.5853 | 6.893% | 3844420.32 | 0.0603
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 1 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 1 (43.1 miles) to a standard rating of 557 MVA | 5467058.1142 | 12.97% | 42161454.4 | 0.05799
GEN-2023-025 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 2 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 2 (43.1 miles) to a standard rating of 557 MVA | 5154044.7037 | 12.22% | 42161454.4 | 0.05799
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 24934.2604 | 2.775% | 898410 | 0.00558
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 260981.737 | 3.495% | 7467300 | 0.05934
GEN-2023-026 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 24.88% | 87298154 | 0.1886
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to G20-007-TAP 345kV line 2 | Current Study | Build a new LACYGNE7 to G20-007-TAP 345 kV line 2 (0.59 miles) to a standard rating of 1792 MVA | 477982.0479 | 54.02% | 884761.05 | 0.20592
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 7821832.2933 | 12.07% | 64782504 | 0.10679
GEN-2023-026 | 03 CENTRAL | 158721 | ERIS | LaCygne - Wolf Creek 345 kV Line GEN-2023-026 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-026 (300MW/Battery/Storage), into LaCygne - Wolf Creek 345 kV Line | 40560386 | 100% | 40560386 | 1
GEN-2023-026 | 03 CENTRAL | 158720 | ERIS | LaCygne - Wolf Creek 345 kV Line GEN-2023-026 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-026 (300MW/Battery/Storage), into LaCygne - Wolf Creek 345 kV Line | 1680753 | 100% | 1680753 | 1
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 916863.4643 | 2.547% | 36004208.24 | 0.03215
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 237412.5196 | 6.423% | 3696554.12 | 0.07666
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 468319.6946 | 2.643% | 17715993.12 | 0.06349
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 675573.5538 | 3.866% | 17475659.88 | 0.05805
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Rebuild the G20-076-TAP to G21-096-TAP 345kV line 1 | Current Study | Rebuild the existing G20-076-TAP to G21-096-TAP 345 kV line 1 (61.1 miles) to a standard rating of 1792 MVA | 29861371.7605 | 42.7% | 69925528.4 | 0.20969
GEN-2023-026 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 430314.2268 | 2.458% | 17509993.2 | 0.06045
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 17874.0218 | 1.99% | 898410 | 0.006
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 147716.66 | 1.978% | 7467300 | 0.05038
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 1529080.798 | 18.42% | 8302968 | 0.13545
GEN-2023-032 | 03 CENTRAL | 158733 | ERIS | Odessa and Lexington 161 kV Line GEN-2023-032 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-032 (200MW/Solar), into Odessa and Lexington 161 kV Line | 15889780 | 100% | 15889780 | 1
GEN-2023-032 | 03 CENTRAL | 158732 | ERIS | Odessa and Lexington 161 kV Line GEN-2023-032 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-032 (200MW/Solar), into Odessa and Lexington 161 kV Line | 751752 | 100% | 751752 | 1
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MOCITYB1 to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing 5MOCITYB1 to ECKLES-161 161 kV line 1 (6.07 miles) to a standard rating of 557 MVA | 1039493.9293 | 17.51% | 5937819.68 | 0.0898
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Rebuild the 5OVERTON 2 to G23-115-TAP 161kV line 1 | Current Study | Rebuild the existing 5OVERTON 2 to G23-115-TAP 161 kV line 1 (20.5 miles) to a standard rating of 557 MVA | 1387848.0245 | 6.921% | 20053592 | 0.07008
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 96666.2681 | 2.615% | 3696554.12 | 0.04682
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 382960.788 | 2.191% | 17475659.88 | 0.04936
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161kV line 1 | Current Study | Rebuild the existing LBRTYST5 to BRMGHAM5 161 kV line 1 (4.03 miles) to a standard rating of 557 MVA | 173403.4078 | 4.399% | 3942242.72 | 0.05062
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 412399.2976 | 2.355% | 17509993.2 | 0.0869
GEN-2023-032 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 208427.9213 | 17.9% | 1164086.56 | 0.27089
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 17278.2211 | 1.923% | 898410 | 0.0058
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 147599.378 | 1.977% | 7467300 | 0.05034
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 774418.1819 | 9.327% | 8302968 | 0.0686
GEN-2023-033 | 03 CENTRAL | 158735 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | 887099 | 100% | 887099 | 1
GEN-2023-033 | 03 CENTRAL | 158734 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | 751752 | 100% | 751752 | 1
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MOCITYB2 to G23-169-TAP 161kV line 1 | Current Study | Rebuild the existing 5MOCITYB2 to G23-169-TAP 161 kV line 1 (0.35 miles) to a standard rating of 557 MVA | 139899.5151 | 40.86% | 342378.4 | 0.30446
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 95159.0837 | 2.574% | 3696554.12 | 0.04609
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 383115.9585 | 2.192% | 17475659.88 | 0.04938
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161kV line 1 | Current Study | Rebuild the existing LBRTYST5 to BRMGHAM5 161 kV line 1 (4.03 miles) to a standard rating of 557 MVA | 2277264.2714 | 57.77% | 3942242.72 | 0.66478
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 439592.0245 | 2.511% | 17509993.2 | 0.09263
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 105564.2911 | 9.068% | 1164086.56 | 0.1372
GEN-2023-033 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYPL to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing SIBLEYPL to ECKLES-161 161 kV line 1 (3.09 miles) to a standard rating of 557 MVA | 366403.1367 | 12.12% | 3022712.16 | 0.19735
GEN-2023-033 | 03 CENTRAL | TBD | NRIS | Rebuild the LEVEE5 to NEASTN 161kV line 1 | Current Study | Rebuild the LEVEE5 to NEASTN 161kV line CKT1 (5.19 miles) to a standard rating of 557 MVA | 2276381.0916 | 44.84% | 5076982.56 | 0.06138
GEN-2023-034 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 27196.2263 | 0.3642% | 7467300 | 0.01427
GEN-2023-034 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 2.049% | 87298154 | 0.03584
GEN-2023-034 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 991224.4257 | 1.53% | 64782504 | 0.03123
GEN-2023-034 | 03 CENTRAL | 158737 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | 13079166 | 100% | 13079166 | 1
GEN-2023-034 | 03 CENTRAL | 158736 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | 745228 | 100% | 745228 | 1
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 17486.7513 | 1.946% | 898410 | 0.00587
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 147775.301 | 1.979% | 7467300 | 0.0504
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 1947673.0165 | 23.46% | 8302968 | 0.17253
GEN-2023-036 | 03 CENTRAL | 158741 | ERIS | Eckles Road 161 kV Substation GEN-2023-036 Interconnection (Non-Shared NU) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-036 (200MW/Battery/Storage), into Eckles Road 161 kV Substation | 3200000 | 100% | 3200000 | 1
GEN-2023-036 | 03 CENTRAL | 158740 | ERIS | Eckles Road 161 kV Substation GEN-2023-036 Interconnection (TOIF) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-036 (200MW/Battery/Storage), into Eckles Road 161 kV Substation. | 0 | 100% | 0 | 1
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MOCITYB1 to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing 5MOCITYB1 to ECKLES-161 161 kV line 1 (6.07 miles) to a standard rating of 557 MVA | 2566670.2556 | 43.23% | 5937819.68 | 0.22173
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 95757.8282 | 2.59% | 3696554.12 | 0.04638
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Rebuild the BLUMILS5 to BLUVLY-161 161kV line 1 | Current Study | Rebuild the existing BLUMILS5 to BLUVLY-161 161 kV line 1 (4.7 miles) to a standard rating of 557 MVA | 1259566.2004 | 27.4% | 4597652.8 | 0.16
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 383271.129 | 2.193% | 17475659.88 | 0.0494
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161kV line 1 | Current Study | Rebuild the existing LBRTYST5 to BRMGHAM5 161 kV line 1 (4.03 miles) to a standard rating of 557 MVA | 442826.1265 | 11.23% | 3942242.72 | 0.12927
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 433185.3611 | 2.474% | 17509993.2 | 0.09128
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 265495.7308 | 22.81% | 1164086.56 | 0.34506
GEN-2023-036 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYPL to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing SIBLEYPL to ECKLES-161 161 kV line 1 (3.09 miles) to a standard rating of 557 MVA | 1046574.3509 | 34.62% | 3022712.16 | 0.5637
GEN-2023-037 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 17486.7513 | 1.946% | 898410 | 0.00587
GEN-2023-037 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 152056.0935 | 2.036% | 7467300 | 0.05186
GEN-2023-037 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 250500.5752 | 3.017% | 8302968 | 0.02219
GEN-2023-037 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 97017.2563 | 2.625% | 3696554.12 | 0.04699
GEN-2023-037 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 395374.4278 | 2.262% | 17475659.88 | 0.05096
GEN-2023-037 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 468398.2816 | 2.675% | 17509993.2 | 0.0987
GEN-2023-037 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 34139.1224 | 2.933% | 1164086.56 | 0.04437
GEN-2023-037 | 03 CENTRAL | 158743 | ERIS | Quindaro Bluffs 161 kV Substation GEN-2023-037 Interconnection (Non-Shared NU) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Quindaro Bluffs 161 kV Substation | 3357305 | 100% | 3357305 | 1
GEN-2023-037 | 03 CENTRAL | 158742 | ERIS | Quindaro Bluffs 161 kV Substation GEN-2023-037 Interconnection (TOIF) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Quindaro Bluffs 161 kV Substation | 0 | 100% | 0 | 1
GEN-2023-039 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 513.1087 | 0.006871% | 7467300 | 0.00014
GEN-2023-039 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.6113% | 87298154 | 0.00556
GEN-2023-039 | 03 CENTRAL | 158746 | ERIS | Carpenter 345 kV Substation GEN-2023-039 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-039 (250MW/Wind), into Carpenter 345 kV Substation | 950000 | 100% | 950000 | 1
GEN-2023-039 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1169967.0967 | 1.764% | 66320529.8 | 0.08838
GEN-2023-039 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 487089.9591 | 1.112% | 43786427.44 | 0.02687
GEN-2023-039 | 03 CENTRAL | 158660 | ERIS | Carpenter 345 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-039/068/093/094 (250MW/Wind), into Carpenter 345 kV Substation | 1268628.5 | 25% | 5074514 | 1
GEN-2023-042 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 15669.5591 | 1.744% | 898410 | 0.00526
GEN-2023-042 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 21785.1287 | 0.2917% | 7467300 | 0.00743
GEN-2023-042 | 03 CENTRAL | TBD | ERIS | Build a new Grove 161/138 kV transformer 2 | Current Study | Build a new Grove 161/138 kV transformer 2 | 953219.5577 | 26.43% | 3606166 | 0.05695
GEN-2023-042 | 03 CENTRAL | 158750 | ERIS | Noel Southwest 161 kV Substation GEN-2023-042 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-042 (200MW/Solar), into Noel Southwest 161 kV Substation | 9592156.56 | 100% | 9592156.56 | 1
GEN-2023-042 | 03 CENTRAL | 158749 | ERIS | Noel Southwest 161 kV Substation GEN-2023-042 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-042 (200MW/Solar), into Noel Southwest 161 kV Substation | 1713303.4 | 100% | 1713303.4 | 1
GEN-2023-042 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 328637.6352 | 1.855% | 17715993.12 | 0.06683
GEN-2023-042 | 03 CENTRAL | TBD | ERIS | Rebuild the FLINTCR5 to DEC392 5 161kV line 1 | Current Study | Rebuild the existing FLINTCR5 to DEC392 5 161 kV line 1 (6.03 miles) to a standard rating of 557 MVA | 3449828.725 | 58.48% | 5898690.72 | 0.54413
GEN-2023-042 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYRD5 to NOL435 5 161kV line 1 | Current Study | Rebuild the existing SIBLEYRD5 to NOL435 5 161 kV line 1 (3.93 miles) to a standard rating of 557 MVA | 2296893.2958 | 59.75% | 3844420.32 | 0.52268
GEN-2023-042 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 2 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 2 (43.1 miles) to a standard rating of 557 MVA | 2413930.9218 | 5.725% | 42161454.4 | 0.02716
GEN-2023-043 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 20934.8343 | 0.2804% | 7467300 | 0.00714
GEN-2023-043 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 1.53% | 87298154 | 0.0174
GEN-2023-043 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 76880.4078 | 6.836% | 1124696.25 | 0.17207
GEN-2023-043 | 03 CENTRAL | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 783211.4625 | 9.433% | 8302968 | 0.04269
GEN-2023-043 | 03 CENTRAL | 158751 | ERIS | Setab 345 kV Substation GEN-2023-043 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043 (200MW/Solar), into Setab 345 kV Substation | 666667 | 100% | 666667 | 1
GEN-2023-043 | 03 CENTRAL | 158675 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043/044/045/046/047/048/107 (200/200/250/250/250/300MW/Solar/Wind), into Setab 345 kV Substation | 2941176.4706 | 11.76% | 25000000 | 1
GEN-2023-043 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 17375.0183 | 2.024% | 858333 | 0.17207
GEN-2023-043 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 3462721.3543 | 5.221% | 66320529.8 | 0.32697
GEN-2023-043 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1445136.2687 | 3.3% | 43786427.44 | 0.09965
GEN-2023-043 | 03 CENTRAL | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 195802.3282 | 9.944% | 1969026.8 | 0.06495
GEN-2023-044 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 20934.8343 | 0.2804% | 7467300 | 0.00714
GEN-2023-044 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 1.53% | 87298154 | 0.0174
GEN-2023-044 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 76880.4078 | 6.836% | 1124696.25 | 0.17207
GEN-2023-044 | 03 CENTRAL | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 783211.4625 | 9.433% | 8302968 | 0.04269
GEN-2023-044 | 03 CENTRAL | 158675 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043/044/045/046/047/048/107 (200/200/250/250/250/300MW/Solar/Wind), into Setab 345 kV Substation | 2941176.4706 | 11.76% | 25000000 | 1
GEN-2023-044 | 03 CENTRAL | 158752 | ERIS | Setab 345 kV Substation GEN-2023-044 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-044 (200MW/Solar), into Setab 345 kV Substation | 666667 | 100% | 666667 | 1
GEN-2023-044 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 17375.0183 | 2.024% | 858333 | 0.17207
GEN-2023-044 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 3462721.3543 | 5.221% | 66320529.8 | 0.32697
GEN-2023-044 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1445136.2687 | 3.3% | 43786427.44 | 0.09965
GEN-2023-044 | 03 CENTRAL | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 195802.3282 | 9.944% | 1969026.8 | 0.06495
GEN-2023-045 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 30823.1717 | 0.4128% | 7467300 | 0.00841
GEN-2023-045 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.6773% | 87298154 | 0.00616
GEN-2023-045 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 94318.9055 | 8.386% | 1124696.25 | 0.16888
GEN-2023-045 | 03 CENTRAL | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 1048730.9727 | 12.63% | 8302968 | 0.04573
GEN-2023-045 | 03 CENTRAL | 158675 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043/044/045/046/047/048/107 (200/200/250/250/250/300MW/Solar/Wind), into Setab 345 kV Substation | 3676470.5882 | 14.71% | 25000000 | 1
GEN-2023-045 | 03 CENTRAL | 158753 | ERIS | Setab 345 kV Substation GEN-2023-045 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-045 (250MW/Wind), into Setab 345 kV Substation | 333333 | 100% | 333333 | 1
GEN-2023-045 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 21316.1293 | 2.483% | 858333 | 0.16888
GEN-2023-045 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 4095943.8719 | 6.176% | 66320529.8 | 0.30941
GEN-2023-045 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1424108.1945 | 3.252% | 43786427.44 | 0.07856
GEN-2023-045 | 03 CENTRAL | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 248935.7544 | 12.64% | 1969026.8 | 0.06606
GEN-2023-046 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 30823.1717 | 0.4128% | 7467300 | 0.00841
GEN-2023-046 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.6773% | 87298154 | 0.00616
GEN-2023-046 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 94318.9055 | 8.386% | 1124696.25 | 0.16888
GEN-2023-046 | 03 CENTRAL | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 1048730.9727 | 12.63% | 8302968 | 0.04573
GEN-2023-046 | 03 CENTRAL | 158675 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043/044/045/046/047/048/107 (200/200/250/250/250/300MW/Solar/Wind), into Setab 345 kV Substation | 3676470.5882 | 14.71% | 25000000 | 1
GEN-2023-046 | 03 CENTRAL | 158754 | ERIS | Setab 345 kV Substation GEN-2023-046 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-046 (250MW/Wind), into Setab 345 kV Substation | 333333 | 100% | 333333 | 1
GEN-2023-046 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 21316.1293 | 2.483% | 858333 | 0.16888
GEN-2023-046 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 4095943.8719 | 6.176% | 66320529.8 | 0.30941
GEN-2023-046 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1424108.1945 | 3.252% | 43786427.44 | 0.07856
GEN-2023-046 | 03 CENTRAL | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 248935.7544 | 12.64% | 1969026.8 | 0.06606
GEN-2023-047 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 30823.1717 | 0.4128% | 7467300 | 0.00841
GEN-2023-047 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.6773% | 87298154 | 0.00616
GEN-2023-047 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 94318.9055 | 8.386% | 1124696.25 | 0.16888
GEN-2023-047 | 03 CENTRAL | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 1048730.9727 | 12.63% | 8302968 | 0.04573
GEN-2023-047 | 03 CENTRAL | 158675 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043/044/045/046/047/048/107 (200/200/250/250/250/300MW/Solar/Wind), into Setab 345 kV Substation | 3676470.5882 | 14.71% | 25000000 | 1
GEN-2023-047 | 03 CENTRAL | 158755 | ERIS | Setab 345 kV Substation GEN-2023-047 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-047 (250MW/Wind), into Setab 345 kV Substation | 333333 | 100% | 333333 | 1
GEN-2023-047 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 21316.1293 | 2.483% | 858333 | 0.16888
GEN-2023-047 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 4095943.8719 | 6.176% | 66320529.8 | 0.30941
GEN-2023-047 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1424108.1945 | 3.252% | 43786427.44 | 0.07856
GEN-2023-047 | 03 CENTRAL | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 248935.7544 | 12.64% | 1969026.8 | 0.06606
GEN-2023-048 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 30823.1717 | 0.4128% | 7467300 | 0.00841
GEN-2023-048 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.6773% | 87298154 | 0.00616
GEN-2023-048 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 94318.9055 | 8.386% | 1124696.25 | 0.16888
GEN-2023-048 | 03 CENTRAL | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 1048730.9727 | 12.63% | 8302968 | 0.04573
GEN-2023-048 | 03 CENTRAL | 158675 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043/044/045/046/047/048/107 (200/200/250/250/250/300MW/Solar/Wind), into Setab 345 kV Substation | 3676470.5882 | 14.71% | 25000000 | 1
GEN-2023-048 | 03 CENTRAL | 158756 | ERIS | Setab 345 kV Substation GEN-2023-048 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-048 (250MW/Wind), into Setab 345 kV Substation | 333333 | 100% | 333333 | 1
GEN-2023-048 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 21316.1293 | 2.483% | 858333 | 0.16888
GEN-2023-048 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 4095943.8719 | 6.176% | 66320529.8 | 0.30941
GEN-2023-048 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1424108.1945 | 3.252% | 43786427.44 | 0.07856
GEN-2023-048 | 03 CENTRAL | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 248935.7544 | 12.64% | 1969026.8 | 0.06606
GEN-2023-050 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 114393.7394 | 12.73% | 898410 | 0.0192
GEN-2023-050 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 1051022.508 | 14.08% | 7467300 | 0.17923
GEN-2023-050 | 03 CENTRAL | TBD | ERIS | Build a new G20-079-TAP to STL439 5 161kV line 1 | Current Study | Build a new G20-079-TAP to STL439 5 161 kV line 1 (12.24 miles) to a standard rating of 557 MVA | 1805977.4234 | 14.11% | 12799894.32 | 0.02155
GEN-2023-050 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 6042223.2292 | 9.327% | 64782504 | 0.06187
GEN-2023-050 | 03 CENTRAL | TBD | ERIS | Build a new RIV4525 to G20-079-TAP 161kV line 2 | Current Study | Build a new RIV4525 to G20-079-TAP 161 kV line 2 (5.47 miles) to a standard rating of 557 MVA | 816916.2161 | 14.28% | 5720214.21 | 0.02722
GEN-2023-050 | 03 CENTRAL | 158760 | ERIS | Neosho 345 kV Substation GEN-2023-050 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-050 (400MW/Hybrid), into Neosho 345 kV Substation | 2764794 | 100% | 2764794 | 1
GEN-2023-050 | 03 CENTRAL | 158759 | ERIS | Neosho 345 kV Substation GEN-2023-050 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-050 (400MW/Hybrid), into Neosho 345 kV Substation | 1325114 | 100% | 1325114 | 1
GEN-2023-050 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 11338117.0678 | 31.49% | 36004208.24 | 0.29818
GEN-2023-050 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 396368.8627 | 10.72% | 3696554.12 | 0.09599
GEN-2023-050 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 1138503.4462 | 6.426% | 17715993.12 | 0.11576
GEN-2023-050 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 2651863.8034 | 15.17% | 17475659.88 | 0.1709
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 8087.9949 | 0.9003% | 898410 | 0.00181
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 138407.4025 | 1.854% | 7467300 | 0.03147
GEN-2023-052 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 6.578% | 87298154 | 0.04986
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 3107784.8507 | 4.797% | 64782504 | 0.04243
GEN-2023-052 | 03 CENTRAL | 158763 | ERIS | Rose Hill 345 kV Substation GEN-2023-052 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-052 (300MW/Hybrid), into Rose Hill 345 kV Substation | 1325114 | 100% | 1325114 | 1
GEN-2023-052 | 03 CENTRAL | 158674 | ERIS | Rose Hill 345 kV Substation Interconnection (DISIS-2023-001) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-052/073 (300/400MW/Hybrid/Battery/Storage), into Rose Hill 345 kV Substation | 6048132 | 42.86% | 14112308 | 1
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 957074.2726 | 2.658% | 36004208.24 | 0.03356
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 95324.2546 | 2.579% | 3696554.12 | 0.03078
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 3414108.8462 | 19.27% | 17715993.12 | 0.46285
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 357745.5821 | 2.047% | 17475659.88 | 0.03074
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Rebuild the ELPASO 4 to ROSEHIL4 138kV line 1 | Current Study | Rebuild the existing ELPASO 4 to ROSEHIL4 138 kV line 1 (8.37 miles) to a standard rating of 478 MVA | 1344339.6243 | 16.66% | 8070010.83 | 0.05301
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Rebuild the ROSEHIL4 to STEARMN4 138kV line 1 | Current Study | Rebuild the existing ROSEHIL4 to STEARMN4 138 kV line 1 (11.64 miles) to a standard rating of 478 MVA | 2778599.9746 | 24.76% | 11222810.76 | 0.03443
GEN-2023-052 | 03 CENTRAL | TBD | ERIS | Rebuild the WEAVER 4 to ROSEHIL4 138kV line 1 | Current Study | Rebuild the existing WEAVER 4 to ROSEHIL4 138 kV line 1 (7.51 miles) to a standard rating of 478 MVA | 1726300.9497 | 23.84% | 7240834.09 | 0.04876
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 21046.6606 | 2.343% | 898410 | 0.01413
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 76247.9505 | 1.021% | 7467300 | 0.05201
GEN-2023-061 | 03 CENTRAL | TBD | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | Current Study | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | 509827.7332 | 14.14% | 3606166 | 0.03991
GEN-2023-061 | 03 CENTRAL | 158778 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | 4200000 | 100% | 4200000 | 1
GEN-2023-061 | 03 CENTRAL | 158777 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | 700000 | 100% | 700000 | 1
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the AUR124 5 to G19-035-TAP 161kV line 1 | Current Study | Rebuild the existing AUR124 5 to G19-035-TAP 161 kV line 1 (8.3 miles) to a standard rating of 557 MVA | 1561061.2214 | 19.23% | 8119259.2 | 0.05201
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the AUR124 5 to MON383 5 161kV line 1 | Current Study | Rebuild the existing AUR124 5 to MON383 5 161 kV line 1 (11.51 miles) to a standard rating of 557 MVA | 1311569.0377 | 11.65% | 11259358.24 | 0.10065
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 171449.2167 | 0.9678% | 17715993.12 | 0.06973
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 201760.4395 | 1.155% | 17475659.88 | 0.05201
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the FLINTCR5 to DEC392 5 161kV line 1 | Current Study | Rebuild the existing FLINTCR5 to DEC392 5 161 kV line 1 (6.03 miles) to a standard rating of 557 MVA | 315926.2775 | 5.356% | 5898690.72 | 0.09966
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the LAR382 5 to MON383 5 161kV line 1 | Current Study | Rebuild the existing LAR382 5 to MON383 5 161 kV line 1 (15.56 miles) to a standard rating of 557 MVA | 2162742.6015 | 14.21% | 15221165.44 | 0.10884
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the NEO SPA5 to CARTHAG5 161kV line 1 | Current Study | Rebuild the existing NEO SPA5 to CARTHAG5 161 kV line 1 (22.9 miles) to a standard rating of 557 MVA | 5229159.0105 | 23.34% | 22401329.6 | 0.21208
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the RDS295 5 to G19-035-TAP 161kV line 1 | Current Study | Rebuild the existing RDS295 5 to G19-035-TAP 161 kV line 1 (15.41 miles) to a standard rating of 557 MVA | 2898307.6411 | 19.23% | 15074431.84 | 0.05201
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYRD5 to NOL435 5 161kV line 1 | Current Study | Rebuild the existing SIBLEYRD5 to NOL435 5 161 kV line 1 (3.93 miles) to a standard rating of 557 MVA | 200167.3866 | 5.207% | 3844420.32 | 0.0911
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 1 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 1 (43.1 miles) to a standard rating of 557 MVA | 5084298.0531 | 12.06% | 42161454.4 | 0.10786
GEN-2023-061 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 2 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 2 (43.1 miles) to a standard rating of 557 MVA | 4793199.3597 | 11.37% | 42161454.4 | 0.10786
GEN-2023-063 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 24994.5852 | 2.782% | 898410 | 0.01243
GEN-2023-063 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 138796.6321 | 1.859% | 7467300 | 0.07013
GEN-2023-063 | 03 CENTRAL | 158782 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | 11500000 | 100% | 11500000 | 1
GEN-2023-063 | 03 CENTRAL | 158781 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | 2125000 | 100% | 2125000 | 1
GEN-2023-063 | 03 CENTRAL | TBD | ERIS | Rebuild the CATOOSA4 to LLANETP4 138kV line 1 | Current Study | Rebuild the existing CATOOSA4 to LLANETP4 138 kV line 1 (1.8 miles) to a standard rating of 286 MVA | 1735486.2 | 100% | 1735486.2 | 0.16964
GEN-2023-063 | 03 CENTRAL | TBD | ERIS | Rebuild the LLAN ET4 to CATOOSA4 138kV line 1 | Current Study | Rebuild the existing LLAN ET4 to CATOOSA4 138 kV line 1 (2.84 miles) to a standard rating of 286 MVA | 2450823.8162 | 89.5% | 2738211.56 | 0.16361
GEN-2023-063 | 03 CENTRAL | TBD | ERIS | Rebuild the LLAN ET4 to E41ST_W4 138kV line 1 | Current Study | Rebuild the existing LLAN ET4 to E41ST_W4 138 kV line 1 (3.46 miles) to a standard rating of 286 MVA | 2985862.8183 | 89.5% | 3335990.14 | 0.16361
GEN-2023-063 | 03 CENTRAL | TBD | ERIS | Rebuild the MAYO--N4 to E41ST_W4 138kV line 1 | Current Study | Rebuild the existing MAYO--N4 to E41ST_W4 138 kV line 1 (2.6 miles) to a standard rating of 286 MVA | 2243711.9444 | 89.5% | 2506813.4 | 0.16361
GEN-2023-063 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO-N4 to MAYO--N4 138kV line 1 | Current Study | Rebuild the existing MINGO-N4 to MAYO--N4 138 kV line 1 (1.75 miles) to a standard rating of 286 MVA | 1510190.7318 | 89.5% | 1687278.25 | 0.16361
GEN-2023-065 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 40679.2565 | 0.5448% | 7467300 | 0.01982
GEN-2023-065 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 2.257% | 87298154 | 0.03666
GEN-2023-065 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 823761.9676 | 1.272% | 64782504 | 0.0241
GEN-2023-065 | 03 CENTRAL | 158786 | ERIS | Halstead 69 kV Substation GEN-2023-065 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-065 (140MW/Battery/Storage), into Halstead 69 kV Substation | 846415 | 100% | 846415 | 1
GEN-2023-065 | 03 CENTRAL | 158785 | ERIS | Halstead 69 kV Substation GEN-2023-065 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-065 (140MW/Battery/Storage), into Halstead 69 kV Substation | 724451 | 100% | 724451 | 1
GEN-2023-068 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 513.1087 | 0.006871% | 7467300 | 0.00014
GEN-2023-068 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.6113% | 87298154 | 0.00556
GEN-2023-068 | 03 CENTRAL | 158660 | ERIS | Carpenter 345 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-039/068/093/094 (250MW/Wind), into Carpenter 345 kV Substation | 1268628.5 | 25% | 5074514 | 1
GEN-2023-068 | 03 CENTRAL | 158791 | ERIS | Carpenter 345 kV Substation GEN-2023-068 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-068 (250MW/Wind), into Carpenter 345 kV Substation | 950000 | 100% | 950000 | 1
GEN-2023-068 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1169967.0967 | 1.764% | 66320529.8 | 0.08838
GEN-2023-068 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 487089.9591 | 1.112% | 43786427.44 | 0.02687
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 10783.9931 | 1.2% | 898410 | 0.00181
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 184543.2033 | 2.471% | 7467300 | 0.03147
GEN-2023-073 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 8.771% | 87298154 | 0.04986
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 4143713.1342 | 6.396% | 64782504 | 0.04243
GEN-2023-073 | 03 CENTRAL | 158674 | ERIS | Rose Hill 345 kV Substation Interconnection (DISIS-2023-001) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-052/073 (300/400MW/Hybrid/Battery/Storage), into Rose Hill 345 kV Substation | 8064176 | 57.14% | 14112308 | 1
GEN-2023-073 | 03 CENTRAL | 158800 | ERIS | Rose Hill 345 kV Substation GEN-2023-073 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-073 (400MW/Battery/Storage), into Rose Hill 345 kV Substation | 1325114 | 100% | 1325114 | 1
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 1276099.0301 | 3.544% | 36004208.24 | 0.03356
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 127099.0061 | 3.438% | 3696554.12 | 0.03078
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 4552145.1283 | 25.7% | 17715993.12 | 0.46285
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 476994.1095 | 2.729% | 17475659.88 | 0.03074
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Rebuild the ELPASO 4 to ROSEHIL4 138kV line 1 | Current Study | Rebuild the existing ELPASO 4 to ROSEHIL4 138 kV line 1 (8.37 miles) to a standard rating of 478 MVA | 1792452.8323 | 22.21% | 8070010.83 | 0.05301
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Rebuild the ROSEHIL4 to STEARMN4 138kV line 1 | Current Study | Rebuild the existing ROSEHIL4 to STEARMN4 138 kV line 1 (11.64 miles) to a standard rating of 478 MVA | 3704799.9661 | 33.01% | 11222810.76 | 0.03443
GEN-2023-073 | 03 CENTRAL | TBD | ERIS | Rebuild the WEAVER 4 to ROSEHIL4 138kV line 1 | Current Study | Rebuild the existing WEAVER 4 to ROSEHIL4 138 kV line 1 (7.51 miles) to a standard rating of 478 MVA | 2301734.5996 | 31.79% | 7240834.09 | 0.04876
GEN-2023-085 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 15684.4541 | 1.746% | 898410 | 0.00702
GEN-2023-085 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 74679.3039 | 1% | 7467300 | 0.03396
GEN-2023-085 | 03 CENTRAL | TBD | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | Current Study | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | 479616.1925 | 13.3% | 3606166 | 0.02503
GEN-2023-085 | 03 CENTRAL | 158817 | ERIS | Mansfield - Logan 161 kV Line GEN-2023-085 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-085 (150MW/Wind), into Mansfield - Logan 161 kV Line | 8600000 | 100% | 8600000 | 1
GEN-2023-085 | 03 CENTRAL | 158816 | ERIS | Mansfield - Logan 161 kV Line GEN-2023-085 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-085 (150MW/Wind), into Mansfield - Logan 161 kV Line | 800000 | 100% | 800000 | 1
GEN-2023-085 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MANSFDMN to G23-085-TAP 161kV line 1 | Current Study | Rebuild the existing 5MANSFDMN to G23-085-TAP 161 kV line 1 (0.8 miles) to a standard rating of 557 MVA | 727469.4872 | 92.96% | 782579.2 | 0.68378
GEN-2023-085 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 197609.6287 | 1.131% | 17475659.88 | 0.03396
GEN-2023-087 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 19989.1144 | 2.225% | 898410 | 0.00671
GEN-2023-087 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 160734.9604 | 2.153% | 7467300 | 0.05482
GEN-2023-087 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 276577.9221 | 3.331% | 8302968 | 0.0245
GEN-2023-087 | 03 CENTRAL | 158821 | ERIS | Archie 161 kV Substation GEN-2023-087 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-087 (200MW/Solar), into Archie 161 kV Substation | 22572276 | 100% | 22572276 | 1
GEN-2023-087 | 03 CENTRAL | 158820 | ERIS | Archie 161 kV Substation GEN-2023-087 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-087 (200MW/Solar), into Archie 161 kV Substation | 884472 | 100% | 884472 | 1
GEN-2023-087 | 03 CENTRAL | TBD | ERIS | Rebuild the 5OVERTON 2 to G23-115-TAP 161kV line 1 | Current Study | Rebuild the existing 5OVERTON 2 to G23-115-TAP 161 kV line 1 (20.5 miles) to a standard rating of 557 MVA | 856314.9055 | 4.27% | 20053592 | 0.04324
GEN-2023-087 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 110230.9281 | 2.982% | 3696554.12 | 0.05339
GEN-2023-087 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 417098.2975 | 2.387% | 17475659.88 | 0.05376
GEN-2023-087 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 402006.2658 | 2.296% | 17509993.2 | 0.08471
GEN-2023-087 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 37701.5325 | 3.239% | 1164086.56 | 0.049
GEN-2023-089 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 27304.7121 | 0.3657% | 7467300 | 0.00745
GEN-2023-089 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.9598% | 87298154 | 0.00873
GEN-2023-089 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 72621.3127 | 6.457% | 1124696.25 | 0.13003
GEN-2023-089 | 03 CENTRAL | TBD | ERIS | Build a new Spearville 345/230 kV transformer 2 | Current Study | Build a new Spearville 345/230 kV transformer 2 | 2067472.1116 | 24.9% | 8302968 | 0.05031
GEN-2023-089 | 03 CENTRAL | 158824 | ERIS | Buckner 345 kV Substation GEN-2023-089 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-089 (250MW/Wind), into Buckner 345 kV Substation | 833333 | 100% | 833333 | 1
GEN-2023-089 | 03 CENTRAL | 158658 | ERIS | Buckner 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-089/090/091 (250/250/504MW/Wind), into Buckner 345 kV Substation | 4357569.7211 | 24.9% | 17500000 | 1
GEN-2023-089 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 16412.4603 | 1.912% | 858333 | 0.13003
GEN-2023-089 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 717627.4758 | 1.082% | 66320529.8 | 0.05421
GEN-2023-089 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 514281.4343 | 1.175% | 43786427.44 | 0.02837
GEN-2023-089 | 03 CENTRAL | TBD | ERIS | Rebuild the SPEARVL6 to G19-053-TAP 230kV line 1 | Current Study | Rebuild the existing SPEARVL6 to G19-053-TAP 230 kV line 1 (24.46 miles) to a standard rating of 796 MVA | 5381133.003 | 24.9% | 21610630.14 | 0.06553
GEN-2023-090 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 27304.7121 | 0.3657% | 7467300 | 0.00745
GEN-2023-090 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.9598% | 87298154 | 0.00873
GEN-2023-090 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 72621.3127 | 6.457% | 1124696.25 | 0.13003
GEN-2023-090 | 03 CENTRAL | TBD | ERIS | Build a new Spearville 345/230 kV transformer 2 | Current Study | Build a new Spearville 345/230 kV transformer 2 | 2067472.1116 | 24.9% | 8302968 | 0.05031
GEN-2023-090 | 03 CENTRAL | 158658 | ERIS | Buckner 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-089/090/091 (250/250/504MW/Wind), into Buckner 345 kV Substation | 4357569.7211 | 24.9% | 17500000 | 1
GEN-2023-090 | 03 CENTRAL | 158825 | ERIS | Buckner 345 kV Substation GEN-2023-090 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-090 (250MW/Wind), into Buckner 345 kV Substation | 833333 | 100% | 833333 | 1
GEN-2023-090 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 16412.4603 | 1.912% | 858333 | 0.13003
GEN-2023-090 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 717627.4758 | 1.082% | 66320529.8 | 0.05421
GEN-2023-090 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 514281.4343 | 1.175% | 43786427.44 | 0.02837
GEN-2023-090 | 03 CENTRAL | TBD | ERIS | Rebuild the SPEARVL6 to G19-053-TAP 230kV line 1 | Current Study | Rebuild the existing SPEARVL6 to G19-053-TAP 230 kV line 1 (24.46 miles) to a standard rating of 796 MVA | 5381133.003 | 24.9% | 21610630.14 | 0.06553
GEN-2023-091 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 55046.2996 | 0.7372% | 7467300 | 0.00745
GEN-2023-091 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 1.935% | 87298154 | 0.00873
GEN-2023-091 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 146404.5664 | 13.02% | 1124696.25 | 0.13003
GEN-2023-091 | 03 CENTRAL | TBD | ERIS | Build a new Spearville 345/230 kV transformer 2 | Current Study | Build a new Spearville 345/230 kV transformer 2 | 4168023.7769 | 50.2% | 8302968 | 0.05031
GEN-2023-091 | 03 CENTRAL | 158658 | ERIS | Buckner 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-089/090/091 (250/250/504MW/Wind), into Buckner 345 kV Substation | 8784860.5578 | 50.2% | 17500000 | 1
GEN-2023-091 | 03 CENTRAL | 158826 | ERIS | Buckner 345 kV Substation GEN-2023-091 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-091 (504MW/Wind), into Buckner 345 kV Substation | 833333 | 100% | 833333 | 1
GEN-2023-091 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 33087.5199 | 3.855% | 858333 | 0.13003
GEN-2023-091 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1446736.9913 | 2.181% | 66320529.8 | 0.05421
GEN-2023-091 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1036791.3715 | 2.368% | 43786427.44 | 0.02837
GEN-2023-091 | 03 CENTRAL | TBD | ERIS | Rebuild the SPEARVL6 to G19-053-TAP 230kV line 1 | Current Study | Rebuild the existing SPEARVL6 to G19-053-TAP 230 kV line 1 (24.46 miles) to a standard rating of 796 MVA | 10848364.134 | 50.2% | 21610630.14 | 0.06553
GEN-2023-093 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 513.1087 | 0.006871% | 7467300 | 0.00014
GEN-2023-093 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.6113% | 87298154 | 0.00556
GEN-2023-093 | 03 CENTRAL | 158660 | ERIS | Carpenter 345 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-039/068/093/094 (250MW/Wind), into Carpenter 345 kV Substation | 1268628.5 | 25% | 5074514 | 1
GEN-2023-093 | 03 CENTRAL | 158829 | ERIS | Carpenter 345 kV Substation GEN-2023-093 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-093 (250MW/Wind), into Carpenter 345 kV Substation | 11573021 | 100% | 11573021 | 1
GEN-2023-093 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1169967.0967 | 1.764% | 66320529.8 | 0.08838
GEN-2023-093 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 487089.9591 | 1.112% | 43786427.44 | 0.02687
GEN-2023-094 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 513.1087 | 0.006871% | 7467300 | 0.00014
GEN-2023-094 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.6113% | 87298154 | 0.00556
GEN-2023-094 | 03 CENTRAL | 158660 | ERIS | Carpenter 345 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-039/068/093/094 (250MW/Wind), into Carpenter 345 kV Substation | 1268628.5 | 25% | 5074514 | 1
GEN-2023-094 | 03 CENTRAL | 158830 | ERIS | Carpenter 345 kV Substation GEN-2023-094 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-094 (250MW/Wind), into Carpenter 345 kV Substation | 950000 | 100% | 950000 | 1
GEN-2023-094 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1169967.0967 | 1.764% | 66320529.8 | 0.08838
GEN-2023-094 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 487089.9591 | 1.112% | 43786427.44 | 0.02687
GEN-2023-099 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 15505.7139 | 1.726% | 898410 | 0.00347
GEN-2023-099 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 171744.8067 | 2.3% | 7467300 | 0.03905
GEN-2023-099 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 1149213.8654 | 1.774% | 64782504 | 0.01569
GEN-2023-099 | 03 CENTRAL | 158838 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | 0 | 100% | 0 | 1
GEN-2023-099 | 03 CENTRAL | 158837 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | 112910 | 100% | 112910 | 1
GEN-2023-099 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 115144.7623 | 3.115% | 3696554.12 | 0.03718
GEN-2023-099 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 451662.5258 | 2.585% | 17475659.88 | 0.03881
GEN-2023-099 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 450886.7349 | 2.575% | 17509993.2 | 0.06334
GEN-2023-107 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 36987.806 | 0.4953% | 7467300 | 0.00841
GEN-2023-107 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.8127% | 87298154 | 0.00616
GEN-2023-107 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 113182.6866 | 10.06% | 1124696.25 | 0.16888
GEN-2023-107 | 03 CENTRAL | TBD | ERIS | Build a new Setab 345/115 kV transformer 2 | Current Study | Build a new Setab 345/115 kV transformer 2 | 1258477.1673 | 15.16% | 8302968 | 0.04573
GEN-2023-107 | 03 CENTRAL | 158675 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043/044/045/046/047/048/107 (200/200/250/250/250/300MW/Solar/Wind), into Setab 345 kV Substation | 4411764.7059 | 17.65% | 25000000 | 1
GEN-2023-107 | 03 CENTRAL | 158849 | ERIS | Setab 345 kV Substation GEN-2023-107 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-107 (300MW/Wind), into Setab 345 kV | 1333333 | 100% | 1333333 | 1
GEN-2023-107 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 25579.3551 | 2.98% | 858333 | 0.16888
GEN-2023-107 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 4915132.6462 | 7.411% | 66320529.8 | 0.30941
GEN-2023-107 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 1708929.8334 | 3.903% | 43786427.44 | 0.07856
GEN-2023-107 | 03 CENTRAL | TBD | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | Current Study | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | 298722.9053 | 15.17% | 1969026.8 | 0.06606
GEN-2023-111 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 39465.3879 | 0.5285% | 7467300 | 0.01346
GEN-2023-111 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 3.1% | 87298154 | 0.03524
GEN-2023-111 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 1316456.5885 | 2.032% | 64782504 | 0.02696
GEN-2023-111 | 03 CENTRAL | 158854 | ERIS | Buffalo Flats 345 kV Substation GEN-2023-111 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-111 (200MW/Solar), into Buffalo Flats 345 kV Substation | 112909 | 100% | 112909 | 1
GEN-2023-111 | 03 CENTRAL | 158659 | ERIS | Buffalo Flats 345 kV Substation Interconnection (DISIS-2023-001) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-111/118 (200/200MW/Solar/Wind), into Buffalo Flats 345 kV Substation | 0 | 50% | 0 | 1
GEN-2023-111 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 460997.2186 | 0.6951% | 66320529.8 | 0.04353
GEN-2023-111 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 431003.0096 | 0.9843% | 43786427.44 | 0.02972
GEN-2023-115 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 25023.6305 | 2.785% | 898410 | 0.0056
GEN-2023-115 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 184587.184 | 2.472% | 7467300 | 0.04197
GEN-2023-115 | 03 CENTRAL | 158858 | ERIS | Tap Georgetown Overton to Sedalia East 161 kV Line GEN-2023-115 Intercon (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-115 (300MW/Solar), into Tap Georgetown Overton to Sedalia East 161 kV Line | 12461515 | 100% | 12461515 | 1
GEN-2023-115 | 03 CENTRAL | 158857 | ERIS | Tap Georgetown Overton to Sedalia East 161 kV Line GEN-2023-115 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-115 (300MW/Solar), into Tap Georgetown Overton to Sedalia East 161 kV Line | 751752 | 100% | 751752 | 1
GEN-2023-115 | 03 CENTRAL | TBD | ERIS | Rebuild the 5OVERTON 2 to G23-115-TAP 161kV line 1 | Current Study | Rebuild the existing 5OVERTON 2 to G23-115-TAP 161 kV line 1 (20.5 miles) to a standard rating of 557 MVA | 17809429.0699 | 88.81% | 20053592 | 0.59953
GEN-2023-115 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 126696.402 | 3.427% | 3696554.12 | 0.04091
GEN-2023-115 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 476334.6349 | 2.726% | 17475659.88 | 0.04093
GEN-2023-115 | 03 CENTRAL | TBD | ERIS | Rebuild the G22-100-TAP to G23-115-TAP 161kV line 1 | Current Study | Rebuild the existing G22-100-TAP to G23-115-TAP 161 kV line 1 (0.8 miles) to a standard rating of 557 MVA | 782579.2 | 100% | 782579.2 | 0.40047
GEN-2023-115 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 344180.1963 | 1.966% | 17509993.2 | 0.04835
GEN-2023-115 | 03 CENTRAL | TBD | ERIS | Rebuild the SEDALIA5 to SEDEAST5 161kV line 1 | Current Study | Rebuild the existing SEDALIA5 to SEDEAST5 161 kV line 1 (8.32 miles) to a standard rating of 557 MVA | 8138823.68 | 100% | 8138823.68 | 0.40047
GEN-2023-115 | 03 CENTRAL | TBD | ERIS | Rebuild the SEDEAST5 to G22-100-TAP 161kV line 1 | Current Study | Rebuild the existing SEDEAST5 to G22-100-TAP 161 kV line 1 (16.89 miles) to a standard rating of 557 MVA | 16522203.36 | 100% | 16522203.36 | 0.40047
GEN-2023-118 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 44479.1928 | 0.5957% | 7467300 | 0.01517
GEN-2023-118 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 2.111% | 87298154 | 0.024
GEN-2023-118 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 797393.7719 | 1.231% | 64782504 | 0.01633
GEN-2023-118 | 03 CENTRAL | 158659 | ERIS | Buffalo Flats 345 kV Substation Interconnection (DISIS-2023-001) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-111/118 (200/200MW/Solar/Wind), into Buffalo Flats 345 kV Substation | 0 | 50% | 0 | 1
GEN-2023-118 | 03 CENTRAL | 158861 | ERIS | Buffalo Flats 345 kV Substation GEN-2023-118 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-118 (200MW/Wind), into Buffalo Flats 345 kV Substation | 112911 | 100% | 112911 | 1
GEN-2023-118 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 275030.9618 | 0.4147% | 66320529.8 | 0.02597
GEN-2023-118 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 125153.2965 | 0.2858% | 43786427.44 | 0.00863
GEN-2023-121 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 2162.3866 | 0.02896% | 7467300 | 0.00295
GEN-2023-121 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.5471% | 87298154 | 0.02488
GEN-2023-121 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 395522.9365 | 0.6105% | 64782504 | 0.0324
GEN-2023-121 | 03 CENTRAL | 158865 | ERIS | Tie 69 kV Substation GEN-2023-121 Interconnection (Non-Shared NU) (GridLiance) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-121 (50MW/Solar), into Tie 69 kV Substation | 1550000 | 100% | 1550000 | 1
GEN-2023-121 | 03 CENTRAL | 158864 | ERIS | Tie 69 kV Substation GEN-2023-121 Interconnection (TOIF) (GridLiance) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-121 (50MW/Solar), into Tie 69 kV Substation | 250000 | 100% | 250000 | 1
GEN-2023-121 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 72877.5962 | 0.4114% | 17715993.12 | 0.05928
GEN-2023-121 | 03 CENTRAL | TBD | ERIS | Rebuild the OAK 2 to PRAIRIJ2 69kV line 1 | Current Study | Rebuild the existing OAK 2 to PRAIRIJ2 69 kV line 1 (1.97 miles) to a local TO rating of 108 MVA | 1790629.53 | 100% | 1790629.53 | 0.16426
GEN-2023-121 | 03 CENTRAL | TBD | ERIS | Rebuild the OAK 2 to STROTHR2 69kV line 1 | Current Study | Rebuild the existing OAK 2 to STROTHR2 69 kV line 1 (6.75 miles) to a local TO rating of 108 MVA | 6135405.75 | 100% | 6135405.75 | 0.32568
GEN-2023-121 | 03 CENTRAL | TBD | ERIS | Rebuild the STROTHR2 to WINFLD 2 69kV line 1 | Current Study | Rebuild the existing STROTHR2 to WINFLD 2 69 kV line 1 (2.3 miles) to a local TO rating of 108 MVA | 2090582.7 | 100% | 2090582.7 | 0.32568
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 19326.286 | 2.151% | 898410 | 0.00519
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 209018.4875 | 2.799% | 7467300 | 0.05703
GEN-2023-122 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 23.52% | 87298154 | 0.21393
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to G20-007-TAP 345kV line 2 | Current Study | Build a new LACYGNE7 to G20-007-TAP 345 kV line 2 (0.59 miles) to a standard rating of 1792 MVA | 332164.098 | 37.54% | 884761.05 | 0.17172
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 5693577.0852 | 8.789% | 64782504 | 0.09328
GEN-2023-122 | 03 CENTRAL | 158867 | ERIS | Wolf Creek - LaCygne 345 kV Line GEN-2023-122 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-122 (250MW/Solar), into Wolf Creek - LaCygne 345 kV Line | 32873895 | 100% | 32873895 | 1
GEN-2023-122 | 03 CENTRAL | 158866 | ERIS | Wolf Creek - LaCygne 345 kV Line GEN-2023-122 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-122 (250MW/Solar), into Wolf Creek - LaCygne 345 kV Line | 1325114 | 100% | 1325114 | 1
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 1090112.1594 | 3.028% | 36004208.24 | 0.04587
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 204915.1454 | 5.543% | 3696554.12 | 0.0794
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 418910.9464 | 2.365% | 17715993.12 | 0.06815
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 541738.9996 | 3.1% | 17475659.88 | 0.05586
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Rebuild the G20-076-TAP to G21-096-TAP 345kV line 1 | Current Study | Rebuild the existing G20-076-TAP to G21-096-TAP 345 kV line 1 (61.1 miles) to a standard rating of 1792 MVA | 27524943.8303 | 39.36% | 69925528.4 | 0.23194
GEN-2023-122 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 221504.4559 | 1.265% | 17509993.2 | 0.03734
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 34184.0667 | 3.805% | 898410 | 0.00765
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 312571.1501 | 4.186% | 7467300 | 0.07107
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 11991669.4733 | 18.51% | 64782504 | 0.16372
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 39624.0207 | 0.4772% | 8302968 | 0.00234
GEN-2023-149 | 03 CENTRAL | 158901 | ERIS | LaCygne - Stilwell 345 kV Line GEN-2023-149 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-149 (300MW/Battery/Storage), into LaCygne - Stilwell 345 kV Line | 28791748 | 100% | 28791748 | 1
GEN-2023-149 | 03 CENTRAL | 158900 | ERIS | LaCygne - Stilwell 345 kV Line GEN-2023-149 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-149 (300MW/Battery/Storage), into LaCygne - Stilwell 345 kV Line | 1325114 | 100% | 1325114 | 1
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 1183794.7871 | 3.288% | 36004208.24 | 0.04151
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 188914.2147 | 5.111% | 3696554.12 | 0.061
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 270783.0523 | 1.528% | 17715993.12 | 0.03671
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 804869.3709 | 4.606% | 17475659.88 | 0.06916
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 7021250.4644 | 24.74% | 28382211.2 | 0.18252
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 1299271.3428 | 7.42% | 17509993.2 | 0.18252
GEN-2023-149 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 5389.7803 | 0.463% | 1164086.56 | 0.00467
GEN-2023-157 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 16377.0725 | 1.823% | 898410 | 0.00733
GEN-2023-157 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 128907.5617 | 1.726% | 7467300 | 0.05862
GEN-2023-157 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 1859324.0263 | 2.87% | 64782504 | 0.05077
GEN-2023-157 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 92371.3815 | 1.113% | 8302968 | 0.01091
GEN-2023-157 | 03 CENTRAL | 158917 | ERIS | Bucyrus 161 kV Substation GEN-2023-157 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-157 (150MW/Battery/Storage), into Bucyrus 161 kV Substation | 17609254 | 100% | 17609254 | 1
GEN-2023-157 | 03 CENTRAL | 158916 | ERIS | Bucyrus 161 kV Substation GEN-2023-157 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-157 (150MW/Battery/Storage), into Bucyrus 161 kV Substation | 884672 | 100% | 884672 | 1
GEN-2023-157 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 79049.7595 | 2.138% | 3696554.12 | 0.05105
GEN-2023-157 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 338601.422 | 1.938% | 17475659.88 | 0.05819
GEN-2023-157 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 373366.1074 | 2.132% | 17509993.2 | 0.1049
GEN-2023-157 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 12591.5424 | 1.082% | 1164086.56 | 0.02182
GEN-2023-163 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 10903.1533 | 1.214% | 898410 | 0.00488
GEN-2023-163 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 92821.361 | 1.243% | 7467300 | 0.04221
GEN-2023-163 | 03 CENTRAL | 158927 | ERIS | Midway - Avenue City 161 kV GEN-2023-163 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-163 (150MW/Solar), into Midway - Avenue City 161 kV | 13604270 | 100% | 13604270 | 1
GEN-2023-163 | 03 CENTRAL | 158926 | ERIS | Midway - Avenue City 161 kV GEN-2023-163 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-163 (150MW/Solar), into Midway - Avenue City 161 kV | 884672 | 100% | 884672 | 1
GEN-2023-163 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 61149.3634 | 1.654% | 3696554.12 | 0.03949
GEN-2023-163 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 240436.686 | 1.376% | 17475659.88 | 0.04132
GEN-2023-163 | 03 CENTRAL | TBD | ERIS | Rebuild the MARYVLE5 to CLRNDA 5 161kV line 1 | Current Study | Rebuild the existing MARYVLE5 to CLRNDA 5 161 kV line 1 (29.3 miles) to a standard rating of 557 MVA | 28661963.2 | 100% | 28661963.2 | 0.17933
GEN-2023-163 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 251817.4652 | 1.438% | 17509993.2 | 0.07075
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 10780.2694 | 1.2% | 898410 | 0.00579
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 91150.0927 | 1.221% | 7467300 | 0.04974
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 902899.9157 | 10.87% | 8302968 | 0.12797
GEN-2023-169 | 03 CENTRAL | 158937 | ERIS | Missouri City - Liberty South 161 kV Line GEN-2023-169 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-169 (125MW/Battery/Storage), into Missouri City - Liberty South 161 kV Line | 14364525 | 100% | 14364525 | 1
GEN-2023-169 | 03 CENTRAL | 158936 | ERIS | Missouri City - Liberty South 161 kV Line GEN-2023-169 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-169 (125MW/Battery/Storage), into Missouri City - Liberty South 161 kV Line | 884672 | 100% | 884672 | 1
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MOCITYB2 to G23-169-TAP 161kV line 1 | Current Study | Rebuild the existing 5MOCITYB2 to G23-169-TAP 161 kV line 1 (0.35 miles) to a standard rating of 557 MVA | 202478.8849 | 59.14% | 342378.4 | 0.70504
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 59074.404 | 1.598% | 3696554.12 | 0.04578
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Rebuild the BLUMILS5 to BLUVLY-161 161kV line 1 | Current Study | Rebuild the existing BLUMILS5 to BLUVLY-161 161 kV line 1 (4.7 miles) to a standard rating of 557 MVA | 477060.6984 | 10.38% | 4597652.8 | 0.09696
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 236392.5549 | 1.353% | 17475659.88 | 0.04875
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161kV line 1 | Current Study | Rebuild the existing LBRTYST5 to BRMGHAM5 161 kV line 1 (4.03 miles) to a standard rating of 557 MVA | 611489.3729 | 15.51% | 3942242.72 | 0.28561
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 265609.5879 | 1.517% | 17509993.2 | 0.08955
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 123078.1918 | 10.57% | 1164086.56 | 0.25594
GEN-2023-169 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYPL to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing SIBLEYPL to ECKLES-161 161 kV line 1 (3.09 miles) to a standard rating of 557 MVA | 473936.0056 | 15.68% | 3022712.16 | 0.40843
GEN-2023-169 | 03 CENTRAL | TBD | NRIS | Rebuild the LEVEE5 to NEASTN 161kV line 1 | Current Study | Rebuild the LEVEE5 to NEASTN 161kV line CKT1 (5.19 miles) to a standard rating of 557 MVA | 911405.4305 | 17.95% | 5076982.56 | 0.03932
GEN-2023-170 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 11819.1969 | 1.316% | 898410 | 0.00529
GEN-2023-170 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 87257.7968 | 1.169% | 7467300 | 0.03968
GEN-2023-170 | 03 CENTRAL | 158939 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | 4766925 | 100% | 4766925 | 1
GEN-2023-170 | 03 CENTRAL | 158938 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | 884672 | 100% | 884672 | 1
GEN-2023-170 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 59538.9472 | 1.611% | 3696554.12 | 0.03845
GEN-2023-170 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 224842.051 | 1.287% | 17475659.88 | 0.03864
GEN-2023-170 | 03 CENTRAL | TBD | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161kV line 1 | Current Study | Rebuild the existing LBRTYST5 to BRMGHAM5 161 kV line 1 (4.03 miles) to a standard rating of 557 MVA | 133264.0472 | 3.38% | 3942242.72 | 0.05187
GEN-2023-170 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 165719.0273 | 0.9464% | 17509993.2 | 0.04656
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 13092.721 | 1.457% | 898410 | 0.00586
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 111711.0906 | 1.496% | 7467300 | 0.0508
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Build a new Sibley 345/161 kV transformer 2 | Current Study | Build a new Sibley 345/161 kV transformer 2 | 686647.025 | 8.27% | 8302968 | 0.0811
GEN-2023-171 | 03 CENTRAL | 158941 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (Non-Shared NU) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation | 2500000 | 100% | 2500000 | 1
GEN-2023-171 | 03 CENTRAL | 158940 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (TOIF) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation. | 400000 | 100% | 400000 | 1
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MOCITYB1 to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing 5MOCITYB1 to ECKLES-161 161 kV line 1 (6.07 miles) to a standard rating of 557 MVA | 506753.2906 | 8.534% | 5937819.68 | 0.05837
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 71988.7036 | 1.947% | 3696554.12 | 0.04649
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 289955.471 | 1.659% | 17475659.88 | 0.04983
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161kV line 1 | Current Study | Rebuild the existing LBRTYST5 to BRMGHAM5 161 kV line 1 (4.03 miles) to a standard rating of 557 MVA | 17547.589 | 0.4451% | 3942242.72 | 0.00683
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 334143.0902 | 1.908% | 17509993.2 | 0.09388
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | Current Study | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | 93599.8251 | 8.041% | 1164086.56 | 0.1622
GEN-2023-171 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYPL to ECKLES-161 161kV line 1 | Current Study | Rebuild the existing SIBLEYPL to ECKLES-161 161 kV line 1 (3.09 miles) to a standard rating of 557 MVA | 330862.8679 | 10.95% | 3022712.16 | 0.23761
GEN-2023-172 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 8854.7899 | 0.1186% | 7467300 | 0.00302
GEN-2023-172 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.5515% | 87298154 | 0.00627
GEN-2023-172 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 94354.6493 | 8.389% | 1124696.25 | 0.21118
GEN-2023-172 | 03 CENTRAL | 158942 | ERIS | Holcomb 345 kV GEN-2023-172 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172 (200MW/Wind), into Holcomb 345 kV | 1250000 | 100% | 1250000 | 1
GEN-2023-172 | 03 CENTRAL | 158666 | ERIS | Holcomb 345 kV Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172/173 (200/100MW/Wind), into Holcomb 345 kV | 10666666.6667 | 66.67% | 16000000 | 1
GEN-2023-172 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 21324.2074 | 2.484% | 858333 | 0.21118
GEN-2023-172 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1333534.7981 | 2.011% | 66320529.8 | 0.12592
GEN-2023-172 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 546874.9492 | 1.249% | 43786427.44 | 0.03771
GEN-2023-173 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 4427.3949 | 0.05929% | 7467300 | 0.00302
GEN-2023-173 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 0.2757% | 87298154 | 0.00627
GEN-2023-173 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 47177.3247 | 4.195% | 1124696.25 | 0.21118
GEN-2023-173 | 03 CENTRAL | 158666 | ERIS | Holcomb 345 kV Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172/173 (200/100MW/Wind), into Holcomb 345 kV | 5333333.3333 | 33.33% | 16000000 | 1
GEN-2023-173 | 03 CENTRAL | 158943 | ERIS | Holcomb 345 kV GEN-2023-173 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-173 (100MW/Wind), into Holcomb 345 kV | 1250000 | 100% | 1250000 | 1
GEN-2023-173 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 10662.1037 | 1.242% | 858333 | 0.21118
GEN-2023-173 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 666767.399 | 1.005% | 66320529.8 | 0.12592
GEN-2023-173 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 273437.4746 | 0.6245% | 43786427.44 | 0.03771
GEN-2023-175 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 6127.9837 | 0.08206% | 7467300 | 0.00209
GEN-2023-175 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 1.546% | 87298154 | 0.01758
GEN-2023-175 | 03 CENTRAL | TBD | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | Current Study | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | 47297.9599 | 4.205% | 1124696.25 | 0.10586
GEN-2023-175 | 03 CENTRAL | 158947 | ERIS | Hickock 115 kV Substation GEN-2023-175 Interconnection (Non-Shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-175 (200MW/Battery/Storage), into Hickock 115 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-175 | 03 CENTRAL | 158946 | ERIS | Hickock 115 kV Substation GEN-2023-175 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-175 (200MW/Battery/Storage), into Hickock 115 kV Substation | 2500000 | 100% | 2500000 | 1
GEN-2023-175 | 03 CENTRAL | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 10689.3673 | 1.245% | 858333 | 0.10586
GEN-2023-175 | 03 CENTRAL | TBD | ERIS | Rebuild the HICKOCK3 to PIONEER3 115kV line 1 | Current Study | Rebuild the existing HICKOCK3 to PIONEER3 115 kV line 1 (12.96 miles) to a standard rating of 239 MVA | 9212486.4 | 100% | 9212486.4 | 0.50251
GEN-2023-175 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1359269.3086 | 2.05% | 66320529.8 | 0.12835
GEN-2023-175 | 03 CENTRAL | TBD | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | Current Study | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | 871432.3972 | 1.99% | 43786427.44 | 0.06009
GEN-2023-186 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 44831.0387 | 0.6004% | 7467300 | 0.01529
GEN-2023-186 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 3.225% | 87298154 | 0.03667
GEN-2023-186 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 1541562.8523 | 2.38% | 64782504 | 0.03157
GEN-2023-186 | 03 CENTRAL | 158964 | ERIS | Murray Gill 138 kV Substation GEN-2023-186 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-186 (200MW/Hybrid), into Murray Gill 138 kV Substation | 846415 | 100% | 846415 | 1
GEN-2023-186 | 03 CENTRAL | 158963 | ERIS | Murray Gill 138 kV Substation GEN-2023-186 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-186 (200MW/Hybrid), into Murray Gill 138 kV Substation | 850069 | 100% | 850069 | 1
GEN-2023-186 | 03 CENTRAL | TBD | ERIS | Rebuild the ELPASO 4 to ROSEHIL4 138kV line 1 | Current Study | Rebuild the existing ELPASO 4 to ROSEHIL4 138 kV line 1 (8.37 miles) to a standard rating of 478 MVA | 1690843.3103 | 20.95% | 8070010.83 | 0.10001
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 14891.1454 | 1.657% | 898410 | 0.01351
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 52008.1098 | 0.6965% | 7467300 | 0.04794
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Build a new G20-079-TAP to STL439 5 161kV line 1 | Current Study | Build a new G20-079-TAP to STL439 5 161 kV line 1 (12.24 miles) to a standard rating of 557 MVA | 625731.3703 | 4.889% | 12799894.32 | 0.04036
GEN-2023-191 | 03 CENTRAL | 158970 | ERIS | Hockersville 138 kV Substation GEN-2023-191 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-191 (74MW/Battery/Storage), into Hockersville 138 kV Substation | 9295029 | 100% | 9295029 | 1
GEN-2023-191 | 03 CENTRAL | 158969 | ERIS | Hockersville 138 kV Substation GEN-2023-191 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-191 (74MW/Battery/Storage), into Hockersville 138 kV Substation | 1927444.2 | 100% | 1927444.2 | 1
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the AUR124 5 to MON383 5 161kV line 1 | Current Study | Rebuild the existing AUR124 5 to MON383 5 161 kV line 1 (11.51 miles) to a standard rating of 557 MVA | 602876.0975 | 5.354% | 11259358.24 | 0.06252
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 137116.0992 | 0.774% | 17715993.12 | 0.07536
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 137619.1626 | 0.7875% | 17475659.88 | 0.04794
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the FLINTCR5 to DEC392 5 161kV line 1 | Current Study | Rebuild the existing FLINTCR5 to DEC392 5 161 kV line 1 (6.03 miles) to a standard rating of 557 MVA | 177297.8523 | 3.006% | 5898690.72 | 0.07558
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the LLAN ET4 to CATOOSA4 138kV line 1 | Current Study | Rebuild the existing LLAN ET4 to CATOOSA4 138 kV line 1 (2.84 miles) to a standard rating of 286 MVA | 287387.7438 | 10.5% | 2738211.56 | 0.035
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the LLAN ET4 to E41ST_W4 138kV line 1 | Current Study | Rebuild the existing LLAN ET4 to E41ST_W4 138 kV line 1 (3.46 miles) to a standard rating of 286 MVA | 350127.3217 | 10.5% | 3335990.14 | 0.035
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the MAYO--N4 to E41ST_W4 138kV line 1 | Current Study | Rebuild the existing MAYO--N4 to E41ST_W4 138 kV line 1 (2.6 miles) to a standard rating of 286 MVA | 263101.4556 | 10.5% | 2506813.4 | 0.035
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the MINGO-N4 to MAYO--N4 138kV line 1 | Current Study | Rebuild the existing MINGO-N4 to MAYO--N4 138 kV line 1 (1.75 miles) to a standard rating of 286 MVA | 177087.5182 | 10.5% | 1687278.25 | 0.035
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the ORO110 5 to RIV4525 161kV line 1 | Current Study | Rebuild the existing ORO110 5 to RIV4525 161 kV line 1 (11.9 miles) to a standard rating of 557 MVA | 1672306.6888 | 14.37% | 11640865.6 | 0.15599
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYRD5 to NOL435 5 161kV line 1 | Current Study | Rebuild the existing SIBLEYRD5 to NOL435 5 161 kV line 1 (3.93 miles) to a standard rating of 557 MVA | 111930.2628 | 2.911% | 3844420.32 | 0.06884
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 1 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 1 (43.1 miles) to a standard rating of 557 MVA | 1745150.189 | 4.139% | 42161454.4 | 0.05003
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 2 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 2 (43.1 miles) to a standard rating of 557 MVA | 1645232.5731 | 3.902% | 42161454.4 | 0.05003
GEN-2023-191 | 03 CENTRAL | TBD | ERIS | Replace Neosho TX-4 161/138 kV transformer 1 | Current Study | Replace existing Neosho TX-4 161/138 kV transformer 1 | 695763.8074 | 19.29% | 3606166 | 0.04982
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 68870.8402 | 7.666% | 898410 | 0.02055
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 228556.9332 | 3.061% | 7467300 | 0.06929
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Build a new G20-079-TAP to STL439 5 161kV line 1 | Current Study | Build a new G20-079-TAP to STL439 5 161 kV line 1 (12.24 miles) to a standard rating of 557 MVA | 8401723.3341 | 65.64% | 12799894.32 | 0.17823
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 1741399.5952 | 2.688% | 64782504 | 0.0317
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Build a new RIV4525 to G20-079-TAP 161kV line 2 | Current Study | Build a new RIV4525 to G20-079-TAP 161 kV line 2 (5.47 miles) to a standard rating of 557 MVA | 4041101.7505 | 70.65% | 5720214.21 | 0.23938
GEN-2023-194 | 03 CENTRAL | 158974 | ERIS | Riverton - Neosho 161 kV Line Tap GEN-2023-194 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-194 (225MW/Solar), into Riverton - Neosho 161 kV Line Tap | 1864449 | 100% | 1864449 | 1
GEN-2023-194 | 03 CENTRAL | 158973 | ERIS | Riverton - Neosho 161 kV Line Tap GEN-2023-194 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-194 (225MW/Solar), into Riverton - Neosho 161 kV Line Tap | 0 | 100% | 0 | 1
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 1134458.1217 | 3.151% | 36004208.24 | 0.05304
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Rebuild the AUR124 5 to MON383 5 161kV line 1 | Current Study | Rebuild the existing AUR124 5 to MON383 5 161 kV line 1 (11.51 miles) to a standard rating of 557 MVA | 2052967.1539 | 18.23% | 11259358.24 | 0.07002
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 435993.1698 | 2.461% | 17715993.12 | 0.07881
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 604786.7124 | 3.461% | 17475659.88 | 0.06929
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Rebuild the FLINTCR5 to DEC392 5 161kV line 1 | Current Study | Rebuild the existing FLINTCR5 to DEC392 5 161 kV line 1 (6.03 miles) to a standard rating of 557 MVA | 601206.1844 | 10.19% | 5898690.72 | 0.08429
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Rebuild the ORO110 5 to RIV4525 161kV line 1 | Current Study | Rebuild the existing ORO110 5 to RIV4525 161 kV line 1 (11.9 miles) to a standard rating of 557 MVA | 5031258.1472 | 43.22% | 11640865.6 | 0.15435
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYRD5 to NOL435 5 161kV line 1 | Current Study | Rebuild the existing SIBLEYRD5 to NOL435 5 161 kV line 1 (3.93 miles) to a standard rating of 557 MVA | 378642.6489 | 9.849% | 3844420.32 | 0.07659
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 1 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 1 (43.1 miles) to a standard rating of 557 MVA | 5894834.9066 | 13.98% | 42161454.4 | 0.05558
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 2 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 2 (43.1 miles) to a standard rating of 557 MVA | 5557329.3708 | 13.18% | 42161454.4 | 0.05558
GEN-2023-194 | 03 CENTRAL | TBD | ERIS | Replace Neosho TX-4 161/138 kV transformer 1 | Current Study | Replace existing Neosho TX-4 161/138 kV transformer 1 | 2910402.1926 | 80.71% | 3606166 | 0.06854
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 33603.1609 | 3.74% | 898410 | 0.00752
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 351714.0126 | 4.71% | 7467300 | 0.07997
GEN-2023-200 | 03 CENTRAL | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | 0 | 1.096% | 87298154 | 0.00831
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Build a new G20-079-TAP to STL439 5 161kV line 1 | Current Study | Build a new G20-079-TAP to STL439 5 161 kV line 1 (12.24 miles) to a standard rating of 557 MVA | 745437.085 | 5.824% | 12799894.32 | 0.01186
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 3575087.8756 | 5.519% | 64782504 | 0.04881
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Build a new RIV4525 to G20-079-TAP 161kV line 2 | Current Study | Build a new RIV4525 to G20-079-TAP 161 kV line 2 (5.47 miles) to a standard rating of 557 MVA | 307469.0167 | 5.375% | 5720214.21 | 0.01366
GEN-2023-200 | 03 CENTRAL | 158984 | ERIS | Caney River 345 kV Substation GEN-2023-200 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-200 (300MW/Solar), into Caney River 345 kV Substation | 1635518 | 100% | 1635518 | 1
GEN-2023-200 | 03 CENTRAL | 158983 | ERIS | Caney River 345 kV Substation GEN-2023-200 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-200 (300MW/Solar), into Caney River 345 kV Substation | 1325114 | 100% | 1325114 | 1
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 3434459.316 | 9.539% | 36004208.24 | 0.12043
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 161630.0469 | 4.372% | 3696554.12 | 0.05219
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 2573729.8447 | 14.53% | 17715993.12 | 0.34892
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 893200.1766 | 5.111% | 17475659.88 | 0.07675
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Rebuild the ELPASO 4 to ROSEHIL4 138kV line 1 | Current Study | Rebuild the existing ELPASO 4 to ROSEHIL4 138 kV line 1 (8.37 miles) to a standard rating of 478 MVA | 1025562.9958 | 12.71% | 8070010.83 | 0.04044
GEN-2023-200 | 03 CENTRAL | TBD | ERIS | Rebuild the ROSEHIL7 to LATHAMS7 345kV line 1 | Current Study | Rebuild the existing ROSEHIL7 to LATHAMS7 345 kV line 1 (30.44 miles) to a standard rating of 1792 MVA | 34836875.36 | 100% | 34836875.36 | 0.64064
GEN-2023-219 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 3407.2354 | 0.3793% | 898410 | 0.00183
GEN-2023-219 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 73594.4455 | 0.9856% | 7467300 | 0.04016
GEN-2023-219 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 108951.92 | 0.1682% | 64782504 | 0.00357
GEN-2023-219 | 03 CENTRAL | TBD | ERIS | Build a new LANG 3 to G22-007-TAP 115kV line 2 | Current Study | Build a new LANG 3 to G22-007-TAP 115 kV line 2 (0.41 miles) to a standard rating of 239 MVA | 368494.47 | 100% | 368494.47 | 0.35461
GEN-2023-219 | 03 CENTRAL | 159017 | ERIS | Reading - Osage Jct 115 kV Line GEN-2023-219 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-219 (125MW/Solar), into Reading - Osage Jct 115 kV Line | 12378356 | 100% | 12378356 | 1
GEN-2023-219 | 03 CENTRAL | 159016 | ERIS | Reading - Osage Jct 115 kV Line GEN-2023-219 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-219 (125MW/Solar), into Reading - Osage Jct 115 kV Line | 749584 | 100% | 749584 | 1
GEN-2023-219 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 47886.6565 | 1.295% | 3696554.12 | 0.03711
GEN-2023-219 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 194738.9744 | 1.114% | 17475659.88 | 0.04016
GEN-2023-219 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 171734.1724 | 0.9808% | 17509993.2 | 0.0579
GEN-2023-220 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 12176.6773 | 1.355% | 898410 | 0.00327
GEN-2023-220 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 148654.9159 | 1.991% | 7467300 | 0.04056
GEN-2023-220 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 610.3749 | 0.0009422% | 64782504 | 1e-05
GEN-2023-220 | 03 CENTRAL | 159019 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | 27848113 | 100% | 27848113 | 1
GEN-2023-220 | 03 CENTRAL | 159018 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | 1325114 | 100% | 1325114 | 1
GEN-2023-220 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 98947.6911 | 2.677% | 3696554.12 | 0.03834
GEN-2023-220 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 393357.2113 | 2.251% | 17475659.88 | 0.04056
GEN-2023-220 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 399526.6497 | 2.282% | 17509993.2 | 0.06735
GEN-2023-221 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 12027.7272 | 1.339% | 898410 | 0.00323
GEN-2023-221 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 147848.6023 | 1.98% | 7467300 | 0.04034
GEN-2023-221 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 5493.3741 | 0.00848% | 64782504 | 9e-05
GEN-2023-221 | 03 CENTRAL | 159021 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | 27848113 | 100% | 27848113 | 1
GEN-2023-221 | 03 CENTRAL | 159020 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | 1325114 | 100% | 1325114 | 1
GEN-2023-221 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 98483.148 | 2.664% | 3696554.12 | 0.03816
GEN-2023-221 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 391223.617 | 2.239% | 17475659.88 | 0.04034
GEN-2023-221 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 394899.6151 | 2.255% | 17509993.2 | 0.06657
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 35360.7731 | 3.936% | 898410 | 0.01187
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 136750.7944 | 1.831% | 7467300 | 0.04664
GEN-2023-226 | 03 CENTRAL | 159027 | ERIS | La Russell 161 kV Substation GEN-2023-226 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-226 (200MW/Battery/Storage), into La Russell 161 kV Substation | 3203739.01 | 100% | 3203739.01 | 1
GEN-2023-226 | 03 CENTRAL | 159026 | ERIS | La Russell 161 kV Substation GEN-2023-226 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-226 (200MW/Battery/Storage), into La Russell 161 kV Substation | 874473.75 | 100% | 874473.75 | 1
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MANSFDMN to G23-085-TAP 161kV line 1 | Current Study | Rebuild the existing 5MANSFDMN to G23-085-TAP 161 kV line 1 (0.8 miles) to a standard rating of 557 MVA | 55109.7128 | 7.042% | 782579.2 | 0.03885
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the AUR124 5 to G19-035-TAP 161kV line 1 | Current Study | Rebuild the existing AUR124 5 to G19-035-TAP 161 kV line 1 (8.3 miles) to a standard rating of 557 MVA | 4251273.0512 | 52.36% | 8119259.2 | 0.07082
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the AUR124 5 to MON383 5 161kV line 1 | Current Study | Rebuild the existing AUR124 5 to MON383 5 161 kV line 1 (11.51 miles) to a standard rating of 557 MVA | 3783938.5709 | 33.61% | 11259358.24 | 0.14519
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 324408.5709 | 1.831% | 17715993.12 | 0.06597
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 361857.6003 | 2.071% | 17475659.88 | 0.04664
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the FLINTCR5 to DEC392 5 161kV line 1 | Current Study | Rebuild the existing FLINTCR5 to DEC392 5 161 kV line 1 (6.03 miles) to a standard rating of 557 MVA | 466439.8201 | 7.908% | 5898690.72 | 0.07357
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the LAR382 5 to MON383 5 161kV line 1 | Current Study | Rebuild the existing LAR382 5 to MON383 5 161 kV line 1 (15.56 miles) to a standard rating of 557 MVA | 9915948.3004 | 65.15% | 15221165.44 | 0.24951
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the NEO SPA5 to CARTHAG5 161kV line 1 | Current Study | Rebuild the existing NEO SPA5 to CARTHAG5 161 kV line 1 (22.9 miles) to a standard rating of 557 MVA | 5756808.9672 | 25.7% | 22401329.6 | 0.11674
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the RDS295 5 to G19-035-TAP 161kV line 1 | Current Study | Rebuild the existing RDS295 5 to G19-035-TAP 161 kV line 1 (15.41 miles) to a standard rating of 557 MVA | 7893026.2313 | 52.36% | 15074431.84 | 0.07082
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the SIBLEYRD5 to NOL435 5 161kV line 1 | Current Study | Rebuild the existing SIBLEYRD5 to NOL435 5 161 kV line 1 (3.93 miles) to a standard rating of 557 MVA | 295175.4853 | 7.678% | 3844420.32 | 0.06717
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 1 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 1 (43.1 miles) to a standard rating of 557 MVA | 16499221.2548 | 39.13% | 42161454.4 | 0.17501
GEN-2023-226 | 03 CENTRAL | TBD | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 2 | Current Study | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 2 (43.1 miles) to a standard rating of 557 MVA | 15554567.4012 | 36.89% | 42161454.4 | 0.17501
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | Current Study | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | 79143.1894 | 8.809% | 898410 | 0.01714
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | Current Study | Build a new 300 MVAR cap bank at DELWARE7 345 kV | 727148.3066 | 9.738% | 7467300 | 0.16
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Build a new G20-079-TAP to STL439 5 161kV line 1 | Current Study | Build a new G20-079-TAP to STL439 5 161 kV line 1 (12.24 miles) to a standard rating of 557 MVA | 1221025.1072 | 9.539% | 12799894.32 | 0.0188
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | Current Study | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | 6294845.1936 | 9.717% | 64782504 | 0.08317
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Build a new RIV4525 to G20-079-TAP 161kV line 2 | Current Study | Build a new RIV4525 to G20-079-TAP 161 kV line 2 (5.47 miles) to a standard rating of 557 MVA | 554727.2267 | 9.698% | 5720214.21 | 0.02385
GEN-2023-231 | 03 CENTRAL | 159037 | ERIS | Neosho - LaCynge 345 kV Line GEN-2023-231 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-231 (310MW/Hybrid), into Neosho - LaCynge 345 kV Line | 77041652 | 100% | 77041652 | 1
GEN-2023-231 | 03 CENTRAL | 159036 | ERIS | Neosho - LaCynge 345 kV Line GEN-2023-231 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-231 (310MW/Hybrid), into Neosho - LaCynge 345 kV Line | 1325114 | 100% | 1325114 | 1
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | Current Study | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | 7437659.163 | 20.66% | 36004208.24 | 0.25239
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | Current Study | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | 287472.7219 | 7.777% | 3696554.12 | 0.08983
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | 776087.3893 | 4.381% | 17715993.12 | 0.10182
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | Current Study | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | 1837649.2893 | 10.52% | 17475659.88 | 0.15281
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 3493752.837 | 36.56% | 9556107.4 | 0.30969
GEN-2023-231 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 5077781.4338 | 29% | 17509993.2 | 0.69031
GEN-2023-003 | 04 SOUTHEAST | TBD | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | Current Study | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | 651400.6736 | 18.06% | 3606166 | 0.02542
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 1571.3512 | 2.356% | 66701.12 | 0.01251
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 1571.3512 | 2.356% | 66701.12 | 0.01251
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 87411.0246 | 2.356% | 3710249.8 | 0.01706
GEN-2023-003 | 04 SOUTHEAST | 158682 | ERIS | Greasy Creek 138kV Switchyard GEN-2023-003 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-003 (200.6MW/Wind), into Greasy Creek 138kV Switchyard | 89700000 | 100% | 89700000 | 1
GEN-2023-003 | 04 SOUTHEAST | 158684 | ERIS | Greasy Creek 138kV Switchyard GEN-2023-003 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-003 (200.6MW/Wind), into Greasy Creek 138kV Switchyard | 600000 | 100% | 600000 | 1
GEN-2023-003 | 04 SOUTHEAST | 158681 | ERIS | Greasy Creek 138kV Switchyard GEN-2023-003 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-003 (200.6MW/Wind), into Greasy Creek 138kV Switchyard | 1200000 | 100% | 1200000 | 1
GEN-2023-003 | 04 SOUTHEAST | 158683 | ERIS | Greasy Creek 138kV Switchyard GEN-2023-003 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-003 (200.6MW/Wind), into Greasy Creek 138kV Switchyard | 299999 | 100% | 299999 | 1
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 4WOODY to PHAROAH4 138kV line 1 | Current Study | Rebuild the 4WOODY to PHAROAH4 138kV line CKT1 (13.36 miles) to a standard rating of 286 MVA | 2332237.5354 | 18.11% | 12881164.24 | 0.09717
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ACOPA2 to ACOPT2 69kV line 1 | Current Study | Rebuild the ACOPA2 to ACOPT2 69kV line CKT1 (3.28 miles) to a standard rating of 143 MVA | 342792.1263 | 11.5% | 2981352.72 | 0.0269
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ALLEN4 to TUPELO4 138kV line 1 | Current Study | Rebuild the ALLEN4 to TUPELO4 138kV line CKT1 (19.4 miles) to a standard rating of 286 MVA | 18704684.6 | 100% | 18704684.6 | 0.30888
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AOCPT2 to LULA2 69kV line 1 | Current Study | Rebuild the AOCPT2 to LULA2 69kV line CKT1 (9.27 miles) to a standard rating of 143 MVA | 968805.796 | 11.5% | 8425957.23 | 0.0269
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 4724.1857 | 5.444% | 86774.31 | 0.02658
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 14172.5571 | 5.444% | 260322.93 | 0.02658
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 554197.7608 | 4.875% | 11367434.61 | 0.02731
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the EXPLOR4 to ALLEN4 138kV line 1 | Current Study | Rebuild the EXPLOR4 to ALLEN4 138kV line CKT1 (14.8 miles) to a standard rating of 286 MVA | 14269553.2 | 100% | 14269553.2 | 0.30888
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 1035306.6374 | 6.615% | 15651584 | 0.06379
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GREASYC4 to EXPLOR4 138kV line 1 | Current Study | Rebuild the GREASYC4 to EXPLOR4 138kV line CKT1 (6.91 miles) to a standard rating of 286 MVA | 6662338.69 | 100% | 6662338.69 | 0.30888
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to LATTAJT4 138kV line 1 | Current Study | Rebuild the LASALLE4 to LATTAJT4 138kV line CKT1 (7.1 miles) to a standard rating of 286 MVA | 868431.535 | 12.69% | 6845528.9 | 0.05696
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | Current Study | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | 734740.5546 | 12.1% | 6074201.7 | 0.05696
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1 | Current Study | Rebuild the LATTAJT4 to OILCRTP4 138kV line CKT1 (4.55 miles) to a standard rating of 286 MVA | 556530.0682 | 12.69% | 4386923.45 | 0.05696
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 299426.6104 | 4.875% | 6141692.83 | 0.02731
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | 546925.0265 | 14.4% | 3798786.46 | 0.10838
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the OKMULGE4 to KELCO4 138kV line 1 | Current Study | Rebuild the OKMULGE4 to KELCO4 138kV line CKT1 (2.24 miles) to a standard rating of 286 MVA | 369878.1974 | 17.13% | 2159716.16 | 0.07204
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 1817.0998 | 2.356% | 77132.72 | 0.01251
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 101074.1371 | 2.356% | 4290507.55 | 0.02047
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 523675.913 | 3.833% | 13662133.03 | 0.03753
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 147103.0027 | 12.93% | 1137707.62 | 0.15006
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VANBUR5 to VBI5 161kV line Z1 | Current Study | Rebuild the VANBUR5 to VBI5 161kV line CKTZ1 (0.22 miles) to a standard rating of 557 MVA | 6017.2144 | 2.796% | 215209.28 | 0.03286
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 9167649.7352 | 58.41% | 15696508.52 | 0.69112
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 399607.5218 | 15.82% | 2526096.58 | 0.31862
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Upgrade the LULA4 138/69 kV transformer 1 | Current Study | Upgrade the LULA4 138/69 kV transformer 1 to a standard rating of 250 MVA | 359738.8724 | 11.5% | 3128743 | 0.0269
GEN-2023-003 | 04 SOUTHEAST | TBD | ERIS | Upgrade the WELEETK5 161/138 kV transformer 1 | Current Study | Upgrade the WELEETK5 161/138 kV transformer 1 to a standard rating of 200 MVA | 708699.323 | 19.65% | 3606166 | 0.07226
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 4065808.8199 | 48.97% | 8302968 | 0.34474
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 261298.3714 | 48.97% | 533608.96 | 0.34474
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 1704.7194 | 2.556% | 66701.12 | 0.01089
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 1704.7194 | 2.556% | 66701.12 | 0.01089
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 94888.826 | 2.557% | 3710249.8 | 0.01486
GEN-2023-009 | 04 SOUTHEAST | 158691 | ERIS | Hugo 138 kV Substation GEN-2023-009 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-009 (250MW/Battery/Storage), into Hugo 138 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-009 | 04 SOUTHEAST | 158690 | ERIS | Hugo 138 kV Substation GEN-2023-009 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-009 (250MW/Battery/Storage), into Hugo 138 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 5519.8732 | 6.361% | 86774.31 | 0.02492
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 16559.6196 | 6.361% | 260322.93 | 0.02492
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 647428.9452 | 5.695% | 11367434.61 | 0.0256
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 349798.3359 | 5.695% | 6141692.83 | 0.0256
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 1971.3259 | 2.556% | 77132.72 | 0.01089
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 109719.1976 | 2.557% | 4290507.55 | 0.01783
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 568296.7364 | 4.16% | 13662133.03 | 0.03268
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to ALLENGT4 138kV line 1 | Current Study | Rebuild the TUPELO4 to ALLENGT4 138kV line CKT1 (0.37 miles) to a standard rating of 286 MVA | 20423.7576 | 5.725% | 356738.83 | 0.04087
GEN-2023-009 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 51226.011 | 4.503% | 1137707.62 | 0.04193
GEN-2023-016 | 04 SOUTHEAST | TBD | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | Current Study | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | 271686.7008 | 7.534% | 3606166 | 0.01636
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 342700.7204 | 4.127% | 8302968 | 0.05588
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 22024.4345 | 4.127% | 533608.96 | 0.05588
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 5269.8842 | 7.901% | 66701.12 | 0.06474
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 5269.8842 | 7.901% | 66701.12 | 0.06474
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 293131.1233 | 7.901% | 3710249.8 | 0.08828
GEN-2023-016 | 04 SOUTHEAST | 158703 | ERIS | Tupelo-Brown 138 kV Line GEN-2023-016 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-016 (130MW/Solar), into Tupelo-Brown 138 kV Line | 8600000 | 100% | 8600000 | 1
GEN-2023-016 | 04 SOUTHEAST | 158702 | ERIS | Tupelo-Brown 138 kV Line GEN-2023-016 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-016 (130MW/Solar), into Tupelo-Brown 138 kV Line | 800000 | 100% | 800000 | 1
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ACOPA2 to ACOPT2 69kV line 1 | Current Study | Rebuild the ACOPA2 to ACOPT2 69kV line CKT1 (3.28 miles) to a standard rating of 143 MVA | 416631.5478 | 13.97% | 2981352.72 | 0.05045
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AOCPT2 to LULA2 69kV line 1 | Current Study | Rebuild the AOCPT2 to LULA2 69kV line CKT1 (9.27 miles) to a standard rating of 143 MVA | 1177492.2098 | 13.97% | 8425957.23 | 0.05045
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 16081.7032 | 18.53% | 86774.31 | 0.13962
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to BODLE4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to BODLE4 138kV line CKT1 (7.56 miles) to a standard rating of 286 MVA | 268345.4253 | 3.681% | 7289042.04 | 0.00382
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 48245.1095 | 18.53% | 260322.93 | 0.13962
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 1886365.1604 | 16.59% | 11367434.61 | 0.14344
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line CKT1 (0.17 miles) to a standard rating of 286 MVA | 24973.0073 | 15.24% | 163907.03 | 0.02931
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | 198562.8553 | 9.235% | 2150074.57 | 0.0963
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 1505.0035 | 0.1753% | 858333 | 0.02293
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to CHIKSAW4 138kV line 1 | Current Study | Rebuild the FNDTION4 to CHIKSAW4 138kV line CKT1 (1.72 miles) to a standard rating of 286 MVA | 166509.8662 | 10.04% | 1658353.48 | 0.06236
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to SPRNDAL4 138kV line 1 | Current Study | Rebuild the FNDTION4 to SPRNDAL4 138kV line CKT1 (2.58 miles) to a standard rating of 286 MVA | 249764.7993 | 10.04% | 2487530.22 | 0.06236
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HLDTNTP4 to LOCO4 138kV line 1 | Current Study | Rebuild the HLDTNTP4 to LOCO4 138kV line CKT1 (12.85 miles) to a standard rating of 286 MVA | 317808.5947 | 2.565% | 12389443.15 | 0.02931
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | Current Study | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | 861856.0065 | 9.084% | 9487324.56 | 0.13862
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to LATTAJT4 138kV line 1 | Current Study | Rebuild the LASALLE4 to LATTAJT4 138kV line CKT1 (7.1 miles) to a standard rating of 286 MVA | 970361.9073 | 14.18% | 6845528.9 | 0.09821
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | Current Study | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | 820979.2219 | 13.52% | 6074201.7 | 0.09821
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1 | Current Study | Rebuild the LATTAJT4 to OILCRTP4 138kV line CKT1 (4.55 miles) to a standard rating of 286 MVA | 621851.6448 | 14.18% | 4386923.45 | 0.09821
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 1019181.1765 | 16.59% | 6141692.83 | 0.14344
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | 655863.9191 | 17.27% | 3798786.46 | 0.20055
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | Current Study | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | 315788.4288 | 6.191% | 5100401.11 | 0.04071
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PARKLN2 to ADAINDU2 69kV line 1 | Current Study | Rebuild the PARKLN2 to ADAINDU2 69kV line CKT1 (2.87 miles) to a standard rating of 143 MVA | 391762.4928 | 15.02% | 2608683.63 | 0.05045
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PAYNESW4 to PAOLI4 138kV line 1 | Current Study | Rebuild the PAYNESW4 to PAOLI4 138kV line CKT1 (12 miles) to a standard rating of 286 MVA | 702832.9639 | 6.075% | 11569908 | 0.05513
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | Current Study | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | 497262.3086 | 6.191% | 8031444.47 | 0.04071
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 6094.0581 | 7.901% | 77132.72 | 0.06474
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | 1078294.2502 | 9.235% | 11675965.49 | 0.0963
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 338964.0153 | 7.9% | 4290507.55 | 0.10593
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 1756176.0333 | 12.85% | 13662133.03 | 0.19421
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | Current Study | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | 111302.0489 | 9.235% | 1205198.75 | 0.0963
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 173236.0335 | 15.23% | 1137707.62 | 0.27269
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VALLYU2 to AOCPA2 69kV line 1 | Current Study | Rebuild the VALLYU2 to AOCPA2 69kV line CKT1 (1.62 miles) to a standard rating of 143 MVA | 221134.2294 | 15.02% | 1472497.38 | 0.05045
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 944745.1413 | 6.019% | 15696508.52 | 0.1099
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 34941.4151 | 1.383% | 2526096.58 | 0.04299
GEN-2023-016 | 04 SOUTHEAST | TBD | ERIS | Upgrade the LULA4 138/69 kV transformer 1 | Current Study | Upgrade the LULA4 138/69 kV transformer 1 to a standard rating of 250 MVA | 437228.7217 | 13.97% | 3128743 | 0.05045
GEN-2023-019 | 04 SOUTHEAST | 158707 | ERIS | Cherry Road 138 kV Substation GEN-2023-019 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-019 (200MW/Battery/Storage), into Cherry Road 138 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-019 | 04 SOUTHEAST | 158706 | ERIS | Cherry Road 138 kV Substation GEN-2023-019 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-019 (200MW/Battery/Storage), into Cherry Road 138 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-019 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ANADARK4 to CHERRYRD4 138kV line 1 | Current Study | Rebuild the ANADARK4 to CHERRYRD4 138kV line CKT1 (25.15 miles) to a standard rating of 478 MVA | 21589246.8075 | 89.03% | 24248598.85 | 0.64734
GEN-2023-019 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CACHEJ5 to G20-016-TAP 138kV 1 | Current Study | Rebuild the CACHEJ5 to G20-016-TAP 138kV CKT1 (3.94 miles) to a standard rating of 286 MVA | 3798786.46 | 100% | 3798786.46 | 0.27729
GEN-2023-019 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3197.9243 | 0.3726% | 858333 | 0.03167
GEN-2023-019 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MDCPRK4 to CACHEJ4 138kV line 1 | Current Study | Rebuild the MDCPRK4 to CACHEJ4 138kV line CKT1 (16.97 miles) to a standard rating of 478 MVA | 16361778.23 | 100% | 16361778.23 | 0.35266
GEN-2023-019 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MDCPRK4 to PARADSE4 138kV line 1 | Current Study | Rebuild the MDCPRK4 to PARADSE4 138kV line CKT1 (3.2 miles) to a standard rating of 478 MVA | 3085308.8 | 100% | 3085308.8 | 0.35266
GEN-2023-019 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PARADSE4 to CHERRYRD4 138kV line 1 | Current Study | Rebuild the PARADSE4 to CHERRYRD4 138kV line CKT1 (2.6 miles) to a standard rating of 478 MVA | 2506813.4 | 100% | 2506813.4 | 0.35266
GEN-2023-019 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SNYDER-4 to SNYDER4 138kV line 1 | Current Study | Rebuild the SNYDER-4 to SNYDER4 138kV line CKT1 (3.7 miles) to a standard rating of 286 MVA | 3567388.3 | 100% | 3567388.3 | 0.26556
GEN-2023-019 | 04 SOUTHEAST | TBD | ERIS | Upgrade the GRANFLD2 138/69 kV transformer 1 | Current Study | Upgrade the GRANFLD2 138/69 kV transformer 1 to a standard rating of 250 MVA | 3128743 | 100% | 3128743 | 0.07537
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 295270.6086 | 3.556% | 8302968 | 0.02845
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 18976.2314 | 3.556% | 533608.96 | 0.02845
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 35812.1949 | 53.69% | 66701.12 | 0.25997
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 35812.1949 | 53.69% | 66701.12 | 0.25997
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 1992026.7946 | 53.69% | 3710249.8 | 0.3545
GEN-2023-020 | 04 SOUTHEAST | 158709 | ERIS | Russett-S Brown 138 kV GEN-2023-020 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-020 (220MW/Solar), into Russett-S Brown 138 kV | 4999999 | 100% | 4999999 | 1
GEN-2023-020 | 04 SOUTHEAST | 158708 | ERIS | Russett-S Brown 138 kV GEN-2023-020 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-020 (220MW/Solar), into Russett-S Brown 138 kV | 499999 | 100% | 499999 | 1
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 4569.002 | 5.265% | 86774.31 | 0.02344
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 13707.0059 | 5.265% | 260322.93 | 0.02344
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 535909.3094 | 4.714% | 11367434.61 | 0.02408
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line CKT1 (0.17 miles) to a standard rating of 286 MVA | 79563.8978 | 48.54% | 163907.03 | 0.05518
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | 899184.0947 | 41.82% | 2150074.57 | 0.25769
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2789.0706 | 0.3249% | 858333 | 0.02511
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to CHIKSAW4 138kV line 1 | Current Study | Rebuild the FNDTION4 to CHIKSAW4 138kV line CKT1 (1.72 miles) to a standard rating of 286 MVA | 796375.1097 | 48.02% | 1658353.48 | 0.17624
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to SPRNDAL4 138kV line 1 | Current Study | Rebuild the FNDTION4 to SPRNDAL4 138kV line CKT1 (2.58 miles) to a standard rating of 286 MVA | 1194562.6646 | 48.02% | 2487530.22 | 0.17624
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HLDTNTP4 to LOCO4 138kV line 1 | Current Study | Rebuild the HLDTNTP4 to LOCO4 138kV line CKT1 (12.85 miles) to a standard rating of 286 MVA | 1012536.8649 | 8.173% | 12389443.15 | 0.05518
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | Current Study | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | 4240477.3263 | 44.7% | 9487324.56 | 0.40302
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | Current Study | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | 282510.0149 | 4.651% | 6074201.7 | 0.01997
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 289545.5726 | 4.714% | 6141692.83 | 0.02408
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | Current Study | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | 1564508.1135 | 30.67% | 5100401.11 | 0.11918
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | Current Study | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | 2463582.7193 | 30.67% | 8031444.47 | 0.11918
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 41412.9778 | 53.69% | 77132.72 | 0.25997
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | 4883013.1779 | 41.82% | 11675965.49 | 0.25769
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 2303623.1663 | 53.69% | 4290507.55 | 0.4254
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 3368184.1576 | 24.65% | 13662133.03 | 0.2201
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | Current Study | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | 504026.9589 | 41.82% | 1205198.75 | 0.25769
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 49207.2688 | 4.325% | 1137707.62 | 0.04577
GEN-2023-020 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 471784.0474 | 3.006% | 15696508.52 | 0.03243
GEN-2023-022 | 04 SOUTHEAST | 158713 | ERIS | CaN/Adian River 345 kV Substation GEN-2023-022 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-022 (250MW/Wind), into CaN/Adian River 345 kV Substation | 1790488 | 100% | 1790488 | 1
GEN-2023-022 | 04 SOUTHEAST | 158712 | ERIS | CaN/Adian River 345 kV Substation GEN-2023-022 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-022 (250MW/Wind), into CaN/Adian River 345 kV Substation | 1591654 | 100% | 1591654 | 1
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Build a new Grove 161/138 kV transformer 2 | Current Study | Build a new Grove 161/138 kV transformer 2 | 971631.1734 | 26.94% | 3606166 | 0.0774
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Build a new GROVE 161/138 kV transformer 3 | Current Study | Build a new GROVE 161/138 kV transformer 3 to a standard rating of 112 MVA | 1320744.0776 | 36.62% | 3606166 | 0.0774
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | Current Study | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | 1064283.4993 | 18.17% | 5856160.8 | 0.08441
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ADAIR2 to VINITA 2 line 69kV | Current Study | Rebuild the ADAIR2 to VINITA 2 line 69kV (19.11 miles) to a standard rating of 71 MVA | 5400753.6366 | 31.09% | 17370015.39 | 0.06091
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 1129816.6017 | 3.981% | 28382211.2 | 0.05874
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 320647.9762 | 3.355% | 9556107.4 | 0.05874
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 209070.7831 | 1.194% | 17509993.2 | 0.05874
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 2121630.447 | 5.289% | 40112762.2 | 0.05874
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GROVE4 to G23-162-TAP 138kV line 1 | Current Study | Rebuild the GROVE4 to G23-162-TAP 138kV line CKT1 (10.53 miles) to a standard rating of 286 MVA | 3707399.9595 | 36.52% | 10152594.27 | 0.2584
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEO1845 to NOL4355 161kV line 1 | Current Study | Rebuild the NEO1845 to NOL4355 161kV line CKT1 (23.13 miles) to a standard rating of 557 MVA | 5224564.8129 | 23.09% | 22626321.12 | 0.10351
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PCP-TAP2 to HUNTAP-2 69kV line 1 | Current Study | Rebuild the PCP-TAP2 to HUNTAP-2 161kV line CKT1 (3.07 miles) to a standard rating of 71 MVA | 1423589.8418 | 51.02% | 2790473.43 | 0.06318
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PCP-TAP2 to PRYORC12 69kV line 1 | Current Study | Rebuild the PCP-TAP2 to PRYORC12 69kV line CKT1 (3.03 miles) to a standard rating of 71 MVA | 1405041.4399 | 51.02% | 2754115.47 | 0.06318
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PRY-JCT2 to PRYORC12 69kV line 1 | Current Study | Rebuild the PRY-JCT2 to PRYORC12 69kV line CKT1 (4.65 miles) to a standard rating of 122 MVA | 2155885.6756 | 51.01% | 4226612.85 | 0.13426
GEN-2023-027 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PRY-JCT4 to G23-027-TAP 138kV line 1 | Current Study | Rebuild the PRY-JCT4 to G23-027-TAP line CKT1 (6.77 miles) to a standard rating of 286 MVA | 4891032.5569 | 74.93% | 6527356.43 | 0.7416
GEN-2023-027 | 04 SOUTHEAST | 158723 | ERIS | Bird Hollow (Langley) - Pryor Junction 138 kV Line GEN-2023-027 Intercon (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-027 (150MW/Hybrid), into Bird Hollow (Langley) - Pryor Junction 138 kV Line | 11500000 | 100% | 11500000 | 1
GEN-2023-027 | 04 SOUTHEAST | 158722 | ERIS | Bird Hollow (Langley) - Pryor Junction 138 kV Line GEN-2023-027 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-027 (150MW/Hybrid), into Bird Hollow (Langley) - Pryor Junction 138 kV Line | 2125000 | 100% | 2125000 | 1
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | Current Study | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | 412566.9369 | 7.045% | 5856160.8 | 0.02134
GEN-2023-028 | 04 SOUTHEAST | 158725 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-028 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-028 (230MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | 5800735 | 100% | 5800735 | 1
GEN-2023-028 | 04 SOUTHEAST | 158724 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-028 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-028 (230MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | 1057500 | 100% | 1057500 | 1
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AFTON5 to KETCHUM5 161kV line 1 | Current Study | Rebuild the AFTON5 to KETCHUM5 161kV line CKT1 (12.8 miles) to a standard rating of 557 MVA | 6302578.4254 | 50.33% | 12521267.2 | 0.1906
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRYGULCH5 to G23-028-TAP 161kV line 1 | Current Study | Rebuild the DRYGULCH5 to G23-028-TAP 161kV line CKT1 (4.82 miles) to a standard rating of 557 MVA | 3097459.7363 | 65.69% | 4715039.68 | 0.62444
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 1848880.5623 | 6.514% | 28382211.2 | 0.06269
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 524722.1627 | 5.491% | 9556107.4 | 0.06269
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 342132.4368 | 1.954% | 17509993.2 | 0.06269
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ORO110 5 to RIV4525 161kV line 1 | Current Study | Rebuild the existing ORO110 5 to RIV4525 161 kV line 1 (11.9 miles) to a standard rating of 557 MVA | 1347492.7338 | 11.58% | 11640865.6 | 0.04044
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 3471927.4686 | 8.655% | 40112762.2 | 0.06269
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MIAMI5 to AFTON5 161kV line 1 | Current Study | Rebuild the MIAMI5 to AFTON5 161kV line CKT1 (13.5 miles) to a standard rating of 557 MVA | 6642211.3287 | 50.3% | 13206024 | 0.09047
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PENSA5 to G23-049-TAP 161kV line 1 | Current Study | Rebuild the PENSA5 to G23-049-TAP 161kV line CKT1 (6.5 miles) to a standard rating of 557 MVA | 3403458.2579 | 53.53% | 6358456 | 0.37556
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PENSA5 to KETCHUM5 161kV line 1 | Current Study | Rebuild the PENSA5 to KETCHUM5 161kV line CKT1 (4.8 miles) to a standard rating of 557 MVA | 2363466.9095 | 50.33% | 4695475.2 | 0.1906
GEN-2023-028 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RIV4525 to STL4395 161kV line 1 | Current Study | Rebuild the RIV4525 to STL4395 161kV line CKT1 (6.82 miles) to a standard rating of 557 MVA | 1736940.4417 | 26.04% | 6671487.68 | 0.04639
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Build a new Grove 161/138 kV transformer 2 | Current Study | Build a new Grove 161/138 kV transformer 2 | 118503.8537 | 3.286% | 3606166 | 0.02832
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Build a new GROVE 161/138 kV transformer 3 | Current Study | Build a new GROVE 161/138 kV transformer 3 to a standard rating of 112 MVA | 161082.9986 | 4.467% | 3606166 | 0.02832
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Build a new HOC404 161/138 kV transformer 3 | Current Study | Build a new HOC404 161/138 kV transformer 3 to a standard rating of 165 MVA | 296729.3177 | 8.228% | 3606166 | 0.04247
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | Current Study | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | 199214.3027 | 3.402% | 5856160.8 | 0.0474
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Build a new RIV4525 to HOC4045 161kV line 1 | Current Study | Build a new RIV4525 to HOC4045 161kV line CKT1 (8.64 miles) to a standard rating of 557 MVA | 745909.3288 | 8.256% | 9035219.52 | 0.07715
GEN-2023-029 | 04 SOUTHEAST | 158727 | ERIS | Adair - Pryor 69 kV Line GEN-2023-029 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-029 (50MW/Solar), into Adair - Pryor 69 kV Line | 10750000 | 100% | 10750000 | 1
GEN-2023-029 | 04 SOUTHEAST | 158726 | ERIS | Adair - Pryor 69 kV Line GEN-2023-029 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-029 (50MW/Solar), into Adair - Pryor 69 kV Line | 1775000 | 100% | 1775000 | 1
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 2J6 to AFTPTP2 69kV line 1 | Current Study | Rebuild the 2J6 to AFTPTP2 69kV line CKT1 (5.13 miles) to a standard rating of 122 MVA | 951791.2831 | 20.41% | 4662908.37 | 0.10187
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 2J6 to VINEOTP2 69kV line 1 | Current Study | Rebuild the 2J6 to VINEOTP2 69kV line CKT1 (2.1 miles) to a standard rating of 122 MVA | 389622.1627 | 20.41% | 1908792.9 | 0.10187
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ADAIR2 to VINITA 2 line 69kV | Current Study | Rebuild the ADAIR2 to VINITA 2 line 69kV (19.11 miles) to a standard rating of 71 MVA | 10322405.7767 | 59.43% | 17370015.39 | 0.34925
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AFTPTP2 to EXPLTP2 69kV line 1 | Current Study | Rebuild the AFTPTP2 to EXPLTP2 69kV line CKT1 (0.3 miles) to a standard rating of 122 MVA | 55660.309 | 20.41% | 272684.7 | 0.10187
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 399109.5418 | 1.406% | 28382211.2 | 0.06225
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 113269.4162 | 1.185% | 9556107.4 | 0.06225
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 73854.5923 | 0.4218% | 17509993.2 | 0.06225
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ORO110 5 to RIV4525 161kV line 1 | Current Study | Rebuild the existing ORO110 5 to RIV4525 161 kV line 1 (11.9 miles) to a standard rating of 557 MVA | 287572.9021 | 2.47% | 11640865.6 | 0.0397
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 749469.3867 | 1.868% | 40112762.2 | 0.06225
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GROVE4 to G23-162-TAP 138kV line 1 | Current Study | Rebuild the GROVE4 to G23-162-TAP 138kV line CKT1 (10.53 miles) to a standard rating of 286 MVA | 439895.0571 | 4.333% | 10152594.27 | 0.09198
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEO1845 to NOL4355 161kV line 1 | Current Study | Rebuild the NEO1845 to NOL4355 161kV line CKT1 (23.13 miles) to a standard rating of 557 MVA | 441479.344 | 1.951% | 22626321.12 | 0.02624
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PCP-TAP2 to HUNTAP-2 69kV line 1 | Current Study | Rebuild the PCP-TAP2 to HUNTAP-2 161kV line CKT1 (3.07 miles) to a standard rating of 71 MVA | 882589.6503 | 31.63% | 2790473.43 | 0.11751
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PCP-TAP2 to PRYORC12 69kV line 1 | Current Study | Rebuild the PCP-TAP2 to PRYORC12 69kV line CKT1 (3.03 miles) to a standard rating of 71 MVA | 871090.1108 | 31.63% | 2754115.47 | 0.11751
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PRY-JCT2 to PRYORC12 69kV line 1 | Current Study | Rebuild the PRY-JCT2 to PRYORC12 69kV line CKT1 (4.65 miles) to a standard rating of 122 MVA | 1345140.3474 | 31.83% | 4226612.85 | 0.25131
GEN-2023-029 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RIV4525 to STL4395 161kV line 1 | Current Study | Rebuild the RIV4525 to STL4395 161kV line CKT1 (6.82 miles) to a standard rating of 557 MVA | 333804.7345 | 5.003% | 6671487.68 | 0.04101
GEN-2023-030 | 04 SOUTHEAST | 158728 | ERIS | Tap between 345 kV SW Shreveport-Dolet Hills Subs GEN-2023-030 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-030 (25MW/Solar), into Tap between 345 kV SW Shreveport-Dolet Hills Subs | 200000 | 100% | 200000 | 1
GEN-2023-030 | 04 SOUTHEAST | 158729 | ERIS | Tap between 345 kV SW Shreveport-Dolet Hills SubsGEN-2023-030 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-030 (25MW/Solar), into Tap between 345 kV SW Shreveport-Dolet Hills Subs | 250000 | 100% | 250000 | 1
GEN-2023-035 | 04 SOUTHEAST | 158739 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | 5000000 | 100% | 5000000 | 1
GEN-2023-035 | 04 SOUTHEAST | 158738 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | 500000 | 100% | 500000 | 1
GEN-2023-035 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2922.2586 | 0.3405% | 858333 | 0.02894
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 430428.0289 | 5.184% | 8302968 | 0.04562
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 27662.4278 | 5.184% | 533608.96 | 0.04562
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 2991.7904 | 4.485% | 66701.12 | 0.02389
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 2991.7904 | 4.485% | 66701.12 | 0.02389
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 166432.1912 | 4.486% | 3710249.8 | 0.03258
GEN-2023-038 | 04 SOUTHEAST | 158745 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | 1676256 | 100% | 1676256 | 1
GEN-2023-038 | 04 SOUTHEAST | 158744 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | 1877533 | 100% | 1877533 | 1
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ACOPA2 to ACOPT2 69kV line 1 | Current Study | Rebuild the ACOPA2 to ACOPT2 69kV line CKT1 (3.28 miles) to a standard rating of 143 MVA | 1225913.7927 | 41.12% | 2981352.72 | 0.09649
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AOCPT2 to LULA2 69kV line 1 | Current Study | Rebuild the AOCPT2 to LULA2 69kV line CKT1 (9.27 miles) to a standard rating of 143 MVA | 3464701.4812 | 41.12% | 8425957.23 | 0.09649
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 9046.2128 | 10.42% | 86774.31 | 0.05105
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 27138.6383 | 10.42% | 260322.93 | 0.05105
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 1061176.5054 | 9.335% | 11367434.61 | 0.05245
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | 109091.4066 | 5.074% | 2150074.57 | 0.03439
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2324.478 | 0.2708% | 858333 | 0.02302
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | Current Study | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | 506478.9801 | 5.338% | 9487324.56 | 0.05295
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to LATTAJT4 138kV line 1 | Current Study | Rebuild the LASALLE4 to LATTAJT4 138kV line CKT1 (7.1 miles) to a standard rating of 286 MVA | 1906020.5299 | 27.84% | 6845528.9 | 0.12539
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | Current Study | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | 1612597.5679 | 26.55% | 6074201.7 | 0.12539
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1 | Current Study | Rebuild the LATTAJT4 to OILCRTP4 138kV line CKT1 (4.55 miles) to a standard rating of 286 MVA | 1221463.8607 | 27.84% | 4386923.45 | 0.12539
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 573341.335 | 9.335% | 6141692.83 | 0.05245
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | Current Study | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | 187003.937 | 3.666% | 5100401.11 | 0.01567
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PARKLN2 to ADAINDU2 69kV line 1 | Current Study | Rebuild the PARKLN2 to ADAINDU2 69kV line CKT1 (2.87 miles) to a standard rating of 143 MVA | 1152738.0631 | 44.19% | 2608683.63 | 0.09649
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PAYNESW4 to PAOLI4 138kV line 1 | Current Study | Rebuild the PAYNESW4 to PAOLI4 138kV line CKT1 (12 miles) to a standard rating of 286 MVA | 1243287.3789 | 10.75% | 11569908 | 0.06339
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | Current Study | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | 294469.3375 | 3.666% | 8031444.47 | 0.01567
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 3459.686 | 4.485% | 77132.72 | 0.02389
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | 592420.1496 | 5.074% | 11675965.49 | 0.03439
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 192436.273 | 4.485% | 4290507.55 | 0.03909
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 997058.1908 | 7.298% | 13662133.03 | 0.07167
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | Current Study | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | 61149.8916 | 5.074% | 1205198.75 | 0.03439
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VALLYU2 to AOCPA2 69kV line 1 | Current Study | Rebuild the VALLYU2 to AOCPA2 69kV line CKT1 (1.62 miles) to a standard rating of 143 MVA | 650674.4468 | 44.19% | 1472497.38 | 0.09649
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 1638210.6902 | 10.44% | 15696508.52 | 0.12387
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 58082.5141 | 2.299% | 2526096.58 | 0.04645
GEN-2023-038 | 04 SOUTHEAST | TBD | ERIS | Upgrade the LULA4 138/69 kV transformer 1 | Current Study | Upgrade the LULA4 138/69 kV transformer 1 to a standard rating of 250 MVA | 1286519.7639 | 41.12% | 3128743 | 0.09649
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Build a new AFTON5 to MIAMI5 161kV line 2 | Current Study | Build a new AFTON5 to MIAMI5 161kV line CKT2 (13.5 miles) to a standard rating of 557 MVA | 10160698.424 | 71.97% | 14117530.5 | 0.11291
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | Current Study | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | 547082.8223 | 9.342% | 5856160.8 | 0.04339
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Build a new RIV4525 to HOC4045 161kV line 1 | Current Study | Build a new RIV4525 to HOC4045 161kV line CKT1 (8.64 miles) to a standard rating of 557 MVA | 2804483.7202 | 31.04% | 9035219.52 | 0.09669
GEN-2023-049 | 04 SOUTHEAST | 158758 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-049 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-049 (150MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | 6176735 | 100% | 6176735 | 1
GEN-2023-049 | 04 SOUTHEAST | 158757 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-049 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-049 (150MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | 682500 | 100% | 682500 | 1
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AFTON5 to KETCHUM5 161kV line 1 | Current Study | Rebuild the AFTON5 to KETCHUM5 161kV line CKT1 (12.8 miles) to a standard rating of 557 MVA | 5141422.0165 | 41.06% | 12521267.2 | 0.23841
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRYGULCH5 to G23-028-TAP 161kV line 1 | Current Study | Rebuild the DRYGULCH5 to G23-028-TAP 161kV line CKT1 (4.82 miles) to a standard rating of 557 MVA | 1617579.9437 | 34.31% | 4715039.68 | 0.50002
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 1228488.0209 | 4.328% | 28382211.2 | 0.06387
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 348651.4512 | 3.648% | 9556107.4 | 0.06387
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 227329.7739 | 1.298% | 17509993.2 | 0.06387
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ORO110 5 to RIV4525 161kV line 1 | Current Study | Rebuild the existing ORO110 5 to RIV4525 161 kV line 1 (11.9 miles) to a standard rating of 557 MVA | 1090241.7503 | 9.366% | 11640865.6 | 0.05017
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 2306920.9508 | 5.751% | 40112762.2 | 0.06387
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MIAMI5 to AFTON5 161kV line 1 | Current Study | Rebuild the MIAMI5 to AFTON5 161kV line CKT1 (13.5 miles) to a standard rating of 557 MVA | 5406347.1517 | 40.94% | 13206024 | 0.11291
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PENSA5 to G23-049-TAP 161kV line 1 | Current Study | Rebuild the PENSA5 to G23-049-TAP 161kV line CKT1 (6.5 miles) to a standard rating of 557 MVA | 2954997.7421 | 46.47% | 6358456 | 0.49998
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PENSA5 to KETCHUM5 161kV line 1 | Current Study | Rebuild the PENSA5 to KETCHUM5 161kV line CKT1 (4.8 miles) to a standard rating of 557 MVA | 1928033.2562 | 41.06% | 4695475.2 | 0.23841
GEN-2023-049 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RIV4525 to STL4395 161kV line 1 | Current Study | Rebuild the RIV4525 to STL4395 161kV line CKT1 (6.82 miles) to a standard rating of 557 MVA | 1442173.1982 | 21.62% | 6671487.68 | 0.05906
GEN-2023-051 | 04 SOUTHEAST | TBD | ERIS | Build a new ELKCITY to G22-145-TAP 138kV line 1 | Current Study | Build a new ELKCITY to G22-145-TAP 138kV line CKT1 (49.812 miles) to a standard rating of 286 MVA | 33690818.6094 | 81.12% | 41531452.37 | 0.08237
GEN-2023-051 | 04 SOUTHEAST | 158762 | ERIS | Red Rock Road - Weatherford Junction 138 kV Line GEN-2023-051 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-051 (150MW/Hybrid), into Red Rock Road - Weatherford Junction 138 kV Line | 11500000 | 100% | 11500000 | 1
GEN-2023-051 | 04 SOUTHEAST | 158761 | ERIS | Red Rock Road - Weatherford Junction 138 kV Line GEN-2023-051 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-051 (150MW/Hybrid), into Red Rock Road - Weatherford Junction 138 kV Line | 2125000 | 100% | 2125000 | 1
GEN-2023-051 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2347.7025 | 0.2735% | 858333 | 0.031
GEN-2023-053 | 04 SOUTHEAST | 158765 | ERIS | Pittsburg - Valiant 345kV line GEN-2023-053 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-053 (212MW/Wind), into Pittsburg - Valiant 345kV line | 18100000 | 100% | 18100000 | 1
GEN-2023-053 | 04 SOUTHEAST | 158764 | ERIS | Pittsburg - Valiant 345kV line GEN-2023-053 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-053 (212MW/Wind), into Pittsburg - Valiant 345kV line | 3275000 | 100% | 3275000 | 1
GEN-2023-053 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 876.617 | 0.1021% | 858333 | 0.00819
GEN-2023-055 | 04 SOUTHEAST | TBD | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | Current Study | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | 2211362.8164 | 37.76% | 5856160.8 | 0.26308
GEN-2023-055 | 04 SOUTHEAST | 158769 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | 1750000 | 100% | 1750000 | 1
GEN-2023-055 | 04 SOUTHEAST | 158768 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | 2406249 | 100% | 2406249 | 1
GEN-2023-055 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AFTON5 to KETCHUM5 161kV line 1 | Current Study | Rebuild the AFTON5 to KETCHUM5 161kV line CKT1 (12.8 miles) to a standard rating of 557 MVA | 1077266.7581 | 8.603% | 12521267.2 | 0.07493
GEN-2023-055 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 764366.9008 | 2.693% | 28382211.2 | 0.05961
GEN-2023-055 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 216931.4024 | 2.27% | 9556107.4 | 0.05961
GEN-2023-055 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 141444.8914 | 0.8078% | 17509993.2 | 0.05961
GEN-2023-055 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 1435369.3218 | 3.578% | 40112762.2 | 0.05961
GEN-2023-055 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MIAMI5 to AFTON5 161kV line 1 | Current Study | Rebuild the MIAMI5 to AFTON5 161kV line CKT1 (13.5 miles) to a standard rating of 557 MVA | 1157465.5196 | 8.765% | 13206024 | 0.03626
GEN-2023-055 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PENSA5 to KETCHUM5 161kV line 1 | Current Study | Rebuild the PENSA5 to KETCHUM5 161kV line CKT1 (4.8 miles) to a standard rating of 557 MVA | 403975.0343 | 8.603% | 4695475.2 | 0.07493
GEN-2023-056 | 04 SOUTHEAST | TBD | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | Current Study | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | 313101.4217 | 8.682% | 3606166 | 0.01634
GEN-2023-056 | 04 SOUTHEAST | 158771 | ERIS | Van Buren 161 kV GEN-2023-056 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-056 (150MW/Battery/Storage), into Van Buren 161 kV | 4400000 | 100% | 4400000 | 1
GEN-2023-056 | 04 SOUTHEAST | 158770 | ERIS | Van Buren 161 kV GEN-2023-056 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-056 (150MW/Battery/Storage), into Van Buren 161 kV | 775000 | 100% | 775000 | 1
GEN-2023-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FTGIB5 to OKAYGR5 161kV line 1 | Current Study | Rebuild the FTGIB5 to OKAYGR5 161kV line CKT1 (5.9 miles) to a standard rating of 557 MVA | 768413.0242 | 13.31% | 5771521.6 | 0.03445
GEN-2023-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 1199404.0801 | 7.663% | 15651584 | 0.09883
GEN-2023-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MUSKTAP5 to FTGIB5 161kV line 1 | Current Study | Rebuild the MUSKTAP5 to FTGIB5 161kV line CKT1 (7.4 miles) to a standard rating of 557 MVA | 1082688.999 | 14.96% | 7238857.6 | 0.03445
GEN-2023-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RSKERR5 to SUNSTCN5 161kV line 1 | Current Study | Rebuild the RSKERR5 to SUNSTCN5 161kV line CKT1 (6.8 miles) to a standard rating of 557 MVA | 278331.2337 | 4.184% | 6651923.2 | 0.02304
GEN-2023-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TARBY5 to SHAD-PT5 161kV line 1 | Current Study | Rebuild the TARBY5 to SHAD-PT5 161kV line CKT1 (1.53 miles) to a standard rating of 557 MVA | 62624.5276 | 4.184% | 1496682.72 | 0.02304
GEN-2023-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VANBUR5 to VBI5 161kV line Z1 | Current Study | Rebuild the VANBUR5 to VBI5 161kV line CKTZ1 (0.22 miles) to a standard rating of 557 MVA | 100445.3453 | 46.67% | 215209.28 | 0.73357
GEN-2023-056 | 04 SOUTHEAST | TBD | ERIS | Upgrade the VBI 161/69 kV transformer 2 | Current Study | Upgrade the VBI 161/69 kV transformer 2 to a standard rating of 250 MVA | 3606166 | 100% | 3606166 | 0.0517
GEN-2023-057 | 04 SOUTHEAST | 158773 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | 0 | 100% | 0 | 1
GEN-2023-057 | 04 SOUTHEAST | 158772 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | 970399 | 100% | 970399 | 1
GEN-2023-057 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 761289.4296 | 2.682% | 28382211.2 | 0.03958
GEN-2023-057 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 216057.9997 | 2.261% | 9556107.4 | 0.03958
GEN-2023-057 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 140875.4102 | 0.8045% | 17509993.2 | 0.03958
GEN-2023-057 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 1429590.2807 | 3.564% | 40112762.2 | 0.03958
GEN-2023-059 | 04 SOUTHEAST | 158775 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | 11500000 | 100% | 11500000 | 1
GEN-2023-059 | 04 SOUTHEAST | 158774 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | 2125000 | 100% | 2125000 | 1
GEN-2023-059 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ROKHILL4 to G23-059-TAP 138kV line 1 | Current Study | Rebuild the ROKHILL4-138 to G23-059-TAP 138kV line CKT1 (7 miles) to a standard rating of 286 MVA | 6749113 | 100% | 6749113 | 0.60704
GEN-2023-064 | 04 SOUTHEAST | TBD | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | Current Study | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | 418235.0285 | 11.6% | 3606166 | 0.01637
GEN-2023-064 | 04 SOUTHEAST | 158784 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | 8600000 | 100% | 8600000 | 1
GEN-2023-064 | 04 SOUTHEAST | 158783 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | 800000 | 100% | 800000 | 1
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 2CHECDST to SUMMIT2 69kV line 1 | Current Study | Rebuild the 2CHECDST to SUMMIT2 69kV line CKT1 (12.9 miles) to a standard rating of 71 MVA | 7030950.2364 | 59.96% | 11725442.1 | 0.01662
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FTGIB5 to OKAYGR5 161kV line 1 | Current Study | Rebuild the FTGIB5 to OKAYGR5 161kV line CKT1 (5.9 miles) to a standard rating of 557 MVA | 1393329.4702 | 24.14% | 5771521.6 | 0.04685
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to G23-145-TAP 161kV line 1 | Current Study | Rebuild the GORE5 to G23-145-TAP 161kV line CKT1 (9.2 miles) to a standard rating of 557 MVA | 1806041.1553 | 20.07% | 8999660.8 | 0.17073
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 2595007.3503 | 16.58% | 15651584 | 0.16037
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MUSKTAP5 to FTGIB5 161kV line 1 | Current Study | Rebuild the MUSKTAP5 to FTGIB5 161kV line CKT1 (7.4 miles) to a standard rating of 557 MVA | 1963192.244 | 27.12% | 7238857.6 | 0.04685
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RSKERR5 to G23-064-TAP 161kV line 1 | Current Study | Rebuild the RSKERR5 to G23-064-TAP 161kV line CKT1 (2 miles) to a standard rating of 557 MVA | 1617549.7515 | 82.68% | 1956448 | 0.69011
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RSKERR5 to SUNSTCN5 161kV line 1 | Current Study | Rebuild the RSKERR5 to SUNSTCN5 161kV line CKT1 (6.8 miles) to a standard rating of 557 MVA | 5257367.7478 | 79.04% | 6651923.2 | 0.3264
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TARBY5 to SHAD-PT5 161kV line 1 | Current Study | Rebuild the TARBY5 to SHAD-PT5 161kV line CKT1 (1.53 miles) to a standard rating of 557 MVA | 1182907.7433 | 79.04% | 1496682.72 | 0.3264
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VANBUR5 to VBI5 161kV line Z1 | Current Study | Rebuild the VANBUR5 to VBI5 161kV line CKTZ1 (0.22 miles) to a standard rating of 557 MVA | 54400.0791 | 25.28% | 215209.28 | 0.29797
GEN-2023-064 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 78677.1106 | 3.115% | 2526096.58 | 0.06292
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 420002.2733 | 5.058% | 8302968 | 0.08903
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 26992.3931 | 5.058% | 533608.96 | 0.08903
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 1577.296 | 2.365% | 66701.12 | 0.02519
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 1577.296 | 2.365% | 66701.12 | 0.02519
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 87737.0437 | 2.365% | 3710249.8 | 0.03435
GEN-2023-069 | 04 SOUTHEAST | 158793 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | 5000000 | 100% | 5000000 | 1
GEN-2023-069 | 04 SOUTHEAST | 158792 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | 500000 | 100% | 500000 | 1
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 4WOODY to PHAROAH4 138kV line 1 | Current Study | Rebuild the 4WOODY to PHAROAH4 138kV line CKT1 (13.36 miles) to a standard rating of 286 MVA | 356195.5454 | 2.765% | 12881164.24 | 0.02977
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ACOPA2 to ACOPT2 69kV line 1 | Current Study | Rebuild the ACOPA2 to ACOPT2 69kV line CKT1 (3.28 miles) to a standard rating of 143 MVA | 372576.6605 | 12.5% | 2981352.72 | 0.05865
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AOCPT2 to LULA2 69kV line 1 | Current Study | Rebuild the AOCPT2 to LULA2 69kV line CKT1 (9.27 miles) to a standard rating of 143 MVA | 1052983.4277 | 12.5% | 8425957.23 | 0.05865
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 4759.6724 | 5.485% | 86774.31 | 0.05372
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 14279.0171 | 5.485% | 260322.93 | 0.05372
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 558306.3044 | 4.911% | 11367434.61 | 0.05519
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | 60572.8528 | 2.817% | 2150074.57 | 0.03819
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 1072.8748 | 0.125% | 858333 | 0.02125
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HUGO-2 to VALYTIM2 69kV line 1 | Current Study | Rebuild the HUGO-2 to VALYTIM2 69kV line CKT1 (12.22 miles) to a standard rating of 71 MVA | 2602731.5175 | 23.43% | 11107356.78 | 0.0553
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | Current Study | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | 258548.1933 | 2.725% | 9487324.56 | 0.05406
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to LATTAJT4 138kV line 1 | Current Study | Rebuild the LASALLE4 to LATTAJT4 138kV line CKT1 (7.1 miles) to a standard rating of 286 MVA | 901935.7855 | 13.18% | 6845528.9 | 0.11867
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | Current Study | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | 763086.9821 | 12.56% | 6074201.7 | 0.11867
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1 | Current Study | Rebuild the LATTAJT4 to OILCRTP4 138kV line CKT1 (4.55 miles) to a standard rating of 286 MVA | 578001.102 | 13.18% | 4386923.45 | 0.11867
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 301646.4088 | 4.911% | 6141692.83 | 0.05519
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | 587627.3051 | 15.47% | 3798786.46 | 0.23359
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | Current Study | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | 99528.5791 | 1.951% | 5100401.11 | 0.01668
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PARKLN2 to ADAINDU2 69kV line 1 | Current Study | Rebuild the PARKLN2 to ADAINDU2 69kV line CKT1 (2.87 miles) to a standard rating of 143 MVA | 350337.2754 | 13.43% | 2608683.63 | 0.05865
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PAYNESW4 to PAOLI4 138kV line 1 | Current Study | Rebuild the PAYNESW4 to PAOLI4 138kV line CKT1 (12 miles) to a standard rating of 286 MVA | 590654.6682 | 5.105% | 11569908 | 0.06023
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | Current Study | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | 156724.5868 | 1.951% | 8031444.47 | 0.01668
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 1823.9743 | 2.365% | 77132.72 | 0.02519
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | 328940.4698 | 2.817% | 11675965.49 | 0.03819
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 101461.028 | 2.365% | 4290507.55 | 0.04122
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 525726.6504 | 3.848% | 13662133.03 | 0.07558
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | Current Study | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | 33953.3928 | 2.817% | 1205198.75 | 0.03819
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to ALLENGT4 138kV line 1 | Current Study | Rebuild the TUPELO4 to ALLENGT4 138kV line CKT1 (0.37 miles) to a standard rating of 286 MVA | 47563.8181 | 13.33% | 356738.83 | 0.23795
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 109611.2021 | 9.634% | 1137707.62 | 0.2243
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VALLYU2 to AOCPA2 69kV line 1 | Current Study | Rebuild the VALLYU2 to AOCPA2 69kV line CKT1 (1.62 miles) to a standard rating of 143 MVA | 197751.354 | 13.43% | 1472497.38 | 0.05865
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 793051.6189 | 5.052% | 15696508.52 | 0.11993
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 29360.1169 | 1.162% | 2526096.58 | 0.04696
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Upgrade the ATOKA-4 138/69 kV transformer 1 | Current Study | Upgrade the ATOKA-4 138/69 kV transformer 1 to a standard rating of 250 MVA | 1849454.6635 | 59.11% | 3128743 | 0.11063
GEN-2023-069 | 04 SOUTHEAST | TBD | ERIS | Upgrade the LULA4 138/69 kV transformer 1 | Current Study | Upgrade the LULA4 138/69 kV transformer 1 to a standard rating of 250 MVA | 390995.876 | 12.5% | 3128743 | 0.05865
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 232480.198 | 2.8% | 8302968 | 0.09856
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 14940.8641 | 2.8% | 533608.96 | 0.09856
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 621.1503 | 0.9312% | 66701.12 | 0.01984
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 621.1503 | 0.9312% | 66701.12 | 0.01984
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 34558.4338 | 0.9314% | 3710249.8 | 0.02706
GEN-2023-070 | 04 SOUTHEAST | 158795 | ERIS | Lane - McGee Creek Tap 69 kV GEN-2023-070 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-070 (50MW/Hybrid), into Lane - McGee Creek Tap 69 kV | 10750000 | 100% | 10750000 | 1
GEN-2023-070 | 04 SOUTHEAST | 158794 | ERIS | Lane - McGee Creek Tap 69 kV GEN-2023-070 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-070 (50MW/Hybrid), into Lane - McGee Creek Tap 69 kV | 1975000 | 100% | 1975000 | 1
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ATOKA-2 to LANE2 69kV line 1 | Current Study | Rebuild the ATOKA-2 to LANE2 69kV line CKT1 (7.93 miles) to a standard rating of 71 MVA | 7207965.57 | 100% | 7207965.57 | 0.71919
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 1895.629 | 2.185% | 86774.31 | 0.04279
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 5686.887 | 2.185% | 260322.93 | 0.04279
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 222351.3784 | 1.956% | 11367434.61 | 0.04396
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HUGO-2 to VALYTIM2 69kV line 1 | Current Study | Rebuild the HUGO-2 to VALYTIM2 69kV line CKT1 (12.22 miles) to a standard rating of 71 MVA | 6608255.3113 | 59.49% | 11107356.78 | 0.28081
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LANE2 to G23-070-TAP 69kV line 1 | Current Study | Rebuild the LANE2 to G23-070-TAP 69kV line CKT1 (6.3 miles) to a standard rating of 71 MVA | 5726378.7 | 100% | 5726378.7 | 0.71919
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to LATTAJT4 138kV line 1 | Current Study | Rebuild the LASALLE4 to LATTAJT4 138kV line CKT1 (7.1 miles) to a standard rating of 286 MVA | 327233.8859 | 4.78% | 6845528.9 | 0.08611
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | Current Study | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | 276857.7569 | 4.558% | 6074201.7 | 0.08611
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1 | Current Study | Rebuild the LATTAJT4 to OILCRTP4 138kV line CKT1 (4.55 miles) to a standard rating of 286 MVA | 209706.2227 | 4.78% | 4386923.45 | 0.08611
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 120133.866 | 1.956% | 6141692.83 | 0.04396
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | 213942.2243 | 5.632% | 3798786.46 | 0.17009
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MCGEETP2 to ANTLTAP2 69kV line 1 | Current Study | Rebuild the MCGEETP2 to ANTLTAP2 69kV line CKT1 (14.83 miles) to a standard rating of 71 MVA | 13479713.67 | 100% | 13479713.67 | 0.28081
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MCGEETP2 to G23-070-TAP 69kV line 1 | Current Study | Rebuild the MCGEETP2 to G23-070-TAP 69kV line CKT1 (4.59 miles) to a standard rating of 71 MVA | 4172075.91 | 100% | 4172075.91 | 0.28081
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PARKLN2 to ADAINDU2 69kV line 1 | Current Study | Rebuild the PARKLN2 to ADAINDU2 69kV line CKT1 (2.87 miles) to a standard rating of 143 MVA | 127620.7313 | 4.892% | 2608683.63 | 0.04273
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 718.294 | 0.9312% | 77132.72 | 0.01984
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 39961.664 | 0.9314% | 4290507.55 | 0.03247
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 207042.2565 | 1.515% | 13662133.03 | 0.05953
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to ALLENGT4 138kV line 1 | Current Study | Rebuild the TUPELO4 to ALLENGT4 138kV line CKT1 (0.37 miles) to a standard rating of 286 MVA | 29408.8117 | 8.244% | 356738.83 | 0.29425
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 45987.3481 | 4.042% | 1137707.62 | 0.18821
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VALLYU2 to AOCPA2 69kV line 1 | Current Study | Rebuild the VALLYU2 to AOCPA2 69kV line CKT1 (1.62 miles) to a standard rating of 143 MVA | 72036.7891 | 4.892% | 1472497.38 | 0.04273
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VALYTIM2 to ANTLTAP2 69kV line 1 | Current Study | Rebuild the VALYTIM2 to ANTLTAP2 69kV line CKT1 (3.5 miles) to a standard rating of 71 MVA | 3181321.5 | 100% | 3181321.5 | 0.28081
GEN-2023-070 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 289500.541 | 1.844% | 15696508.52 | 0.08756
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Build a new HANNA to WELEETK 138kV line 1 | Current Study | Build a new HANNA to WELEETK 138kV line CKT1 (21.204 miles) to a standard rating of 478 MVA | 17627572.7032 | 99.71% | 17679131.86 | 0.28035
GEN-2023-072 | 04 SOUTHEAST | 158799 | ERIS | McAlister 138 kV Substation GEN-2023-072 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-072 (250MW/Wind), into McAlister 138 kV Substation | 5000000 | 100% | 5000000 | 1
GEN-2023-072 | 04 SOUTHEAST | 158798 | ERIS | McAlister 138 kV Substation GEN-2023-072 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-072 (250MW/Wind), into McAlister 138 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 4WOODY to PHAROAH4 138kV line 1 | Current Study | Rebuild the 4WOODY to PHAROAH4 138kV line CKT1 (13.36 miles) to a standard rating of 286 MVA | 2807268.3859 | 21.79% | 12881164.24 | 0.09385
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DUSTIN4 to HANNA4 138kV line 1 | Current Study | Rebuild the DUSTIN4 to HANNA4 138kV line CKT1 (10.37 miles) to a standard rating of 478 MVA | 9998328.83 | 100% | 9998328.83 | 0.32108
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 1277721.9424 | 8.164% | 15651584 | 0.06317
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | 324265.4207 | 8.536% | 3798786.46 | 0.05156
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Rebuild the OKMULGE4 to KELCO4 138kV line 1 | Current Study | Rebuild the OKMULGE4 to KELCO4 138kV line CKT1 (2.24 miles) to a standard rating of 286 MVA | 443304.3443 | 20.53% | 2159716.16 | 0.06928
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 88536.8236 | 7.782% | 1137707.62 | 0.07247
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VANBUR5 to VBI5 161kV line Z1 | Current Study | Rebuild the VANBUR5 to VBI5 161kV line CKTZ1 (0.22 miles) to a standard rating of 557 MVA | 7451.0965 | 3.462% | 215209.28 | 0.03265
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 380130.9856 | 15.05% | 2526096.58 | 0.2432
GEN-2023-072 | 04 SOUTHEAST | TBD | ERIS | Upgrade the WELEETK5 161/138 kV transformer 1 | Current Study | Upgrade the WELEETK5 161/138 kV transformer 1 to a standard rating of 200 MVA | 797542.1719 | 22.12% | 3606166 | 0.06525
GEN-2023-075 | 04 SOUTHEAST | 158801 | ERIS | Delaware - Neosho 345 kV GEN-2023-075 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075 (200MW/Wind), into Delaware - Neosho 345 kV | 1325114 | 100% | 1325114 | 1
GEN-2023-075 | 04 SOUTHEAST | 158663 | ERIS | Delaware - Neosho 345 kV Interconnection (DISIS-2023-001) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075/076 (200/100MW/Wind), into Delaware - Neosho 345 kV | 17579961.3333 | 66.67% | 26369942 | 1
GEN-2023-075 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 4008406.1932 | 14.12% | 28382211.2 | 0.1563
GEN-2023-075 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 1137607.0523 | 11.9% | 9556107.4 | 0.1563
GEN-2023-075 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 741749.2544 | 4.236% | 17509993.2 | 0.1563
GEN-2023-075 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 7527200.9729 | 18.77% | 40112762.2 | 0.1563
GEN-2023-076 | 04 SOUTHEAST | 158663 | ERIS | Delaware - Neosho 345 kV Interconnection (DISIS-2023-001) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075/076 (200/100MW/Wind), into Delaware - Neosho 345 kV | 8789980.6667 | 33.33% | 26369942 | 1
GEN-2023-076 | 04 SOUTHEAST | 158802 | ERIS | Delaware - Neosho 345 kV GEN-2023-076 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-076 (100MW/Wind), into Delaware - Neosho 345 kV | 112911 | 100% | 112911 | 1
GEN-2023-076 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 2004203.0966 | 7.061% | 28382211.2 | 0.1563
GEN-2023-076 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 568803.5261 | 5.952% | 9556107.4 | 0.1563
GEN-2023-076 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 370874.6272 | 2.118% | 17509993.2 | 0.1563
GEN-2023-076 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 3763600.4864 | 9.383% | 40112762.2 | 0.1563
GEN-2023-080 | 04 SOUTHEAST | 158807 | ERIS | Lydia - Northwest TexarkaN/A 345 kV GEN-2023-080 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-080 (200MW/Hybrid), into Lydia - Northwest TexarkaN/A 345 kV | 18100000 | 100% | 18100000 | 1
GEN-2023-080 | 04 SOUTHEAST | 158806 | ERIS | Lydia - Northwest TexarkaN/A 345 kV GEN-2023-080 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-080 (200MW/Hybrid), into Lydia - Northwest TexarkaN/A 345 kV | 3475000 | 100% | 3475000 | 1
GEN-2023-080 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NNBOSTN4 to G18-003-TAP 138kV line 1 | Current Study | Rebuild the NNBOSTN4 to G18-003-TAP 138kV line CKT1 (1.7 miles) to a standard rating of 478 MVA | 61623.5018 | 3.76% | 1639070.3 | 0.01717
GEN-2023-088 | 04 SOUTHEAST | 158823 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-088 | 04 SOUTHEAST | 158822 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 4WOODY to PHAROAH4 138kV line 1 | Current Study | Rebuild the 4WOODY to PHAROAH4 138kV line CKT1 (13.36 miles) to a standard rating of 286 MVA | 1795225.549 | 13.94% | 12881164.24 | 0.12824
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 507990.4716 | 1.79% | 28382211.2 | 0.03386
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 144170.4047 | 1.509% | 9556107.4 | 0.03386
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 94002.8369 | 0.5369% | 17509993.2 | 0.03386
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 953931.8592 | 2.378% | 40112762.2 | 0.03386
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 744319.8563 | 4.756% | 15651584 | 0.07863
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the OKMULGE4 to KELCO4 138kV line 1 | Current Study | Rebuild the OKMULGE4 to KELCO4 138kV line CKT1 (2.24 miles) to a standard rating of 286 MVA | 264962.9042 | 12.27% | 2159716.16 | 0.08848
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RSKERR5 to G23-064-TAP 161kV line 1 | Current Study | Rebuild the RSKERR5 to G23-064-TAP 161kV line CKT1 (2 miles) to a standard rating of 557 MVA | 50528.0671 | 2.583% | 1956448 | 0.03685
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 32773.1141 | 2.881% | 1137707.62 | 0.05732
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VANBUR5 to VBI5 161kV line Z1 | Current Study | Rebuild the VANBUR5 to VBI5 161kV line CKTZ1 (0.22 miles) to a standard rating of 557 MVA | 4387.4612 | 2.039% | 215209.28 | 0.04108
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 301693.395 | 11.94% | 2526096.58 | 0.41243
GEN-2023-088 | 04 SOUTHEAST | TBD | ERIS | Upgrade the WELEETK5 161/138 kV transformer 1 | Current Study | Upgrade the WELEETK5 161/138 kV transformer 1 to a standard rating of 200 MVA | 515170.4408 | 14.29% | 3606166 | 0.09006
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 1738294.2564 | 20.94% | 8302968 | 0.29478
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 111715.3999 | 20.94% | 533608.96 | 0.29478
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 2364.5351 | 3.545% | 66701.12 | 0.03021
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 2364.5351 | 3.545% | 66701.12 | 0.03021
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 131509.7828 | 3.544% | 3710249.8 | 0.04119
GEN-2023-092 | 04 SOUTHEAST | 158828 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | 5000000 | 100% | 5000000 | 1
GEN-2023-092 | 04 SOUTHEAST | 158827 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | 499999 | 100% | 499999 | 1
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 7373.8595 | 8.498% | 86774.31 | 0.06658
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to BODLE4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to BODLE4 138kV line CKT1 (7.56 miles) to a standard rating of 286 MVA | 122933.1137 | 1.687% | 7289042.04 | 0.00182
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 22121.5785 | 8.498% | 260322.93 | 0.06658
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 864924.6064 | 7.609% | 11367434.61 | 0.0684
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | 93500.1224 | 4.349% | 2150074.57 | 0.04716
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to CHIKSAW4 138kV line 1 | Current Study | Rebuild the FNDTION4 to CHIKSAW4 138kV line CKT1 (1.72 miles) to a standard rating of 286 MVA | 86009.2841 | 5.186% | 1658353.48 | 0.0335
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to SPRNDAL4 138kV line 1 | Current Study | Rebuild the FNDTION4 to SPRNDAL4 138kV line CKT1 (2.58 miles) to a standard rating of 286 MVA | 129013.9262 | 5.186% | 2487530.22 | 0.0335
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HLDTNTP4 to LOCO4 138kV line 1 | Current Study | Rebuild the HLDTNTP4 to LOCO4 138kV line CKT1 (12.85 miles) to a standard rating of 286 MVA | 205704.3925 | 1.66% | 12389443.15 | 0.01973
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | Current Study | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | 361625.5135 | 3.812% | 9487324.56 | 0.06049
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 467308.7144 | 7.609% | 6141692.83 | 0.0684
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | Current Study | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | 127021.2607 | 2.49% | 5100401.11 | 0.01703
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | Current Study | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | 200016.4653 | 2.49% | 8031444.47 | 0.01703
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 2734.3322 | 3.545% | 77132.72 | 0.03021
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | 507751.7857 | 4.349% | 11675965.49 | 0.04716
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 152086.9304 | 3.545% | 4290507.55 | 0.04943
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 787929.1654 | 5.767% | 13662133.03 | 0.09062
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | Current Study | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | 52410.3825 | 4.349% | 1205198.75 | 0.04716
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to ALLENGT4 138kV line 1 | Current Study | Rebuild the TUPELO4 to ALLENGT4 138kV line CKT1 (0.37 miles) to a standard rating of 286 MVA | 7525.8573 | 2.11% | 356738.83 | 0.03012
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 31868.1254 | 2.801% | 1137707.62 | 0.05217
GEN-2023-092 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 208628.1879 | 1.329% | 15696508.52 | 0.02524
GEN-2023-100 | 04 SOUTHEAST | 158839 | ERIS | Degrasse 345 kV Substation GEN-2023-100 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100 (300MW/Hybrid), into Degrasse 345 kV Substation | 2756115 | 100% | 2756115 | 1
GEN-2023-100 | 04 SOUTHEAST | 158662 | ERIS | Degrasse 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100/102 (300/475MW/Hybrid), into Degrasse 345 kV Substation | 1890912 | 38.71% | 4884856 | 1
GEN-2023-100 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 4442.4591 | 0.5176% | 858333 | 0.02933
GEN-2023-101 | 04 SOUTHEAST | 158841 | ERIS | Tap Stateline Demarc - Wheeler 230 kV Line GEN-2023-101 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-101 (150MW/Hybrid), into Tap Stateline Demarc - Wheeler 230 kV Line | 11369957 | 100% | 11369957 | 1
GEN-2023-101 | 04 SOUTHEAST | 158840 | ERIS | Tap Stateline Demarc - Wheeler 230 kV Line GEN-2023-101 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-101 (150MW/Hybrid), into Tap Stateline Demarc - Wheeler 230 kV Line | 1700000 | 100% | 1700000 | 1
GEN-2023-101 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3735.8763 | 0.4352% | 858333 | 0.04933
GEN-2023-102 | 04 SOUTHEAST | 158662 | ERIS | Degrasse 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100/102 (300/475MW/Hybrid), into Degrasse 345 kV Substation | 2993944 | 61.29% | 4884856 | 1
GEN-2023-102 | 04 SOUTHEAST | 158842 | ERIS | Degrasse 345 kV Substation GEN-2023-102 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-102 (475MW/Hybrid), into Degrasse 345 kV Substation | 2756115 | 100% | 2756115 | 1
GEN-2023-102 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7033.8935 | 0.8195% | 858333 | 0.02933
GEN-2023-103 | 04 SOUTHEAST | 158844 | ERIS | Northeastern 138 kV Substation GEN-2023-103 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-103 (200MW/Battery/Storage), into Northeastern 138 kV Substation | 2050000 | 100% | 2050000 | 1
GEN-2023-103 | 04 SOUTHEAST | 158843 | ERIS | Northeastern 138 kV Substation GEN-2023-103 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-103 (200MW/Battery/Storage), into Northeastern 138 kV Substation | 2325000 | 100% | 2325000 | 1
GEN-2023-103 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 1538222.671 | 5.42% | 28382211.2 | 0.05998
GEN-2023-103 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 436555.7965 | 4.568% | 9556107.4 | 0.05998
GEN-2023-103 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 284645.6832 | 1.626% | 17509993.2 | 0.05998
GEN-2023-103 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 2888557.3535 | 7.201% | 40112762.2 | 0.05998
GEN-2023-104 | 04 SOUTHEAST | 158846 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | 5000000 | 100% | 5000000 | 1
GEN-2023-104 | 04 SOUTHEAST | 158845 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | 500000 | 100% | 500000 | 1
GEN-2023-104 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 1457.0902 | 0.1698% | 858333 | 0.02886
GEN-2023-132 | 04 SOUTHEAST | TBD | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | Current Study | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | 302179.2791 | 8.38% | 3606166 | 0.01577
GEN-2023-132 | 04 SOUTHEAST | 158875 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | 8600000 | 100% | 8600000 | 1
GEN-2023-132 | 04 SOUTHEAST | 158874 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | 800000 | 100% | 800000 | 1
GEN-2023-132 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 5HEBERN# to GREERSF5 161kV line 1 | Current Study | Rebuild the 5HEBERN# to GREERSF5 161kV line CKT1 (1.66 miles) to a standard rating of 557 MVA | 1623851.84 | 100% | 1623851.84 | 0.16008
GEN-2023-134 | 04 SOUTHEAST | TBD | ERIS | Build a new FIXCT4 to MAUD4 138kV line 1 | Current Study | Build a new FIXCT4 to MAUD4 138kV line CKT1 (13.2 miles) to a standard rating of 286 MVA | 11005684.8 | 100% | 11005684.8 | 0.25043
GEN-2023-134 | 04 SOUTHEAST | 158879 | ERIS | Fixico Tap to Weleetka 138 kV Line GEN-2023-134 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-134 (252MW/Wind), into Fixico Tap to Weleetka 138 kV Line | 11500000 | 100% | 11500000 | 1
GEN-2023-134 | 04 SOUTHEAST | 158878 | ERIS | Fixico Tap to Weleetka 138 kV Line GEN-2023-134 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-134 (252MW/Wind), into Fixico Tap to Weleetka 138 kV Line | 1925000 | 100% | 1925000 | 1
GEN-2023-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 4WOODY to PHAROAH4 138kV line 1 | Current Study | Rebuild the 4WOODY to PHAROAH4 138kV line CKT1 (13.36 miles) to a standard rating of 286 MVA | 2029503.3877 | 15.76% | 12881164.24 | 0.06731
GEN-2023-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 875075.8964 | 5.591% | 15651584 | 0.04292
GEN-2023-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild the OKMULGE4 to KELCO4 138kV line 1 | Current Study | Rebuild the OKMULGE4 to KELCO4 138kV line CKT1 (2.24 miles) to a standard rating of 286 MVA | 466716.5469 | 21.61% | 2159716.16 | 0.07236
GEN-2023-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 23262.5953 | 2.045% | 1137707.62 | 0.01889
GEN-2023-134 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 473041.0005 | 18.73% | 2526096.58 | 0.30024
GEN-2023-134 | 04 SOUTHEAST | TBD | ERIS | Upgrade the WELEETK5 161/138 kV transformer 1 | Current Study | Upgrade the WELEETK5 161/138 kV transformer 1 to a standard rating of 200 MVA | 625149.8563 | 17.34% | 3606166 | 0.05074
GEN-2023-135 | 04 SOUTHEAST | 158881 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | 250000 | 100% | 250000 | 1
GEN-2023-135 | 04 SOUTHEAST | 158880 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | 200000 | 100% | 200000 | 1
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Build a new AFTON5 to MIAMI5 161kV line 2 | Current Study | Build a new AFTON5 to MIAMI5 161kV line CKT2 (13.5 miles) to a standard rating of 557 MVA | 3956832.076 | 28.03% | 14117530.5 | 0.04397
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Build a new HOC404 161/138 kV transformer 3 | Current Study | Build a new HOC404 161/138 kV transformer 3 to a standard rating of 165 MVA | 3309436.6823 | 91.77% | 3606166 | 0.15789
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | Current Study | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | 305756.1291 | 5.221% | 5856160.8 | 0.02425
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Build a new RIV4525 to HOC4045 161kV line 1 | Current Study | Build a new RIV4525 to HOC4045 161kV line CKT1 (8.64 miles) to a standard rating of 557 MVA | 5484826.471 | 60.7% | 9035219.52 | 0.1891
GEN-2023-136 | 04 SOUTHEAST | 158883 | ERIS | Vinita Junction - Hockerville 138 kV GEN-2023-136 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-136 (150MW/Hybrid), into Vinita Junction - Hockerville 138 kV | 11500000 | 100% | 11500000 | 1
GEN-2023-136 | 04 SOUTHEAST | 158882 | ERIS | Vinita Junction - Hockerville 138 kV GEN-2023-136 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-136 (150MW/Hybrid), into Vinita Junction - Hockerville 138 Kv | 2125000 | 100% | 2125000 | 1
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 2J6 to AFTPTP2 69kV line 1 | Current Study | Rebuild the 2J6 to AFTPTP2 69kV line CKT1 (5.13 miles) to a standard rating of 122 MVA | 3711117.0869 | 79.59% | 4662908.37 | 0.1324
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 2J6 to VINEOTP2 69kV line 1 | Current Study | Rebuild the 2J6 to VINEOTP2 69kV line CKT1 (2.1 miles) to a standard rating of 122 MVA | 1519170.7373 | 79.59% | 1908792.9 | 0.1324
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AFTPTP2 to EXPLTP2 69kV line 1 | Current Study | Rebuild the AFTPTP2 to EXPLTP2 69kV line CKT1 (0.3 miles) to a standard rating of 122 MVA | 217024.391 | 79.59% | 272684.7 | 0.1324
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 1348894.0803 | 4.753% | 28382211.2 | 0.07013
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 382823.3329 | 4.006% | 9556107.4 | 0.07013
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 249610.7256 | 1.426% | 17509993.2 | 0.07013
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ORO110 5 to RIV4525 161kV line 1 | Current Study | Rebuild the existing ORO110 5 to RIV4525 161 kV line 1 (11.9 miles) to a standard rating of 557 MVA | 2211993.3778 | 19% | 11640865.6 | 0.10179
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 2533025.932 | 6.315% | 40112762.2 | 0.07013
GEN-2023-136 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RIV4525 to STL4395 161kV line 1 | Current Study | Rebuild the RIV4525 to STL4395 161kV line CKT1 (6.82 miles) to a standard rating of 557 MVA | 3158569.3056 | 47.34% | 6671487.68 | 0.12935
GEN-2023-137 | 04 SOUTHEAST | 158885 | ERIS | North Boston - Bann 138 kV Line Tap GEN-2023-137 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-137 (150MW/Battery/Storage), into North Boston - Bann 138 kV Line Tap | 250000 | 100% | 250000 | 1
GEN-2023-137 | 04 SOUTHEAST | 158884 | ERIS | North Boston - Bann 138 kV Line Tap GEN-2023-137 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-137 (150MW/Battery/Storage), into North Boston - Bann 138 kV Line Tap | 200000 | 100% | 200000 | 1
GEN-2023-137 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEWBOST2 to NNBOSTN2 69kV line 1 | Current Study | Rebuild the NEWBOST2 to NNBOSTN2 69kV line CKT1 (1.3 miles) to a standard rating of 122 MVA | 1181633.7 | 100% | 1181633.7 | 0.10913
GEN-2023-137 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NNBOSTN4 to G18-003-TAP 138kV line 1 | Current Study | Rebuild the NNBOSTN4 to G18-003-TAP 138kV line CKT1 (1.7 miles) to a standard rating of 478 MVA | 1350405.2882 | 82.39% | 1639070.3 | 0.50168
GEN-2023-137 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NWT-BNT4 to G18-003-TAP 138kV line 1 | Current Study | Rebuild the NWT-BNT4 to G18-003-TAP 138kV line CKT1 (12.49 miles) to a standard rating of 478 MVA | 12042345.91 | 100% | 12042345.91 | 0.49832
GEN-2023-138 | 04 SOUTHEAST | 158887 | ERIS | GRDA1 - Tonece7 345 kV Line GEN-2023-138 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-138 (250MW/Wind), into GRDA1 - Tonece7 345 kV Line | 10070786 | 100% | 10070786 | 1
GEN-2023-138 | 04 SOUTHEAST | 158886 | ERIS | GRDA1 - Tonece7 345 kV Line GEN-2023-138 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-138 (250MW/Wind), into GRDA1 - Tonece7 345 kV Line | 1531872 | 100% | 1531872 | 1
GEN-2023-138 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AVOCA5 to BEAVER5 161kV line 1 | Current Study | Rebuild the AVOCA5 to BEAVER5 161kV line CKT1 (11 miles) to a standard rating of 557 MVA | 2699552.3189 | 25.09% | 10760464 | 0.04234
GEN-2023-138 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AVOCA5 to EROGERS5 161kV line 1 | Current Study | Rebuild the AVOCA5 to EROGERS5 161kV line CKT1 (5.81 miles) to a standard rating of 557 MVA | 1425854.4521 | 25.09% | 5683481.44 | 0.04234
GEN-2023-138 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 1954514.7601 | 6.886% | 28382211.2 | 0.06097
GEN-2023-138 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 554701.7113 | 5.805% | 9556107.4 | 0.06097
GEN-2023-138 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 361679.8788 | 2.066% | 17509993.2 | 0.06097
GEN-2023-138 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 3670293.0528 | 9.15% | 40112762.2 | 0.06097
GEN-2023-138 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEO1845 to NOL4355 161kV line 1 | Current Study | Rebuild the NEO1845 to NOL4355 161kV line CKT1 (23.13 miles) to a standard rating of 557 MVA | 2853464.0527 | 12.61% | 22626321.12 | 0.03392
GEN-2023-145 | 04 SOUTHEAST | TBD | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | Current Study | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | 379400.7436 | 10.52% | 3606166 | 0.0165
GEN-2023-145 | 04 SOUTHEAST | 158893 | ERIS | Eufaula - Gore 161 kV Line GEN-2023-145 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-145 (180MW/Solar), into Eufaula - Gore 161 kV Line | 35300000 | 100% | 35300000 | 1
GEN-2023-145 | 04 SOUTHEAST | 158892 | ERIS | Eufaula - Gore 161 kV Line GEN-2023-145 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-145 (180MW/Solar), into Eufaula - Gore 161 kV Line | 800000 | 100% | 800000 | 1
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 2CHECDST to SUMMIT2 69kV line 1 | Current Study | Rebuild the 2CHECDST to SUMMIT2 69kV line CKT1 (12.9 miles) to a standard rating of 71 MVA | 4694491.8636 | 40.04% | 11725442.1 | 0.01233
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 823992.9046 | 2.903% | 28382211.2 | 0.0357
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 233853.5802 | 2.447% | 9556107.4 | 0.0357
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 152478.5895 | 0.8708% | 17509993.2 | 0.0357
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FTGIB5 to OKAYGR5 161kV line 1 | Current Study | Rebuild the FTGIB5 to OKAYGR5 161kV line CKT1 (5.9 miles) to a standard rating of 557 MVA | 2975866.2421 | 51.56% | 5771521.6 | 0.11118
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 1547338.2422 | 3.857% | 40112762.2 | 0.0357
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to G23-145-TAP 161kV line 1 | Current Study | Rebuild the GORE5 to G23-145-TAP 161kV line CKT1 (9.2 miles) to a standard rating of 557 MVA | 6876189.902 | 76.4% | 8999660.8 | 0.72225
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 5843208.3261 | 37.33% | 15651584 | 0.40123
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GOREGR2 to ILLINOTP2 69kV line 1 | Current Study | Rebuild the GOREGR2 to ILLINOTP2 69kV line CKT1 (0.52 miles) to a standard rating of 71 MVA | 472653.48 | 100% | 472653.48 | 0.02477
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GREENLF2 to MUSKSW2 69kV line 1 | Current Study | Rebuild the GREENLF2 to MUSKSW2 69kV line CKT1 (14.73 miles) to a standard rating of 71 MVA | 13388818.77 | 100% | 13388818.77 | 0.02477
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ILLINOTP2 to GREENLF2 69kV line 1 | Current Study | Rebuild the ILLINOTP2 to GREENLF2 69kV line CKT1 (3.51 miles) to a standard rating of 71 MVA | 3190410.99 | 100% | 3190410.99 | 0.02477
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MUSKTAP5 to FTGIB5 161kV line 1 | Current Study | Rebuild the MUSKTAP5 to FTGIB5 161kV line CKT1 (7.4 miles) to a standard rating of 557 MVA | 4192976.3569 | 57.92% | 7238857.6 | 0.11118
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the OKAYGR2 to MUSKSW2 69kV line 1 | Current Study | Rebuild the OKAYGR2 to MUSKSW2 69kV line CKT1 (10.16 miles) to a standard rating of 71 MVA | 9234921.84 | 100% | 9234921.84 | 0.02212
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RSKERR5 to G23-064-TAP 161kV line 1 | Current Study | Rebuild the RSKERR5 to G23-064-TAP 161kV line CKT1 (2 miles) to a standard rating of 557 MVA | 288370.1815 | 14.74% | 1956448 | 0.1367
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RSKERR5 to SUNSTCN5 161kV line 1 | Current Study | Rebuild the RSKERR5 to SUNSTCN5 161kV line CKT1 (6.8 miles) to a standard rating of 557 MVA | 1116224.2185 | 16.78% | 6651923.2 | 0.077
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TARBY5 to SHAD-PT5 161kV line 1 | Current Study | Rebuild the TARBY5 to SHAD-PT5 161kV line CKT1 (1.53 miles) to a standard rating of 557 MVA | 251150.4492 | 16.78% | 1496682.72 | 0.077
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VANBUR5 to VBI5 161kV line Z1 | Current Study | Rebuild the VANBUR5 to VBI5 161kV line CKTZ1 (0.22 miles) to a standard rating of 557 MVA | 27691.5153 | 12.87% | 215209.28 | 0.16853
GEN-2023-145 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 111345.8676 | 4.408% | 2526096.58 | 0.09894
GEN-2023-148 | 04 SOUTHEAST | 158899 | ERIS | Russell - Lake Pauline 138 kV Line GEN-2023-148 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-148 (110MW/Hybrid), into Russell - Lake Pauline 138 kV Line | 11500000 | 100% | 11500000 | 1
GEN-2023-148 | 04 SOUTHEAST | 158898 | ERIS | Russell - Lake Pauline 138 kV Line GEN-2023-148 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-148 (110MW/Hybrid), into Russell - Lake Pauline 138 kV Line | 2125000 | 100% | 2125000 | 1
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ANADARK4 to CHERRYRD4 138kV line 1 | Current Study | Rebuild the ANADARK4 to CHERRYRD4 138kV line CKT1 (25.15 miles) to a standard rating of 478 MVA | 2659352.0425 | 10.97% | 24248598.85 | 0.14498
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DUKE2 to GYPSUM2 69kV line 1 | Current Study | Rebuild the DUKE2 to GYPSUM2 69kV line CKT1 (3.6 miles) to a standard rating of 71 MVA | 3272216.4 | 100% | 3272216.4 | 0.05696
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ELDORDJ2 to ELDORDO2 69kV line 1 | Current Study | Rebuild the ELDORDJ2 to ELDORDO2 69kV line CKT1 (11.49 miles) to a standard rating of 71 MVA | 10443824.01 | 100% | 10443824.01 | 0.05696
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ELDORDJ2 to GYPSUM2 69kV line 1 | Current Study | Rebuild the ELDORDJ2 to GYPSUM2 69kV line CKT1 (7.51 miles) to a standard rating of 71 MVA | 6826206.99 | 100% | 6826206.99 | 0.05696
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2082.6393 | 0.2426% | 858333 | 0.0375
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LAKE4WPT to G23-148-TAP 138kV line 1 | Current Study | Rebuild the LAKE4WPT to G23-148-TAP 138kV line CKT1 (18.2 miles) to a standard rating of 286 MVA | 17547693.8 | 100% | 17547693.8 | 0.23154
GEN-2023-148 | 04 SOUTHEAST | TBD | NRIS | Rebuild the LAKEP2WT to ELDORADO2 69kV line 1 | Current Study | Rebuild the LAKEP2WT to ELDORADO2 69kV line CKT1 (16.32 miles) to a standard rating of 71 MVA | 14834047.68 | 100% | 14834047.68 | 0.06162
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSEL4 to G23-148-TAP 138kV line 1 | Current Study | Rebuild the RUSSEL4 to G23-148-TAP 138kV line CKT1 (19.25 miles) to a standard rating of 286 MVA | 18560060.75 | 100% | 18560060.75 | 0.76846
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SNYDER2 to TOMSTEED2 69kV line 1 | Current Study | Rebuild the SNYDER2 to TOMSTEED2 69kV line CKT1 (15.01 miles) to a standard rating of 71 MVA | 13643324.49 | 100% | 13643324.49 | 0.03013
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | REPLACE the breaker at DUKE | Current Study | Replace the existing breaker at DUKE with a standard rating of 71 MVA | 566485 | 100% | 566485 | 0.05696
GEN-2023-148 | 04 SOUTHEAST | TBD | ERIS | Upgrade the RUSSELL2 138/69 kV transformer 1 | Current Study | Upgrade the RUSSELL2 138/69 kV transformer 1 to a standard rating of 250 MVA | 3128743 | 100% | 3128743 | 0.19197
GEN-2023-150 | 04 SOUTHEAST | 158903 | ERIS | Gracemont 138 kV Substation GEN-2023-150 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-150 (150MW/Solar), into Gracemont 138 kV Substation | 2262110 | 100% | 2262110 | 1
GEN-2023-150 | 04 SOUTHEAST | 158902 | ERIS | Gracemont 138 kV Substation GEN-2023-150 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-150 (150MW/Solar), into Gracemont 138 kV Substation | 2663387 | 100% | 2663387 | 1
GEN-2023-150 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2349.9745 | 0.2738% | 858333 | 0.03103
GEN-2023-151 | 04 SOUTHEAST | 158905 | ERIS | South N/Ashville - South Murfreesboro 138kV GEN-2023-151 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-151 (100MW/Hybrid), into South N/Ashville - South Murfreesboro 138kV | 11500000 | 100% | 11500000 | 1
GEN-2023-151 | 04 SOUTHEAST | 158904 | ERIS | South N/Ashville - South Murfreesboro 138kV GEN-2023-151 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-151 (100MW/Hybrid), into South N/Ashville - South Murfreesboro 138kV | 2125000 | 100% | 2125000 | 1
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 360410.3524 | 4.341% | 8302968 | 0.05457
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 23162.5839 | 4.341% | 533608.96 | 0.05457
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 2565.8767 | 3.847% | 66701.12 | 0.02927
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 2565.8767 | 3.847% | 66701.12 | 0.02927
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 142713.816 | 3.846% | 3710249.8 | 0.03991
GEN-2023-152 | 04 SOUTHEAST | 158907 | ERIS | Allen NG4 138 kV Substation GEN-2023-152 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-152 (140MW/Solar), into Allen NG4 138 kV Substation | 10725000 | 100% | 10725000 | 1
GEN-2023-152 | 04 SOUTHEAST | 158906 | ERIS | Allen NG4 138 kV Substation GEN-2023-152 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-152 (140MW/Solar), into Allen NG4 138 kV Substation | 5225000 | 100% | 5225000 | 1
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 4WOODY to PHAROAH4 138kV line 1 | Current Study | Rebuild the 4WOODY to PHAROAH4 138kV line CKT1 (13.36 miles) to a standard rating of 286 MVA | 551271.5338 | 4.28% | 12881164.24 | 0.03291
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ACOPA2 to ACOPT2 69kV line 1 | Current Study | Rebuild the ACOPA2 to ACOPT2 69kV line CKT1 (3.28 miles) to a standard rating of 143 MVA | 623438.5927 | 20.91% | 2981352.72 | 0.0701
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AOCPT2 to LULA2 69kV line 1 | Current Study | Rebuild the AOCPT2 to LULA2 69kV line CKT1 (9.27 miles) to a standard rating of 143 MVA | 1761974.3153 | 20.91% | 8425957.23 | 0.0701
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ATOKA-4 to LEHIGH-4 138kV line 1 | Current Study | Rebuild the ATOKA-4 to LEHIGH-4 138kV line CKT1 (7.99 miles) to a standard rating of 286 MVA | 7703630.41 | 100% | 7703630.41 | 0.10016
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 7716.6587 | 8.893% | 86774.31 | 0.06221
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to BODLE4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to BODLE4 138kV line CKT1 (7.56 miles) to a standard rating of 286 MVA | 128606.9497 | 1.764% | 7289042.04 | 0.0017
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 23149.9761 | 8.893% | 260322.93 | 0.06221
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 905267.5226 | 7.964% | 11367434.61 | 0.06392
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | 96881.6705 | 4.506% | 2150074.57 | 0.04363
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 1572.7083 | 0.1832% | 858333 | 0.02225
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HUGO-2 to VALYTIM2 69kV line 1 | Current Study | Rebuild the HUGO-2 to VALYTIM2 69kV line CKT1 (12.22 miles) to a standard rating of 71 MVA | 1896369.9512 | 17.07% | 11107356.78 | 0.02878
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | Current Study | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | 427317.1286 | 4.504% | 9487324.56 | 0.06382
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to LATTAJT4 138kV line 1 | Current Study | Rebuild the LASALLE4 to LATTAJT4 138kV line CKT1 (7.1 miles) to a standard rating of 286 MVA | 1444556.5276 | 21.1% | 6845528.9 | 0.13576
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | Current Study | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | 1222173.7943 | 20.12% | 6074201.7 | 0.13576
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1 | Current Study | Rebuild the LATTAJT4 to OILCRTP4 138kV line CKT1 (4.55 miles) to a standard rating of 286 MVA | 925736.9297 | 21.1% | 4386923.45 | 0.13576
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 489105.5232 | 7.964% | 6141692.83 | 0.06392
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | 983487.7133 | 25.89% | 3798786.46 | 0.27925
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | Current Study | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | 164150.5523 | 3.218% | 5100401.11 | 0.01965
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PARKLN2 to ADAINDU2 69kV line 1 | Current Study | Rebuild the PARKLN2 to ADAINDU2 69kV line CKT1 (2.87 miles) to a standard rating of 143 MVA | 586225.0674 | 22.47% | 2608683.63 | 0.0701
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PAYNESW4 to PAOLI4 138kV line 1 | Current Study | Rebuild the PAYNESW4 to PAOLI4 138kV line CKT1 (12 miles) to a standard rating of 286 MVA | 942791.9391 | 8.149% | 11569908 | 0.06867
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | Current Study | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | 258482.8167 | 3.218% | 8031444.47 | 0.01965
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 2967.1623 | 3.847% | 77132.72 | 0.02927
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | 526115.2599 | 4.506% | 11675965.49 | 0.04363
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 165030.4727 | 3.846% | 4290507.55 | 0.04789
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 855018.7862 | 6.258% | 13662133.03 | 0.0878
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | Current Study | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | 54305.8691 | 4.506% | 1205198.75 | 0.04363
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to ALLENGT4 138kV line 1 | Current Study | Rebuild the TUPELO4 to ALLENGT4 138kV line CKT1 (0.37 miles) to a standard rating of 286 MVA | 251816.5854 | 70.59% | 356738.83 | 0.89984
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 258849.5659 | 22.75% | 1137707.62 | 0.37835
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VALLYU2 to AOCPA2 69kV line 1 | Current Study | Rebuild the VALLYU2 to AOCPA2 69kV line CKT1 (1.62 miles) to a standard rating of 143 MVA | 330900.5607 | 22.47% | 1472497.38 | 0.0701
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 1356526.2671 | 8.642% | 15696508.52 | 0.14653
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 52246.7532 | 2.068% | 2526096.58 | 0.05969
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Upgrade the ATOKA-4 138/69 kV transformer 1 | Current Study | Upgrade the ATOKA-4 138/69 kV transformer 1 to a standard rating of 250 MVA | 1279288.3365 | 40.89% | 3128743 | 0.05466
GEN-2023-152 | 04 SOUTHEAST | TBD | ERIS | Upgrade the LULA4 138/69 kV transformer 1 | Current Study | Upgrade the LULA4 138/69 kV transformer 1 to a standard rating of 250 MVA | 654259.7659 | 20.91% | 3128743 | 0.0701
GEN-2023-155 | 04 SOUTHEAST | 158913 | ERIS | Longwood - Lieberman 138 kV GEN-2023-155 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-155 (200MW/Solar), into Longwood - Lieberman 138 kV | 11500000 | 100% | 11500000 | 1
GEN-2023-155 | 04 SOUTHEAST | 158912 | ERIS | Longwood - Lieberman 138 kV GEN-2023-155 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-155 (200MW/Solar), into Longwood - Lieberman 138 kV | 1925000 | 100% | 1925000 | 1
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 869.1095 | 1.303% | 66701.12 | 0.00694
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 869.1095 | 1.303% | 66701.12 | 0.00694
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 48325.6148 | 1.302% | 3710249.8 | 0.00946
GEN-2023-156 | 04 SOUTHEAST | 143806 /143815 /143816 /143817 /144173 | ERIS | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild | Contingent | Build new 2.1 mile 138 kV line from Marietta Tap (OKGE) – Marietta Switchyard (WFEC). Convert the Marietta 2 substation from 69 kV to 138 kV and install terminal equipment to support a new 138 kV line from Marietta 4. Rebuild the existing 69 kV line from Rocky Point to Marietta 2 as a 138 kV line. Replace the existing relays at Rocky Point. Install terminal equipment at WFEC Marietta Switch to support a new 138 kV line from OG&E Marietta. (NTC 210656 & 210657) | 0 | 100% | 34759778 | 0.3027
GEN-2023-156 | 04 SOUTHEAST | 158915 | ERIS | Between South Wilson - Ringling 138 kV Line GEN-2023-156 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-156 (200MW/Hybrid), into Between South Wilson - Ringling 138 kV Line | 5000000 | 100% | 5000000 | 1
GEN-2023-156 | 04 SOUTHEAST | 158914 | ERIS | Between South Wilson - Ringling 138 kV Line GEN-2023-156 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-156 (200MW/Hybrid), into Between South Wilson - Ringling 138 kV Line | 500000 | 100% | 500000 | 1
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BASELIN2 to VELMA2 69kV line 1 | Current Study | Rebuild the BASELIN2 to VELMA2 69kV line CKT1 (5.67 miles) to a standard rating of 71 MVA | 5153740.83 | 100% | 5153740.83 | 0.03055
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | 263196.1036 | 12.24% | 2150074.57 | 0.08297
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DUNCNJT2 to HARISBG2 69kV line 1 | Current Study | Rebuild the DUNCNJT2 to HARISBG2 69kV line CKT1 (6.99 miles) to a standard rating of 71 MVA | 6353553.51 | 100% | 6353553.51 | 0.03055
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2767.7646 | 0.3225% | 858333 | 0.02741
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to CHIKSAW4 138kV line 1 | Current Study | Rebuild the FNDTION4 to CHIKSAW4 138kV line CKT1 (1.72 miles) to a standard rating of 286 MVA | 232466.4067 | 14.02% | 1658353.48 | 0.05659
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to SPRNDAL4 138kV line 1 | Current Study | Rebuild the FNDTION4 to SPRNDAL4 138kV line CKT1 (2.58 miles) to a standard rating of 286 MVA | 348699.61 | 14.02% | 2487530.22 | 0.05659
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HLDTNTP4 to LOCO4 138kV line 1 | Current Study | Rebuild the HLDTNTP4 to LOCO4 138kV line CKT1 (12.85 miles) to a standard rating of 286 MVA | 10097844.0878 | 81.5% | 12389443.15 | 0.60533
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HRSBGSW2 to HARISBG2 69kV line 1 | Current Study | Rebuild the HRSBGSW2 to HARISBG2 69kV line CKT1 (4.05 miles) to a standard rating of 71 MVA | 3681243.45 | 100% | 3681243.45 | 0.03055
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HRSBGSW2 to VELMA2 69kV line 1 | Current Study | Rebuild the HRSBGSW2 to VELMA2 69kV line CKT1 (2.95 miles) to a standard rating of 71 MVA | 2681399.55 | 100% | 2681399.55 | 0.03055
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | Current Study | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | 981966.6119 | 10.35% | 9487324.56 | 0.10266
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | Current Study | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | 1966823.1566 | 38.56% | 5100401.11 | 0.16481
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PAYNESW4 to PAOLI4 138kV line 1 | Current Study | Rebuild the PAYNESW4 to PAOLI4 138kV line CKT1 (12 miles) to a standard rating of 286 MVA | 2364187.7371 | 20.43% | 11569908 | 0.12054
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | Current Study | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | 3097095.8212 | 38.56% | 8031444.47 | 0.16481
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 1005.0323 | 1.303% | 77132.72 | 0.00694
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | 1429284.6703 | 12.24% | 11675965.49 | 0.08297
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 55874.9475 | 1.302% | 4290507.55 | 0.01135
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 289504.4084 | 2.119% | 13662133.03 | 0.02081
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | Current Study | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | 147531.4482 | 12.24% | 1205198.75 | 0.08297
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 6167.1572 | 0.5421% | 1137707.62 | 0.00631
GEN-2023-156 | 04 SOUTHEAST | TBD | ERIS | Upgrade the BASELIN2 138/69 kV transformer 1 | Current Study | Upgrade the BASELIN2 138/69 kV transformer 1 to a standard rating of 250 MVA | 3128743 | 100% | 3128743 | 0.06849
GEN-2023-161 | 04 SOUTHEAST | TBD | ERIS | Build a new ELKCITY to G22-145-TAP 138kV line 1 | Current Study | Build a new ELKCITY to G22-145-TAP 138kV line CKT1 (49.812 miles) to a standard rating of 286 MVA | 7840633.7606 | 18.88% | 41531452.37 | 0.03839
GEN-2023-161 | 04 SOUTHEAST | 158923 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | 1540091 | 100% | 1540091 | 1
GEN-2023-161 | 04 SOUTHEAST | 158922 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | 1231357 | 100% | 1231357 | 1
GEN-2023-161 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 1180.2274 | 0.1375% | 858333 | 0.03121
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Build a new Grove 161/138 kV transformer 2 | Current Study | Build a new Grove 161/138 kV transformer 2 | 1562811.4153 | 43.34% | 3606166 | 0.18674
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Build a new GROVE 161/138 kV transformer 3 | Current Study | Build a new GROVE 161/138 kV transformer 3 to a standard rating of 112 MVA | 2124338.9238 | 58.91% | 3606166 | 0.18674
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | Current Study | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | 458697.2362 | 7.833% | 5856160.8 | 0.05457
GEN-2023-162 | 04 SOUTHEAST | 158925 | ERIS | Grove - Jay 138 kV Line GEN-2023-162 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-162 (100MW/Hybrid), into Grove - Jay 138 kV Line | 11500000 | 100% | 11500000 | 1
GEN-2023-162 | 04 SOUTHEAST | 158924 | ERIS | Grove - Jay 138 kV Line GEN-2023-162 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-162 (100MW/Hybrid), into Grove - Jay 138 kV Line | 2125000 | 100% | 2125000 | 1
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the ADAIR2 to VINITA 2 line 69kV | Current Study | Rebuild the ADAIR2 to VINITA 2 line 69kV (19.11 miles) to a standard rating of 71 MVA | 1646855.9767 | 9.481% | 17370015.39 | 0.02786
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 752057.0161 | 2.65% | 28382211.2 | 0.05865
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 213437.7915 | 2.234% | 9556107.4 | 0.05865
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 139166.9666 | 0.7948% | 17509993.2 | 0.05865
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 1412253.1576 | 3.521% | 40112762.2 | 0.05865
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GROVE4 to G23-162-TAP 138kV line 1 | Current Study | Rebuild the GROVE4 to G23-162-TAP 138kV line CKT1 (10.53 miles) to a standard rating of 286 MVA | 6005299.2533 | 59.15% | 10152594.27 | 0.62784
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEO1845 to NOL4355 161kV line 1 | Current Study | Rebuild the NEO1845 to NOL4355 161kV line CKT1 (23.13 miles) to a standard rating of 557 MVA | 8158955.5289 | 36.06% | 22626321.12 | 0.24247
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PCP-TAP2 to HUNTAP-2 69kV line 1 | Current Study | Rebuild the PCP-TAP2 to HUNTAP-2 161kV line CKT1 (3.07 miles) to a standard rating of 71 MVA | 484293.9379 | 17.36% | 2790473.43 | 0.03224
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PCP-TAP2 to PRYORC12 69kV line 1 | Current Study | Rebuild the PCP-TAP2 to PRYORC12 69kV line CKT1 (3.03 miles) to a standard rating of 71 MVA | 477983.9192 | 17.36% | 2754115.47 | 0.03224
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PRY-JCT2 to PRYORC12 69kV line 1 | Current Study | Rebuild the PRY-JCT2 to PRYORC12 69kV line CKT1 (4.65 miles) to a standard rating of 122 MVA | 725586.827 | 17.17% | 4226612.85 | 0.06778
GEN-2023-162 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PRY-JCT4 to G23-027-TAP 138kV line 1 | Current Study | Rebuild the PRY-JCT4 to G23-027-TAP line CKT1 (6.77 miles) to a standard rating of 286 MVA | 1636323.8731 | 25.07% | 6527356.43 | 0.37216
GEN-2023-164 | 04 SOUTHEAST | 158928 | ERIS | Gracemont 345 kV Substation GEN-2023-164 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164 (210MW/Battery/Storage), into Gracemont 345 kV Substation | 1960313 | 100% | 1960313 | 1
GEN-2023-164 | 04 SOUTHEAST | 158664 | ERIS | Gracemont 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164/165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | 2292428 | 50% | 4584856 | 1
GEN-2023-164 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3331.3142 | 0.3881% | 858333 | 0.03142
GEN-2023-165 | 04 SOUTHEAST | 158664 | ERIS | Gracemont 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164/165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | 2292428 | 50% | 4584856 | 1
GEN-2023-165 | 04 SOUTHEAST | 158929 | ERIS | Gracemont 345 kV Substation GEN-2023-165 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | 1960313 | 100% | 1960313 | 1
GEN-2023-165 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3331.3142 | 0.3881% | 858333 | 0.03142
GEN-2023-166 | 04 SOUTHEAST | 158931 | ERIS | 84th Street - Tennessee Tap 138 kV Line GEN-2023-166 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-166 (150MW/Battery/Storage), into 84th Street - Tennessee Tap 138 kV Line | 10000000 | 100% | 10000000 | 1
GEN-2023-166 | 04 SOUTHEAST | 158930 | ERIS | 84th Street - Tennessee Tap 138 kV Line GEN-2023-166 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-166 (150MW/Battery/Storage), into 84th Street - Tennessee Tap 138 kV Line | 3500000 | 100% | 3500000 | 1
GEN-2023-166 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 1985.702 | 0.2313% | 858333 | 0.02622
GEN-2023-167 | 04 SOUTHEAST | 158933 | ERIS | Washington Park 138 kV Substation GEN-2023-167 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-167 (250MW/Battery/Storage), into Washington Park 138 kV Substation | 1190091 | 100% | 1190091 | 1
GEN-2023-167 | 04 SOUTHEAST | 158932 | ERIS | Washington Park 138 kV Substation GEN-2023-167 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-167 (250MW/Battery/Storage), into Washington Park 138 kV Substation | 981357 | 100% | 981357 | 1
GEN-2023-167 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3319.6009 | 0.3867% | 858333 | 0.0263
GEN-2023-168 | 04 SOUTHEAST | 158935 | ERIS | Classen 138 kV Substation GEN-2023-168 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-168 (175MW/Battery/Storage), into Classen 138 kV Substation | 10000000 | 100% | 10000000 | 1
GEN-2023-168 | 04 SOUTHEAST | 158934 | ERIS | Classen 138 kV Substation GEN-2023-168 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-168 (175MW/Battery/Storage), into Classen 138 kV Substation | 2000000 | 100% | 2000000 | 1
GEN-2023-168 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2360.8295 | 0.275% | 858333 | 0.02672
GEN-2023-174 | 04 SOUTHEAST | 158945 | ERIS | Paoli West 138 kV Substation GEN-2023-174 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-174 (150MW/Battery/Storage), into Paoli West 138 kV Substation | 10000000 | 100% | 10000000 | 1
GEN-2023-174 | 04 SOUTHEAST | 158944 | ERIS | Paoli West 138 kV Substation GEN-2023-174 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-174 (150MW/Battery/Storage), into Paoli West 138 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-174 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2070.5222 | 0.2412% | 858333 | 0.02734
GEN-2023-174 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | 210898.3053 | 5.552% | 3798786.46 | 0.05589
GEN-2023-174 | 04 SOUTHEAST | TBD | ERIS | Rebuild the PAYNESW4 to PAOLI4 138kV line 1 | Current Study | Rebuild the PAYNESW4 to PAOLI4 138kV line CKT1 (12 miles) to a standard rating of 286 MVA | 5726153.3128 | 49.49% | 11569908 | 0.38927
GEN-2023-174 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 326332.8391 | 2.079% | 15696508.52 | 0.0329
GEN-2023-177 | 04 SOUTHEAST | 158950 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | 2338281 | 100% | 2338281 | 1
GEN-2023-177 | 04 SOUTHEAST | 158949 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | 3924886 | 100% | 3924886 | 1
GEN-2023-177 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2706.1689 | 0.3153% | 858333 | 0.0268
GEN-2023-180 | 04 SOUTHEAST | 158954 | ERIS | Hackett - N Huntington 161 kV Line Tap GEN-2023-180 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-180 (150MW/Solar), into Hackett - N Huntington 161 kV Line Tap | 11650000 | 100% | 11650000 | 1
GEN-2023-180 | 04 SOUTHEAST | 158953 | ERIS | Hackett - N Huntington 161 kV Line Tap GEN-2023-180 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-180 (150MW/Solar), into Hackett - N Huntington 161 kV Line Tap | 1950000 | 100% | 1950000 | 1
GEN-2023-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FTGIB5 to OKAYGR5 161kV line 1 | Current Study | Rebuild the FTGIB5 to OKAYGR5 161kV line CKT1 (5.9 miles) to a standard rating of 557 MVA | 633912.8635 | 10.98% | 5771521.6 | 0.02842
GEN-2023-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to G23-145-TAP 161kV line 1 | Current Study | Rebuild the GORE5 to G23-145-TAP 161kV line CKT1 (9.2 miles) to a standard rating of 557 MVA | 317429.7427 | 3.527% | 8999660.8 | 0.04001
GEN-2023-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 966999.06 | 6.178% | 15651584 | 0.07968
GEN-2023-180 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VANBUR5 to VBI5 161kV line Z1 | Current Study | Rebuild the VANBUR5 to VBI5 161kV line CKTZ1 (0.22 miles) to a standard rating of 557 MVA | 9765.6148 | 4.538% | 215209.28 | 0.07132
GEN-2023-193 | 04 SOUTHEAST | 158972 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | 11500000 | 100% | 11500000 | 1
GEN-2023-193 | 04 SOUTHEAST | 158971 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | 2125000 | 100% | 2125000 | 1
GEN-2023-204 | 04 SOUTHEAST | 158992 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | 18100000 | 100% | 18100000 | 1
GEN-2023-204 | 04 SOUTHEAST | 158991 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | 3275000 | 100% | 3275000 | 1
GEN-2023-205 | 04 SOUTHEAST | 158994 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | 11500000 | 100% | 11500000 | 1
GEN-2023-205 | 04 SOUTHEAST | 158993 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | 1925000 | 100% | 1925000 | 1
GEN-2023-205 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 4WOODY to PHAROAH4 138kV line 1 | Current Study | Rebuild the 4WOODY to PHAROAH4 138kV line CKT1 (13.36 miles) to a standard rating of 286 MVA | 1937885.6339 | 15.04% | 12881164.24 | 0.08998
GEN-2023-205 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 818745.2885 | 5.231% | 15651584 | 0.05622
GEN-2023-205 | 04 SOUTHEAST | TBD | ERIS | Rebuild the OKMULGE4 to KELCO4 138kV line 1 | Current Study | Rebuild the OKMULGE4 to KELCO4 138kV line CKT1 (2.24 miles) to a standard rating of 286 MVA | 443800.8861 | 20.55% | 2159716.16 | 0.09633
GEN-2023-205 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 46391.4875 | 4.078% | 1137707.62 | 0.05274
GEN-2023-205 | 04 SOUTHEAST | TBD | ERIS | Rebuild the VANBUR5 to VBI5 161kV line Z1 | Current Study | Rebuild the VANBUR5 to VBI5 161kV line CKTZ1 (0.22 miles) to a standard rating of 557 MVA | 5050.9534 | 2.347% | 215209.28 | 0.03074
GEN-2023-205 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 435345.0112 | 17.23% | 2526096.58 | 0.38684
GEN-2023-205 | 04 SOUTHEAST | TBD | ERIS | Upgrade the WELEETK5 161/138 kV transformer 1 | Current Study | Upgrade the WELEETK5 161/138 kV transformer 1 to a standard rating of 200 MVA | 603535.9134 | 16.74% | 3606166 | 0.06858
GEN-2023-206 | 04 SOUTHEAST | 158996 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | 20000 | 100% | 20000 | 1
GEN-2023-206 | 04 SOUTHEAST | 158995 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | 20000 | 100% | 20000 | 1
GEN-2023-206 | 04 SOUTHEAST | TBD | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | Current Study | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | 295795.5625 | 1.89% | 15651584 | 0.07312
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 139096.5633 | 1.675% | 8302968 | 0.05897
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 8939.3543 | 1.675% | 533608.96 | 0.05897
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 3779.8123 | 5.667% | 66701.12 | 0.12073
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 3779.8123 | 5.667% | 66701.12 | 0.12073
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 210249.6289 | 5.667% | 3710249.8 | 0.16463
GEN-2023-207 | 04 SOUTHEAST | 158998 | ERIS | Colbert 138 kV Substation GEN-2023-207 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-207 (50MW/Battery/Storage), into Colbert 138 kV Substation | 0 | 100% | 0 | 1
GEN-2023-207 | 04 SOUTHEAST | 158997 | ERIS | Colbert 138 kV Substation GEN-2023-207 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-207 (50MW/Battery/Storage), into Colbert 138 kV Substation | 50000 | 100% | 50000 | 1
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 1275.8615 | 1.47% | 86774.31 | 0.0288
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to BODLE4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to BODLE4 138kV line CKT1 (7.56 miles) to a standard rating of 286 MVA | 6596239.644 | 90.5% | 7289042.04 | 0.24414
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 3827.5846 | 1.47% | 260322.93 | 0.0288
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 1380541.0648 | 12.14% | 11367434.61 | 0.27294
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line CKT1 (0.17 miles) to a standard rating of 286 MVA | 19809.7039 | 12.09% | 163907.03 | 0.06045
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the COLBRT-4 to COLBERT4 138kV line 1 | Current Study | Rebuild the COLBRT-4 to COLBERT4 138kV line CKT1 (1.01 miles) to a standard rating of 478 MVA | 973800.59 | 100% | 973800.59 | 0.48983
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | 143033.775 | 6.653% | 2150074.57 | 0.18036
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 605.6063 | 0.07056% | 858333 | 0.02399
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to CHIKSAW4 138kV line 1 | Current Study | Rebuild the FNDTION4 to CHIKSAW4 138kV line CKT1 (1.72 miles) to a standard rating of 286 MVA | 125671.1176 | 7.578% | 1658353.48 | 0.12237
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to SPRNDAL4 138kV line 1 | Current Study | Rebuild the FNDTION4 to SPRNDAL4 138kV line CKT1 (2.58 miles) to a standard rating of 286 MVA | 188506.6764 | 7.578% | 2487530.22 | 0.12237
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HLDTNTP4 to LOCO4 138kV line 1 | Current Study | Rebuild the HLDTNTP4 to LOCO4 138kV line CKT1 (12.85 miles) to a standard rating of 286 MVA | 252099.96 | 2.035% | 12389443.15 | 0.06045
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | Current Study | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | 616240.0056 | 6.495% | 9487324.56 | 0.2577
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to LATTAJT4 138kV line 1 | Current Study | Rebuild the LASALLE4 to LATTAJT4 138kV line CKT1 (7.1 miles) to a standard rating of 286 MVA | 142202.9034 | 2.077% | 6845528.9 | 0.03742
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | Current Study | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | 120311.4303 | 1.981% | 6074201.7 | 0.03742
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1 | Current Study | Rebuild the LATTAJT4 to OILCRTP4 138kV line CKT1 (4.55 miles) to a standard rating of 286 MVA | 91130.0296 | 2.077% | 4386923.45 | 0.03742
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 745890.2954 | 12.14% | 6141692.83 | 0.27294
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | 91858.4316 | 2.418% | 3798786.46 | 0.07303
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | Current Study | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | 226385.7489 | 4.439% | 5100401.11 | 0.07588
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | Current Study | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | 356482.6632 | 4.439% | 8031444.47 | 0.07588
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 4370.9491 | 5.667% | 77132.72 | 0.12073
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | 776743.9531 | 6.653% | 11675965.49 | 0.18036
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 243129.8652 | 5.667% | 4290507.55 | 0.19755
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 1259643.2801 | 9.22% | 13662133.03 | 0.36218
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | Current Study | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | 80175.8829 | 6.653% | 1205198.75 | 0.18036
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 24478.0433 | 2.152% | 1137707.62 | 0.10018
GEN-2023-207 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 166604.9824 | 1.061% | 15696508.52 | 0.05039
GEN-2023-210 | 04 SOUTHEAST | 159004 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | 4999999 | 100% | 4999999 | 1
GEN-2023-210 | 04 SOUTHEAST | 159003 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | 500000 | 100% | 500000 | 1
GEN-2023-210 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 4WOODY to PHAROAH4 138kV line 1 | Current Study | Rebuild the 4WOODY to PHAROAH4 138kV line CKT1 (13.36 miles) to a standard rating of 286 MVA | 1071576.6688 | 8.319% | 12881164.24 | 0.04689
GEN-2023-210 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2108.0147 | 0.2456% | 858333 | 0.02186
GEN-2023-210 | 04 SOUTHEAST | TBD | ERIS | Rebuild the OKMULGE4 to KELCO4 138kV line 1 | Current Study | Rebuild the OKMULGE4 to KELCO4 138kV line CKT1 (2.24 miles) to a standard rating of 286 MVA | 171053.2812 | 7.92% | 2159716.16 | 0.03499
GEN-2023-210 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | Current Study | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | 171624.8885 | 6.794% | 2526096.58 | 0.14372
GEN-2023-210 | 04 SOUTHEAST | TBD | ERIS | Upgrade the WELEETK5 161/138 kV transformer 1 | Current Study | Upgrade the WELEETK5 161/138 kV transformer 1 to a standard rating of 200 MVA | 356068.2946 | 9.874% | 3606166 | 0.03813
GEN-2023-211 | 04 SOUTHEAST | TBD | ERIS | Build a new HANNA to WELEETK 138kV line 1 | Current Study | Build a new HANNA to WELEETK 138kV line CKT1 (21.204 miles) to a standard rating of 478 MVA | 51559.1568 | 0.2286% | 17679131.86 | 0.00082
GEN-2023-211 | 04 SOUTHEAST | 159006 | ERIS | Ranch Road 345 kV Substation GEN-2023-211 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-211 (250MW/Hybrid), into Ranch Road 345 kV Substation | 20000 | 100% | 20000 | 1
GEN-2023-211 | 04 SOUTHEAST | 159005 | ERIS | Ranch Road 345 kV Substation GEN-2023-211 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-211 (250MW/Hybrid), into Ranch Road 345 kV Substation | 20000 | 100% | 20000 | 1
GEN-2023-212 | 04 SOUTHEAST | 159008 | ERIS | Northwest TexarkaN/A - Valliant 345 kV Line GEN-2023-212 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-212 (400MW/Hybrid), into Northwest TexarkaN/A - Valliant 345 kV Line | 18100000 | 100% | 18100000 | 1
GEN-2023-212 | 04 SOUTHEAST | 159007 | ERIS | Northwest TexarkaN/A - Valliant 345 kV Line GEN-2023-212 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-212 (400MW/Hybrid), into Northwest TexarkaN/A - Valliant 345 kV Line | 3275000 | 100% | 3275000 | 1
GEN-2023-212 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NNBOSTN4 to G18-003-TAP 138kV line 1 | Current Study | Rebuild the NNBOSTN4 to G18-003-TAP 138kV line CKT1 (1.7 miles) to a standard rating of 478 MVA | 227041.5099 | 13.85% | 1639070.3 | 0.03163
GEN-2023-213 | 04 SOUTHEAST | TBD | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | Current Study | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | 210225.7262 | 3.59% | 5856160.8 | 0.02501
GEN-2023-213 | 04 SOUTHEAST | 159010 | ERIS | Chamber Springs 161 kV Substation GEN-2023-213 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-213 (100MW/Battery/Storage), into Chamber Springs 161 kV Substation | 2250000 | 100% | 2250000 | 1
GEN-2023-213 | 04 SOUTHEAST | 159009 | ERIS | Chamber Springs 161 kV Substation GEN-2023-213 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-213 (100MW/Battery/Storage), into Chamber Springs 161 kV Substation | 2525000 | 100% | 2525000 | 1
GEN-2023-213 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AVOCA5 to BEAVER5 161kV line 1 | Current Study | Rebuild the AVOCA5 to BEAVER5 161kV line CKT1 (11 miles) to a standard rating of 557 MVA | 2308582.6727 | 21.45% | 10760464 | 0.09052
GEN-2023-213 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AVOCA5 to EROGERS5 161kV line 1 | Current Study | Rebuild the AVOCA5 to EROGERS5 161kV line CKT1 (5.81 miles) to a standard rating of 557 MVA | 1219351.3935 | 21.45% | 5683481.44 | 0.09052
GEN-2023-213 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 662553.8964 | 2.334% | 28382211.2 | 0.05167
GEN-2023-213 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 188036.3288 | 1.968% | 9556107.4 | 0.05167
GEN-2023-213 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 122604.5553 | 0.7002% | 17509993.2 | 0.05167
GEN-2023-213 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 1244179.3803 | 3.102% | 40112762.2 | 0.05167
GEN-2023-213 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEO1845 to NOL4355 161kV line 1 | Current Study | Rebuild the NEO1845 to NOL4355 161kV line CKT1 (23.13 miles) to a standard rating of 557 MVA | 1849367.7398 | 8.174% | 22626321.12 | 0.05496
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGO7 345/138 kV transformer 2 | Current Study | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | 278476.1787 | 3.354% | 8302968 | 0.05903
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | Current Study | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | 17896.8995 | 3.354% | 533608.96 | 0.05903
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | 7573.4 | 11.35% | 66701.12 | 0.12095
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | Current Study | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | 7573.4 | 11.35% | 66701.12 | 0.12095
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | Current Study | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | 421265.5202 | 11.35% | 3710249.8 | 0.16493
GEN-2023-214 | 04 SOUTHEAST | 159012 | ERIS | Brown 138 kV Substation GEN-2023-214 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-214 (100MW/Battery/Storage), into Brown 138 kV Substation | 2338281 | 100% | 2338281 | 1
GEN-2023-214 | 04 SOUTHEAST | 159011 | ERIS | Brown 138 kV Substation GEN-2023-214 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-214 (100MW/Battery/Storage), into Brown 138 kV Substation | 3924886 | 100% | 3924886 | 1
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | 23811.6521 | 27.44% | 86774.31 | 0.26875
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to BODLE4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to BODLE4 138kV line CKT1 (7.56 miles) to a standard rating of 286 MVA | 172916.9072 | 2.372% | 7289042.04 | 0.0032
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | Current Study | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | 71434.9563 | 27.44% | 260322.93 | 0.26875
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | 2750966.0523 | 24.2% | 11367434.61 | 0.27194
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line 1 | Current Study | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line CKT1 (0.17 miles) to a standard rating of 286 MVA | 39560.421 | 24.14% | 163907.03 | 0.06036
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | 286051.6891 | 13.3% | 2150074.57 | 0.18035
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 1210.7077 | 0.1411% | 858333 | 0.02398
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to CHIKSAW4 138kV line 1 | Current Study | Rebuild the FNDTION4 to CHIKSAW4 138kV line CKT1 (1.72 miles) to a standard rating of 286 MVA | 251321.6957 | 15.15% | 1658353.48 | 0.12236
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FNDTION4 to SPRNDAL4 138kV line 1 | Current Study | Rebuild the FNDTION4 to SPRNDAL4 138kV line CKT1 (2.58 miles) to a standard rating of 286 MVA | 376982.5435 | 15.15% | 2487530.22 | 0.12236
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the HLDTNTP4 to LOCO4 138kV line 1 | Current Study | Rebuild the HLDTNTP4 to LOCO4 138kV line CKT1 (12.85 miles) to a standard rating of 286 MVA | 503449.2501 | 4.064% | 12389443.15 | 0.06036
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | Current Study | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | 1232814.7942 | 12.99% | 9487324.56 | 0.25777
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to LATTAJT4 138kV line 1 | Current Study | Rebuild the LASALLE4 to LATTAJT4 138kV line CKT1 (7.1 miles) to a standard rating of 286 MVA | 284785.8253 | 4.16% | 6845528.9 | 0.03747
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | Current Study | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | 240944.377 | 3.967% | 6074201.7 | 0.03747
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1 | Current Study | Rebuild the LATTAJT4 to OILCRTP4 138kV line CKT1 (4.55 miles) to a standard rating of 286 MVA | 182503.5922 | 4.16% | 4386923.45 | 0.03747
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | Current Study | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | 1486314.9918 | 24.2% | 6141692.83 | 0.27194
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | 183918.1141 | 4.841% | 3798786.46 | 0.07311
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | Current Study | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | 449191.3331 | 8.807% | 5100401.11 | 0.07528
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | Current Study | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | 707327.7514 | 8.807% | 8031444.47 | 0.07528
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | 8757.8281 | 11.35% | 77132.72 | 0.12095
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | Current Study | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | 1553401.7735 | 13.3% | 11675965.49 | 0.18035
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | 487145.8529 | 11.35% | 4290507.55 | 0.19791
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | Current Study | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | 2523877.4519 | 18.47% | 13662133.03 | 0.36284
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | Current Study | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | 160342.8751 | 13.3% | 1205198.75 | 0.18035
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | Current Study | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | 49009.8415 | 4.308% | 1137707.62 | 0.10029
GEN-2023-214 | 04 SOUTHEAST | TBD | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | Current Study | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | 333474.4696 | 2.125% | 15696508.52 | 0.05043
GEN-2023-227 | 04 SOUTHEAST | 159029 | ERIS | Petty to Chapel 138 kV Line GEN-2023-227 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-227 (200MW/Battery/Storage), into Petty to Chapel 138 kV Line | 11500000 | 100% | 11500000 | 1
GEN-2023-227 | 04 SOUTHEAST | 159028 | ERIS | Petty to Chapel 138 kV Line GEN-2023-227 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-227 (200MW/Battery/Storage), into Petty to Chapel 138 kV Line | 1925000 | 100% | 1925000 | 1
GEN-2023-229 | 04 SOUTHEAST | 159033 | ERIS | Southwestern Power Station 138 kV Sub (SWS4) GEN-2023-229 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | 800000 | 100% | 800000 | 1
GEN-2023-229 | 04 SOUTHEAST | 159032 | ERIS | Southwestern Power Station 138 kV Substation (SWS4) GEN-2023-229 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | 1825000 | 100% | 1825000 | 1
GEN-2023-229 | 04 SOUTHEAST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2213.3029 | 0.2579% | 858333 | 0.01906
GEN-2023-230 | 04 SOUTHEAST | 159035 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | 1850000 | 100% | 1850000 | 1
GEN-2023-230 | 04 SOUTHEAST | 159034 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | 2275000 | 100% | 2275000 | 1
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Build a new CHAMSPR5 345/161 kV transformer 2 | Current Study | Build a new CHAMSPR5 345/161 kV transformer 2 to a standard rating of 675 MVA | 8302968 | 100% | 8302968 | 0.17644
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | Current Study | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | 446971.331 | 7.632% | 5856160.8 | 0.02127
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Build a new TONTITN7 345/161 kV transformer 2 | Current Study | Build a new TONTITN7 345/161 kV transformer 2 to a standard rating of 675 MVA | 8302968 | 100% | 8302968 | 0.11381
GEN-2023-235 | 04 SOUTHEAST | 159039 | ERIS | Chamber Springs 345 kV Substation GEN-2023-235 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-235 (250MW/Battery/Storage), into Chamber Springs 345 kV Substation | 5200000 | 100% | 5200000 | 1
GEN-2023-235 | 04 SOUTHEAST | 159038 | ERIS | Chamber Springs 345 kV Substation GEN-2023-235 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-235 (250MW/Battery/Storage), into Chamber Springs 345 kV Substation | 2825000 | 100% | 2825000 | 1
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AVOCA5 to BEAVER5 161kV line 1 | Current Study | Rebuild the AVOCA5 to BEAVER5 161kV line CKT1 (11 miles) to a standard rating of 557 MVA | 5752329.0083 | 53.46% | 10760464 | 0.09022
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild the AVOCA5 to EROGERS5 161kV line 1 | Current Study | Rebuild the AVOCA5 to EROGERS5 161kV line CKT1 (5.81 miles) to a standard rating of 557 MVA | 3038275.5944 | 53.46% | 5683481.44 | 0.09022
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | 1628174.5886 | 5.737% | 28382211.2 | 0.05079
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | 462084.6304 | 4.835% | 9556107.4 | 0.05079
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | Current Study | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | 301291.1439 | 1.721% | 17509993.2 | 0.05079
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | Current Study | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | 3057473.9077 | 7.622% | 40112762.2 | 0.05079
GEN-2023-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEO1845 to NOL4355 161kV line 1 | Current Study | Rebuild the NEO1845 to NOL4355 161kV line CKT1 (23.13 miles) to a standard rating of 557 MVA | 4098489.6417 | 18.11% | 22626321.12 | 0.04872
GEN-2023-241 | 04 SOUTHEAST | 159051 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | 3425000 | 100% | 3425000 | 1
GEN-2023-241 | 04 SOUTHEAST | 159050 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | 2025000 | 100% | 2025000 | 1
ASGI-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | Current Study | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | 26108.4322 | 0.1652% | 15802413.9 | 0.02402
ASGI-2023-001 | 05 SOUTHWEST | 158657 | ERIS | Chevron Green 115 kV Substation ASGI-2023-001 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ASGI-2023-001 (20MW/Solar), into Chevron Green 115 kV Substation ($0 assigned because request is not interconnecting to SPP facilities) | 0 | 100% | 0 | 1
ASGI-2023-001 | 05 SOUTHWEST | 158656 | ERIS | Chevron Green 115 kV Substation ASGI-2023-001 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ASGI-2023-001 (20MW/Solar), into Chevron Green 115 kV Substation ($0 assigned because request is not interconnecting to SPP facilities) | 0 | 100% | 0 | 1
ASGI-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | Current Study | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | 364111.4511 | 0.7208% | 50515758.16 | 0.0354
ASGI-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 528.3088 | 0.06155% | 858333 | 0.05232
ASGI-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 54190.7367 | 0.08171% | 66320529.8 | 0.05117
ASGI-2023-001 | 05 SOUTHWEST | TBD | NRIS | Rebuild the RED_BLUFF3 to RDRUNNER3 115kV line 1 | Current Study | Rebuild the RED_BLUFF3 to RDRUNNER3 115kV line CKT1 (11.54 miles) to a standard rating of 239 MVA | 379982.7826 | 4.632% | 8203093.6 | 0.06972
ASGI-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the TOLK to NEEDMORE 230 kV line 1 | Current Study | Rebuild the TOLK to NEEDMORE 230 kV line CKT1 (13.65 miles) to a standard rating of 796 MVA | 21249.3352 | 0.1762% | 12059897.85 | 0.02402
GEN-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | Current Study | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | 480620.1498 | 3.041% | 15802413.9 | 0.03845
GEN-2023-001 | 05 SOUTHWEST | 158680 | ERIS | T14 Circuit 115 V Line GEN-2023-001 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-001 (230MW/Solar), into T14 Circuit 115 V Line | 0 | 100% | 0 | 1
GEN-2023-001 | 05 SOUTHWEST | 158679 | ERIS | T14 Circuit 115 V Line GEN-2023-001 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-001 (230MW/Solar), into T14 Circuit 115 V Line | 0 | 100% | 0 | 1
GEN-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | Current Study | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | 4095019.5486 | 8.106% | 50515758.16 | 0.03462
GEN-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 6101.0983 | 0.7108% | 858333 | 0.05254
GEN-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 625629.2484 | 0.9433% | 66320529.8 | 0.05137
GEN-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the TAYLOR to W_BENDER 115kV line 1 | Current Study | Rebuild the TAYLOR to W_BENDER 115kV line CKT1 (6.4 miles) to a standard rating of 239 MVA | 4549376 | 100% | 4549376 | 0.14098
GEN-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the TOLK to NEEDMORE 230 kV line 1 | Current Study | Rebuild the TOLK to NEEDMORE 230 kV line CKT1 (13.65 miles) to a standard rating of 796 MVA | 391170.8903 | 3.244% | 12059897.85 | 0.03845
GEN-2023-005 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 231780.3964 | 2.792% | 8302968 | 0.03231
GEN-2023-005 | 05 SOUTHWEST | 158685 | ERIS | Plant X 230 kV Substation GEN-2023-005 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005 (256MW/Solar), into Plant X 230kV Substation | 1700000 | 100% | 1700000 | 1
GEN-2023-005 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 16072105.6721 | 19.89% | 80800000 | 1
GEN-2023-005 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7447.3769 | 0.8677% | 858333 | 0.05762
GEN-2023-005 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 756268.4258 | 1.14% | 66320529.8 | 0.05579
GEN-2023-005 | 05 SOUTHWEST | TBD | ERIS | Upgrade the PLANTX 230/115kV transformer 1 | Current Study | Upgrade the PLANTX 230/115kV transformer 1 to a standard rating of 308 MVA | 1311146.0773 | 19.8% | 6621188 | 0.06124
GEN-2023-008 | 05 SOUTHWEST | 158689 | ERIS | Tuco - Carlisle 230 kV line GEN-2023-008 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-008 (75MW/Solar), into Tuco - Carlisle 230 kV line | 0 | 100% | 0 | 1
GEN-2023-008 | 05 SOUTHWEST | 158688 | ERIS | Tuco - Carlisle 230 kV line GEN-2023-008 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-008 (75MW/Solar), into Tuco - Carlisle 230 kV line | 0 | 100% | 0 | 1
GEN-2023-008 | 05 SOUTHWEST | TBD | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | Current Study | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | 1321446.8553 | 2.616% | 50515758.16 | 0.03426
GEN-2023-008 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 1928.524 | 0.2247% | 858333 | 0.05093
GEN-2023-008 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 198687.8949 | 0.2996% | 66320529.8 | 0.05003
GEN-2023-010 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 734323.212 | 8.844% | 8302968 | 0.09359
GEN-2023-010 | 05 SOUTHWEST | 158693 | ERIS | Moore Co 230 kV Substation GEN-2023-010 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-010 (280MW/Wind), into Moore Co 230 kV Substation | 2485000 | 100% | 2485000 | 1
GEN-2023-010 | 05 SOUTHWEST | 158692 | ERIS | Moore Co 230 kV Substation GEN-2023-010 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-010 (280MW/Wind), into Moore Co 230 kV Substation | 1700000 | 100% | 1700000 | 1
GEN-2023-010 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 9432.0085 | 1.099% | 858333 | 0.06672
GEN-2023-010 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 811452.5357 | 1.224% | 66320529.8 | 0.05473
GEN-2023-060 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 231780.3964 | 2.792% | 8302968 | 0.03231
GEN-2023-060 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 16072105.6721 | 19.89% | 80800000 | 1
GEN-2023-060 | 05 SOUTHWEST | 158776 | ERIS | Plant X 230 kV Substation GEN-2023-060 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-060 (256MW/Solar), into Plant X 230kV Substation | 1700000 | 100% | 1700000 | 1
GEN-2023-060 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7447.3769 | 0.8677% | 858333 | 0.05762
GEN-2023-060 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 756268.4258 | 1.14% | 66320529.8 | 0.05579
GEN-2023-060 | 05 SOUTHWEST | TBD | ERIS | Upgrade the PLANTX 230/115kV transformer 1 | Current Study | Upgrade the PLANTX 230/115kV transformer 1 to a standard rating of 308 MVA | 1311146.0773 | 19.8% | 6621188 | 0.06124
GEN-2023-081 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | Current Study | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | 635863.1484 | 4.024% | 15802413.9 | 0.01872
GEN-2023-081 | 05 SOUTHWEST | 158808 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-081 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-081 (625MW/Hybrid), into Crossroads - Hobbs 345 kV Line | 0 | 100% | 0 | 1
GEN-2023-081 | 05 SOUTHWEST | 158809 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-081 Interconnection (Non-Shared NU) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-081 (625MW/Hybrid), into Crossroads - Hobbs 345 kV Line | 27767200 | 100% | 27767200 | 1
GEN-2023-081 | 05 SOUTHWEST | TBD | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | Current Study | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | 11683837.612 | 23.13% | 50515758.16 | 0.03635
GEN-2023-081 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 16405.5181 | 1.911% | 858333 | 0.05199
GEN-2023-081 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1683863.0313 | 2.539% | 66320529.8 | 0.05088
GEN-2023-086 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 1036619.3955 | 12.48% | 8302968 | 0.12331
GEN-2023-086 | 05 SOUTHWEST | 158819 | ERIS | Potter - Newhart 230 kV line GEN-2023-086 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-086 (300MW/Hybrid), into Potter - Newhart 230 kV line | 11573021 | 100% | 11573021 | 1
GEN-2023-086 | 05 SOUTHWEST | 158818 | ERIS | Potter - Newhart 230 kV line GEN-2023-086 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-086 (300MW/Hybrid), into Potter - Newhart 230 kV line | 1700000 | 100% | 1700000 | 1
GEN-2023-086 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 10205.6901 | 1.189% | 858333 | 0.06738
GEN-2023-086 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1020643.3939 | 1.539% | 66320529.8 | 0.06425
GEN-2023-109 | 05 SOUTHWEST | TBD | ERIS | Build a new DUMAS19ST to MOORE_W 115kV line 1 | Current Study | Build a new DUMAS19ST to MOORE_W 115kV line CKT1 (12.18 miles) to a standard rating of 239 MVA | 10946982.06 | 100% | 10946982.06 | 0.39457
GEN-2023-109 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTER_CO to HARRNG_MID6 230kV line 1 | Current Study | Build a new POTTER_CO to HARRNG_MID6 230kV line CKT1 (11.2 miles) to a standard rating of 796 MVA | 133216.6383 | 1.027% | 12966083.2 | 0.03657
GEN-2023-109 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 192561.8674 | 2.319% | 8302968 | 0.10572
GEN-2023-109 | 05 SOUTHWEST | 158851 | ERIS | Dumas and 19th Street 115 kV Substation GEN-2023-109 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-109 (65MW/Solar), into Dumas and 19th Street 115 kV Substation | 12536957 | 100% | 12536957 | 1
GEN-2023-109 | 05 SOUTHWEST | 158850 | ERIS | Dumas and 19th Street 115 kV Substation GEN-2023-109 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-109 (65MW/Solar), into Dumas and 19th Street 115 kV Substation | 1900000 | 100% | 1900000 | 1
GEN-2023-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 2408.4651 | 0.2806% | 858333 | 0.07339
GEN-2023-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 238417.5312 | 0.3595% | 66320529.8 | 0.06927
GEN-2023-110 | 05 SOUTHWEST | 158853 | ERIS | Tap Border to Tuco 345 kV Line GEN-2023-110 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-110 (250MW/Solar), into Tap Border to Tuco 345 kV Line | 16856930 | 100% | 16856930 | 1
GEN-2023-110 | 05 SOUTHWEST | 158852 | ERIS | Tap Border to Tuco 345 kV Line GEN-2023-110 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-110 (250MW/Solar), into Tap Border to Tuco 345 kV Line | 1900000 | 100% | 1900000 | 1
GEN-2023-110 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 6612.6955 | 0.7704% | 858333 | 0.05239
GEN-2023-110 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 696843.9463 | 1.051% | 66320529.8 | 0.05264
GEN-2023-120 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTER_CO to HARRNG_MID6 230kV line 1 | Current Study | Build a new POTTER_CO to HARRNG_MID6 230kV line CKT1 (11.2 miles) to a standard rating of 796 MVA | 421907.3296 | 3.254% | 12966083.2 | 0.05791
GEN-2023-120 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 219737.6437 | 2.646% | 8302968 | 0.06032
GEN-2023-120 | 05 SOUTHWEST | 158863 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | 5412393 | 100% | 5412393 | 1
GEN-2023-120 | 05 SOUTHWEST | 158862 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | 1200000 | 100% | 1200000 | 1
GEN-2023-120 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3871.1343 | 0.451% | 858333 | 0.05898
GEN-2023-120 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 392303.0201 | 0.5915% | 66320529.8 | 0.05699
GEN-2023-123 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTER_CO to HARRNG_MID6 230kV line 1 | Current Study | Build a new POTTER_CO to HARRNG_MID6 230kV line CKT1 (11.2 miles) to a standard rating of 796 MVA | 3664184.708 | 28.26% | 12966083.2 | 0.22941
GEN-2023-123 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 916745.3036 | 11.04% | 8302968 | 0.11479
GEN-2023-123 | 05 SOUTHWEST | 158869 | ERIS | Pringle Interchange 230 kV Substation GEN-2023-123 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-123 (285MW/Wind), into Pringle Interchange 230 kV Substation | 9010000 | 100% | 9010000 | 1
GEN-2023-123 | 05 SOUTHWEST | 158868 | ERIS | Pringle Interchange 230 kV Substation GEN-2023-123 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-123 (285MW/Wind), into Pringle Interchange 230 kV Substation | 900000 | 100% | 900000 | 1
GEN-2023-123 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 9196.1023 | 1.071% | 858333 | 0.06391
GEN-2023-123 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 792289.3272 | 1.195% | 66320529.8 | 0.0525
GEN-2023-123 | 05 SOUTHWEST | TBD | ERIS | Rebuild the PRINGLE3 to RIVERVIEW3 115kV line 1 | Current Study | Rebuild the PRINGLE3 to RIVERVIEW3 115kV line CKT1 (20.25 miles) to a standard rating of 239 MVA | 7595402.8668 | 52.77% | 14394510 | 0.14441
GEN-2023-123 | 05 SOUTHWEST | TBD | ERIS | Upgrade the PRINGLE 230/115 kV transformer 1 | Current Study | Upgrade the PRINGLE 230/115 kV transformer 1 to a standard rating of 308 MVA | 6621188 | 100% | 6621188 | 0.40567
GEN-2023-124 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTER_CO to HARRNG_MID6 230kV line 1 | Current Study | Build a new POTTER_CO to HARRNG_MID6 230kV line CKT1 (11.2 miles) to a standard rating of 796 MVA | 1303332.3402 | 10.05% | 12966083.2 | 0.11628
GEN-2023-124 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 379250.3149 | 4.568% | 8302968 | 0.06767
GEN-2023-124 | 05 SOUTHWEST | 158871 | ERIS | Spearman Interchange 115 kV Substation GEN-2023-124 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-124 (200MW/Wind), into Spearman Interchange 115 kV Substation | 6767393 | 100% | 6767393 | 1
GEN-2023-124 | 05 SOUTHWEST | 158870 | ERIS | Spearman Interchange 115 kV Substation GEN-2023-124 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-124 (200MW/Wind), into Spearman Interchange 115 kV Substation | 1200000 | 100% | 1200000 | 1
GEN-2023-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 6865.3891 | 0.7999% | 858333 | 0.06799
GEN-2023-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 590305.191 | 0.8901% | 66320529.8 | 0.05574
GEN-2023-124 | 05 SOUTHWEST | TBD | ERIS | Rebuild the PRINGLE3 to RIVERVIEW3 115kV line 1 | Current Study | Rebuild the PRINGLE3 to RIVERVIEW3 115kV line CKT1 (20.25 miles) to a standard rating of 239 MVA | 6799107.1332 | 47.23% | 14394510 | 0.18421
GEN-2023-142 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 248982.8477 | 2.999% | 8302968 | 0.03231
GEN-2023-142 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 17264957.265 | 21.37% | 80800000 | 1
GEN-2023-142 | 05 SOUTHWEST | 158888 | ERIS | Plant X 230 kV Substation GEN-2023-142 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-142 (275MW/Solar), into Plant X 230 kV Substation | 850000 | 100% | 850000 | 1
GEN-2023-142 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 8000.1119 | 0.9321% | 858333 | 0.05762
GEN-2023-142 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 812397.723 | 1.225% | 66320529.8 | 0.05579
GEN-2023-142 | 05 SOUTHWEST | TBD | ERIS | Upgrade the PLANTX 230/115kV transformer 1 | Current Study | Upgrade the PLANTX 230/115kV transformer 1 to a standard rating of 308 MVA | 1408457.7002 | 21.27% | 6621188 | 0.06124
GEN-2023-143 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 181078.4347 | 2.181% | 8302968 | 0.03231
GEN-2023-143 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 12556332.5563 | 15.54% | 80800000 | 1
GEN-2023-143 | 05 SOUTHWEST | 158889 | ERIS | Plant X 230 kV Substation GEN-2023-143 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-143 (200MW/Battery/Storage), into Plant X 230 kV Substation | 850000 | 100% | 850000 | 1
GEN-2023-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5818.2632 | 0.6779% | 858333 | 0.05762
GEN-2023-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 590834.7076 | 0.8909% | 66320529.8 | 0.05579
GEN-2023-143 | 05 SOUTHWEST | TBD | ERIS | Upgrade the PLANTX 230/115kV transformer 1 | Current Study | Upgrade the PLANTX 230/115kV transformer 1 to a standard rating of 308 MVA | 1024332.8729 | 15.47% | 6621188 | 0.06124
GEN-2023-158 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 197698.3077 | 2.381% | 8302968 | 0.02106
GEN-2023-158 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | Current Study | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | 7888260.0698 | 49.92% | 15802413.9 | 0.43327
GEN-2023-158 | 05 SOUTHWEST | 158918 | ERIS | Needmore - Yoakum 230 kV Line GEN-2023-158 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158 (335MW/Solar), into Needmore - Yoakum 230 kV Line | 850000 | 100% | 850000 | 1
GEN-2023-158 | 05 SOUTHWEST | 158669 | ERIS | Needmore - Yoakum 230 kV Line Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158/159 (335/200MW/Solar/Battery/Storage), into Needmore - Yoakum 230 kV Line | 7152420.9439 | 62.62% | 11422523 | 1
GEN-2023-158 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 9559.5418 | 1.114% | 858333 | 0.05652
GEN-2023-158 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 972441.4909 | 1.466% | 66320529.8 | 0.05482
GEN-2023-158 | 05 SOUTHWEST | TBD | ERIS | Rebuild the TOLK to NEEDMORE 230 kV line 1 | Current Study | Rebuild the TOLK to NEEDMORE 230 kV line CKT1 (13.65 miles) to a standard rating of 796 MVA | 6420158.8623 | 53.24% | 12059897.85 | 0.43327
GEN-2023-159 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 118028.8404 | 1.422% | 8302968 | 0.02106
GEN-2023-159 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | Current Study | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | 4709408.9969 | 29.8% | 15802413.9 | 0.43327
GEN-2023-159 | 05 SOUTHWEST | 158669 | ERIS | Needmore - Yoakum 230 kV Line Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158/159 (335/200MW/Solar/Battery/Storage), into Needmore - Yoakum 230 kV Line | 4270102.0561 | 37.38% | 11422523 | 1
GEN-2023-159 | 05 SOUTHWEST | 158919 | ERIS | Needmore - Yoakum 230 kV Line GEN-2023-159 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-159 (200MW/Battery/Storage), into Needmore - Yoakum 230 kV Line | 850000 | 100% | 850000 | 1
GEN-2023-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5707.1891 | 0.6649% | 858333 | 0.05652
GEN-2023-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 580562.0841 | 0.8754% | 66320529.8 | 0.05482
GEN-2023-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild the TOLK to NEEDMORE 230 kV line 1 | Current Study | Rebuild the TOLK to NEEDMORE 230 kV line CKT1 (13.65 miles) to a standard rating of 796 MVA | 3832930.6641 | 31.78% | 12059897.85 | 0.43327
GEN-2023-176 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 269768.1972 | 3.249% | 8302968 | 0.03209
GEN-2023-176 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 18834498.8345 | 23.31% | 80800000 | 1
GEN-2023-176 | 05 SOUTHWEST | 158948 | ERIS | Plant X 230 kV Substation GEN-2023-176 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-176 (300MW/Wind), into Plant X 230 kV Substation | 1700000 | 100% | 1700000 | 1
GEN-2023-176 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7532.3385 | 0.8776% | 858333 | 0.04973
GEN-2023-176 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 639867.9519 | 0.9648% | 66320529.8 | 0.04028
GEN-2023-176 | 05 SOUTHWEST | TBD | ERIS | Upgrade the PLANTX 230/115kV transformer 1 | Current Study | Upgrade the PLANTX 230/115kV transformer 1 to a standard rating of 308 MVA | 1566105.2725 | 23.65% | 6621188 | 0.06242
GEN-2023-178 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 131591.5087 | 1.585% | 8302968 | 0.02348
GEN-2023-178 | 05 SOUTHWEST | 158952 | ERIS | Roosevelt 230kV Substation GEN-2023-178 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-178 (200MW/Solar), into Roosevelt 230kV Substation | 0 | 100% | 0 | 1
GEN-2023-178 | 05 SOUTHWEST | 158951 | ERIS | Roosevelt 230kV Substation GEN-2023-178 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-178 (200MW/Solar), into Roosevelt 230kV Substation | 0 | 100% | 0 | 1
GEN-2023-178 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5716.277 | 0.666% | 858333 | 0.05661
GEN-2023-178 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 581409.3108 | 0.8767% | 66320529.8 | 0.0549
GEN-2023-183 | 05 SOUTHWEST | 158958 | ERIS | Tuco 345kV GEN-2023-183 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-183 (217MW/Thermal), into Tuco 345kV | 0 | 100% | 0 | 1
GEN-2023-183 | 05 SOUTHWEST | 158957 | ERIS | Tuco 345kV GEN-2023-183 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-183 (217MW/Thermal), into Tuco 345kV | 0 | 100% | 0 | 1
GEN-2023-184 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | Current Study | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | 265214.7149 | 1.678% | 15802413.9 | 0.0244
GEN-2023-184 | 05 SOUTHWEST | 158960 | ERIS | Phantom 115 kV Substation GEN-2023-184 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-184 (200MW/Solar), into Phantom 115 kV Substation | 5780000 | 100% | 5780000 | 1
GEN-2023-184 | 05 SOUTHWEST | 158959 | ERIS | Phantom 115 kV Substation GEN-2023-184 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-184 (200MW/Solar), into Phantom 115 kV Substation | 1200000 | 100% | 1200000 | 1
GEN-2023-184 | 05 SOUTHWEST | TBD | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | Current Study | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | 3642143.0742 | 7.21% | 50515758.16 | 0.03541
GEN-2023-184 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5282.0783 | 0.6154% | 858333 | 0.05231
GEN-2023-184 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 541801.4634 | 0.8169% | 66320529.8 | 0.05116
GEN-2023-184 | 05 SOUTHWEST | TBD | NRIS | Rebuild the RED_BLUFF3 to RDRUNNER3 115kV line 1 | Current Study | Rebuild the RED_BLUFF3 to RDRUNNER3 115kV line CKT1 (11.54 miles) to a standard rating of 239 MVA | 7823110.8174 | 95.37% | 8203093.6 | 0.14354
GEN-2023-184 | 05 SOUTHWEST | TBD | ERIS | Rebuild the TOLK to NEEDMORE 230 kV line 1 | Current Study | Rebuild the TOLK to NEEDMORE 230 kV line CKT1 (13.65 miles) to a standard rating of 796 MVA | 215855.0285 | 1.79% | 12059897.85 | 0.0244
GEN-2023-185 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTER_CO to HARRNG_MID6 230kV line 1 | Current Study | Build a new POTTER_CO to HARRNG_MID6 230kV line CKT1 (11.2 miles) to a standard rating of 796 MVA | 2158349.9636 | 16.65% | 12966083.2 | 0.25675
GEN-2023-185 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 546219.6515 | 6.579% | 8302968 | 0.12995
GEN-2023-185 | 05 SOUTHWEST | 158962 | ERIS | Nichols - Amarillo 230 kV line tap GEN-2023-185 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-185 (150MW/Solar), into Nichols - Amarillo 230 kV line tap | 11470657 | 100% | 11470657 | 1
GEN-2023-185 | 05 SOUTHWEST | 158961 | ERIS | Nichols - Amarillo 230 kV line tap GEN-2023-185 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-185 (150MW/Solar), into Nichols - Amarillo 230 kV line tap | 1700000 | 100% | 1700000 | 1
GEN-2023-185 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5203.5691 | 0.6062% | 858333 | 0.06871
GEN-2023-185 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 519852.9972 | 0.7838% | 66320529.8 | 0.06545
GEN-2023-188 | 05 SOUTHWEST | 158966 | ERIS | Oklaunion - Lawton 345 kV Line GEN-2023-188 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-188 (160MW/Hybrid), into Oklaunion - Lawton 345 kV Line | 18700000 | 100% | 18700000 | 1
GEN-2023-188 | 05 SOUTHWEST | 158965 | ERIS | Oklaunion - Lawton 345 kV Line GEN-2023-188 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-188 (160MW/Hybrid), into Oklaunion - Lawton 345 kV Line | 3475000 | 100% | 3475000 | 1
GEN-2023-188 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 3153.6966 | 0.3674% | 858333 | 0.03904
GEN-2023-195 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 157483.8754 | 1.897% | 8302968 | 0.02248
GEN-2023-195 | 05 SOUTHWEST | 158975 | ERIS | Roosevelt - Tolk 230 kV line tap GEN-2023-195 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-195 (250MW/Solar), into Roosevelt - Tolk 230 kV line tap | 850000 | 100% | 850000 | 1
GEN-2023-195 | 05 SOUTHWEST | 158673 | ERIS | Roosevelt - Tolk 230 kV line tap Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-195/196 (250/150MW/Solar/Battery/Storage), into Roosevelt - Tolk 230 kV line tap | 7119473.125 | 62.5% | 11391157 | 1
GEN-2023-195 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7168.066 | 0.8351% | 858333 | 0.05679
GEN-2023-195 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 728747.326 | 1.099% | 66320529.8 | 0.05505
GEN-2023-196 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 94490.3252 | 1.138% | 8302968 | 0.02248
GEN-2023-196 | 05 SOUTHWEST | 158673 | ERIS | Roosevelt - Tolk 230 kV line tap Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-195/196 (250/150MW/Solar/Battery/Storage), into Roosevelt - Tolk 230 kV line tap | 4271683.875 | 37.5% | 11391157 | 1
GEN-2023-196 | 05 SOUTHWEST | 158976 | ERIS | Roosevelt - Tolk 230 kV line tap GEN-2023-196 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-196 (150MW/Battery/Storage), into Roosevelt - Tolk 230 kV line tap | 850000 | 100% | 850000 | 1
GEN-2023-196 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 4300.8396 | 0.5011% | 858333 | 0.05679
GEN-2023-196 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 437248.3956 | 0.6593% | 66320529.8 | 0.05505
GEN-2023-201 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | Current Study | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | 348909.5225 | 2.208% | 15802413.9 | 0.0214
GEN-2023-201 | 05 SOUTHWEST | 158985 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-201 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-201 (300MW/Hybrid), into Crossroads - Hobbs 345 kV Line | 0 | 100% | 0 | 1
GEN-2023-201 | 05 SOUTHWEST | 158986 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-201 Interconnection (Non-Shared NU) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-201 (300MW/Hybrid), into Crossroads - Hobbs 345 kV Line | 24961200 | 100% | 24961200 | 1
GEN-2023-201 | 05 SOUTHWEST | TBD | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | Current Study | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | 5566585.2352 | 11.02% | 50515758.16 | 0.03608
GEN-2023-201 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7885.2512 | 0.9187% | 858333 | 0.05206
GEN-2023-201 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 809207.385 | 1.22% | 66320529.8 | 0.05094
GEN-2023-203 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | Current Study | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | 853687.0372 | 5.402% | 15802413.9 | 0.05236
GEN-2023-203 | 05 SOUTHWEST | 158990 | ERIS | Hobbs - Ink Basin 230 kV Transmission Line GEN-2023-203 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-203 (300MW/Hybrid), into Hobbs - Ink Basin 230 kV Transmission Line | 11348902 | 100% | 11348902 | 1
GEN-2023-203 | 05 SOUTHWEST | 158989 | ERIS | Hobbs - Ink Basin 230 kV Transmission Line GEN-2023-203 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-203 (300MW/Hybrid), into Hobbs - Ink Basin 230 kV Transmission Line | 1700000 | 100% | 1700000 | 1
GEN-2023-203 | 05 SOUTHWEST | TBD | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | Current Study | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | 5258016.2088 | 10.41% | 50515758.16 | 0.03408
GEN-2023-203 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7980.674 | 0.9298% | 858333 | 0.05269
GEN-2023-203 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 818103.2652 | 1.234% | 66320529.8 | 0.0515
GEN-2023-203 | 05 SOUTHWEST | TBD | ERIS | Rebuild the TOLK to NEEDMORE 230 kV line 1 | Current Study | Rebuild the TOLK to NEEDMORE 230 kV line CKT1 (13.65 miles) to a standard rating of 796 MVA | 694805.4893 | 5.761% | 12059897.85 | 0.05236
GEN-2023-208 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTER_CO to HARRNG_MID6 230kV line 1 | Current Study | Build a new POTTER_CO to HARRNG_MID6 230kV line CKT1 (11.2 miles) to a standard rating of 796 MVA | 2065851.2524 | 15.93% | 12966083.2 | 0.18431
GEN-2023-208 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 748524.7829 | 9.015% | 8302968 | 0.13356
GEN-2023-208 | 05 SOUTHWEST | 159000 | ERIS | Rolling Hills 115 kV GEN-2023-208 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-208 (200MW/Battery/Storage), into Rolling Hills 115 kV | 5005000 | 100% | 5005000 | 1
GEN-2023-208 | 05 SOUTHWEST | 158999 | ERIS | Rolling Hills 115 kV GEN-2023-208 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-208 (200MW/Battery/Storage), into Rolling Hills 115 kV | 1200000 | 100% | 1200000 | 1
GEN-2023-208 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 7015.844 | 0.8174% | 858333 | 0.06948
GEN-2023-208 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 700232.853 | 1.056% | 66320529.8 | 0.06612
GEN-2023-209 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTER_CO to HARRNG_MID6 230kV line 1 | Current Study | Build a new POTTER_CO to HARRNG_MID6 230kV line CKT1 (11.2 miles) to a standard rating of 796 MVA | 1432875.3702 | 11.05% | 12966083.2 | 0.20454
GEN-2023-209 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 447512.0089 | 5.39% | 8302968 | 0.12776
GEN-2023-209 | 05 SOUTHWEST | 159002 | ERIS | Amarillo South 115 kV GEN-2023-209 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-209 (125MW/Battery/Storage), into Amarillo South 115 kV | 9460000 | 100% | 9460000 | 1
GEN-2023-209 | 05 SOUTHWEST | 159001 | ERIS | Amarillo South 115 kV GEN-2023-209 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-209 (125MW/Battery/Storage), into Amarillo South 115 kV | 1200000 | 100% | 1200000 | 1
GEN-2023-209 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 4326.2099 | 0.504% | 858333 | 0.06855
GEN-2023-209 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 432284.1768 | 0.6518% | 66320529.8 | 0.06531
GEN-2023-228 | 05 SOUTHWEST | 159031 | ERIS | Tuco-Okalunion 345 kV line GEN-2023-228 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-228 (250MW/Battery/Storage), into Tuco-Okalunion 345 kV line | 0 | 100% | 0 | 1
GEN-2023-228 | 05 SOUTHWEST | 159030 | ERIS | Tuco-Okalunion 345 kV line GEN-2023-228 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-228 (250MW/Battery/Storage), into Tuco-Okalunion 345 kV line | 0 | 100% | 0 | 1
GEN-2023-228 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 5585.2601 | 0.6507% | 858333 | 0.04425
GEN-2023-228 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 586174.9609 | 0.8839% | 66320529.8 | 0.04428
GEN-2023-236 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | Current Study | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | 594341.8283 | 3.761% | 15802413.9 | 0.02734
GEN-2023-236 | 05 SOUTHWEST | 159041 | ERIS | Hobbs - Yoakum 345 kV GEN-2023-236 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-236 (400MW/Solar), into Hobbs - Yoakum 345 kV | 17684222 | 100% | 17684222 | 1
GEN-2023-236 | 05 SOUTHWEST | 159040 | ERIS | Hobbs - Yoakum 345 kV GEN-2023-236 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-236 (400MW/Solar), into Hobbs - Yoakum 345 Kv | 1900000 | 100% | 1900000 | 1
GEN-2023-236 | 05 SOUTHWEST | TBD | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | Current Study | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | 7319257.3048 | 14.49% | 50515758.16 | 0.03558
GEN-2023-236 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 10529.8245 | 1.227% | 858333 | 0.05214
GEN-2023-236 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1080637.6334 | 1.629% | 66320529.8 | 0.05102
GEN-2023-236 | 05 SOUTHWEST | TBD | ERIS | Rebuild the TOLK to NEEDMORE 230 kV line 1 | Current Study | Rebuild the TOLK to NEEDMORE 230 kV line CKT1 (13.65 miles) to a standard rating of 796 MVA | 483727.5803 | 4.011% | 12059897.85 | 0.02734
GEN-2023-237 | 05 SOUTHWEST | 159043 | ERIS | Crawfish Draw 345 kV Substation GEN-2023-237 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-237 (500MW/Wind), into Crawfish Draw 345 kV Substation | 18553998 | 100% | 18553998 | 1
GEN-2023-237 | 05 SOUTHWEST | 159042 | ERIS | Crawfish Draw 345 kV Substation GEN-2023-237 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-237 (500MW/Wind), into Crawfish Draw 345 kV Substation | 1900000 | 100% | 1900000 | 1
GEN-2023-237 | 05 SOUTHWEST | TBD | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | Current Study | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | 11265340.87 | 22.3% | 50515758.16 | 0.04381
GEN-2023-237 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 10367.7573 | 1.208% | 858333 | 0.04107
GEN-2023-237 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 869201.6245 | 1.311% | 66320529.8 | 0.03283
GEN-2023-238 | 05 SOUTHWEST | 159045 | ERIS | Potter County 345 kV Substation GEN-2023-238 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-238 (280MW/Solar), into Potter County 345 kV Substation | 11628280 | 100% | 11628280 | 1
GEN-2023-238 | 05 SOUTHWEST | 159044 | ERIS | Potter County 345 kV Substation GEN-2023-238 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-238 (280MW/Solar), into Potter County 345 kV Substation | 1900000 | 100% | 1900000 | 1
GEN-2023-238 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 10223.6639 | 1.191% | 858333 | 0.07232
GEN-2023-238 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1015761.2502 | 1.532% | 66320529.8 | 0.06851
GEN-2023-239 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTER_CO to HARRNG_MID6 230kV line 1 | Current Study | Build a new POTTER_CO to HARRNG_MID6 230kV line CKT1 (11.2 miles) to a standard rating of 796 MVA | 1786365.5979 | 13.78% | 12966083.2 | 0.10625
GEN-2023-239 | 05 SOUTHWEST | TBD | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | Current Study | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | 1218790.6898 | 14.68% | 8302968 | 0.14498
GEN-2023-239 | 05 SOUTHWEST | 159047 | ERIS | Rolling Hills 230 kV Substation GEN-2023-239 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-239 (300MW/Solar), into Rolling Hills 230 kV Substation | 9035000 | 100% | 9035000 | 1
GEN-2023-239 | 05 SOUTHWEST | 159046 | ERIS | Rolling Hills 230 kV Substation GEN-2023-239 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-239 (300MW/Solar), into Rolling Hills 230 kV Substation | 1700000 | 100% | 1700000 | 1
GEN-2023-239 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 10650.9963 | 1.241% | 858333 | 0.07032
GEN-2023-239 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1061469.1297 | 1.601% | 66320529.8 | 0.06682
GEN-2023-240 | 05 SOUTHWEST | 159049 | ERIS | Tolk 345 kV Substation GEN-2023-240 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-240 (550MW/Solar), into Tolk 345 kV Substation | 5975000 | 100% | 5975000 | 1
GEN-2023-240 | 05 SOUTHWEST | 159048 | ERIS | Tolk 345 kV Substation GEN-2023-240 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-240 (550MW/Solar), into Tolk 345 kV Substation | 1900000 | 100% | 1900000 | 1
GEN-2023-240 | 05 SOUTHWEST | TBD | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | Current Study | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | 15944.6868 | 1.858% | 858333 | 0.05742
GEN-2023-240 | 05 SOUTHWEST | TBD | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | Current Study | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | 1618970.7626 | 2.441% | 66320529.8 | 0.05559
GEN-2023-074 | WECC | 159062 | ERIS | Custer - Rosebud Creek 230 kV Line Tap GEN-2023-074 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-074 (85MW/Solar/Storage), into Custer - Rosebud Creek 230 kV Line Tap | 22360000 | 100% | 22360000 | 1
GEN-2023-074 | WECC | 159061 | ERIS | Custer - Rosebud Creek 230 kV Line Tap GEN-2023-074 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-074 (85MW/Solar/Storage), into Custer - Rosebud Creek 230 kV Line Tap | 595000 | 100% | 595000 | 1
GEN-2023-074 | WECC | TBD | ERIS | Columbus 230kV Subsystem Reconfiguration | Current Study | Reconfigure Columbus 230kV substation to add a breaker between Shorey Road to Stillwater Wind 230kV line | 4606938 | 100% | 4606938 | 1
|  |  |  | 679 |  |  | 7195472474.22

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new OAHE to SWEET W3 345 kV line 1 | TBD | Build a new OAHE to SWEET W3 345 kV line 1 (260 miles) to a standard rating of 1792 MVA | NPPD, WAPA | 36 | 389894700
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 | TBD | Build a new CHAPELLE-BE3 to S3458 3 345 kV line 1 (240 miles) to a standard rating of 1792 MVA | OPPD, WAPA | 36 | 359902800
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 | TBD | Build a new GROTON__-BE3 to TURTLE.CRK 3 345 kV line 1 (220 miles) to a standard rating of 1792 MVA | BEPC, WAPA | 36 | 329910900
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the CHAPELLE-BE3 to S3458 3 345 kV line 1 | TBD | Increase the ratings of the new S3458 3 to CHAPELLE-BE3 345 kV line 1 (240 miles) to a higher rating of 2150 MVA at 0 cost. | OPPD, WAPA | 36 | 0
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new BELFELD3 to MAURINE 345 kV line 1 | TBD | Build a new BELFELD3 to MAURINE 345 kV line 1 (170 miles) to a standard rating of 1792 MVA | BEPC, WAPA | 36 | 273358902
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new OAHE to MAURINE 345 kV line 1 | TBD | Build a new OAHE to MAURINE 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | BEPC, WAPA | 36 | 149959500
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 | TBD | Build a new BROADLND-BE3 to GROTON__-BE3 345 kV line 1 (100 miles) to a standard rating of 1792 MVA | BEPC, WAPA | 36 | 149959500
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new OAHE to MAURINE 345 kV line 2 | TBD | Build a new OAHE to MAURINE 345 kV line 2 (100 miles) to a standard rating of 1792 MVA | BEPC, WAPA | 36 | 149959500
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the G22-020-PROX to G23-054-TAP 345kV line 1 | TBD | Rebuild the existing G22-020-PROX to G23-054-TAP 345 kV line 1 (100.42 miles) to a standard rating of 1792 MVA | BEPC, WAPA | 36 | 114925066.48
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the MAURINE4 to NUNDRWD-LNX3 230kV line 1 | TBD | Rebuild the existing MAURINE4 to NUNDRWD-LNX3 230 kV line 1 (71.98 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 63594977.82
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the RAUN 3 to G18-043 TAP 345kV line 1 | TBD | Rebuild the existing RAUN 3 to G18-043 TAP 345 kV line 1 (50.04 miles) to a standard rating of 1792 MVA | BEPC, WAPA | 36 | 57267977.76
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the JAMESTN4 to PICKERT4 230kV line 1 | TBD | Rebuild the existing JAMESTN4 to PICKERT4 230 kV line 1 (61.36 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 54212112.24
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new 200 MVAR cap bank at Oahe 345 kV | TBD | Build 200Mvar Reactive Support at Oahe 345kV | BEPC, WAPA | 36 | 4978200
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the GRNDFKS4 to PICKERT4 230kV line 1 | TBD | Rebuild the existing GRNDFKS4 to PICKERT4 230 kV line 1 (49 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 43291941
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new BOWMAN__-BE4 to HETINGR4 230 kV line 2 | TBD | Build a new BOWMAN__-BE4 to HETINGR4 230 kV line 2 (36.35 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 42081886.1
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new 150 MVAR cap bank at Maurine 345 kV | TBD | Build 150Mvar Reactive Support at Maurine 345kV | BEPC, WAPA | 36 | 3733650
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the G17-094-TAP to FTTHOMP4 230kV line 1 | TBD | Rebuild the existing G17-094-TAP to FTTHOMP4 230 kV line 1 (37.37 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 33016731.33
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the BISON___-GE4 to HETINGR4 230kV line 1 | TBD | Rebuild the existing BISON___-GE4 to HETINGR4 230 kV line 1 (37.09 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 32769348.81
Contingent | Steady State | 01 NORTH | 2021 ITP | ERIS | Whitlock - Glenham 230 kV Clearance Increase | 143614 | Increase ground clearance of the Whitlock - Glenham 230 kV. (NTC 210648) | BEPC, WAPA | 36 | 5845900
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the JAMESTN4 to G23-144-TAP 230kV line 1 | TBD | Rebuild the existing JAMESTN4 to G23-144-TAP 230 kV line 1 (30.2 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 26681971.8
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the GENTLMN4 to OGALALA4 230kV line 1 | TBD | Rebuild the existing GENTLMN4 to OGALALA4 230 kV line 1 (30.09 miles) to a standard rating of 796 MVA | NPPD | 36 | 26584785.81
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the MAURINE7 to SULPHUR 115kV line 1 | TBD | Rebuild the existing MAURINE7 to SULPHUR 115 kV line 1 (34.16 miles) to a standard rating of 239 MVA | BEPC, WAPA | 36 | 24282294.4
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the G17-094-TAP to HURON 4 230kV line 1 | TBD | Rebuild the existing G17-094-TAP to HURON 4 230 kV line 1 (21.91 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 19357682.19
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the SB.LS-WK-ER4 to WHITLOCK_-RM 230kV line 1 | TBD | Rebuild the existing SB.LS-WK-ER4 to WHITLOCK_-RM 230 kV line 1 (21.56 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 19048454.04
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the ELKCRK 7 to NEWELL 7 115kV line 1 | TBD | Rebuild the existing ELKCRK 7 to NEWELL 7 115 kV line 1 (26 miles) to a standard rating of 239 MVA | BEPC, WAPA | 36 | 18481840
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the BISON___-GE4 to G23-098-TAP 230kV line 1 | TBD | Rebuild the existing BISON___-GE4 to G23-098-TAP 230 kV line 1 (19.76 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 17458137.84
Contingent | Steady State | 01 NORTH | 2021 ITP | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | 122734 | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation (NTC 210648) | BEPC, WAPA | 36 | 561800
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the G22-066-PROX to G23-098-TAP 230kV line 1 | TBD | Rebuild the existing G22-066-PROX to G23-098-TAP 230 kV line 1 (15.35 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 13561863.15
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the NEWELL 7 to SULPHUR 115kV line 1 | TBD | Rebuild the existing NEWELL 7 to SULPHUR 115 kV line 1 (17.52 miles) to a standard rating of 239 MVA | BEPC, WAPA | 36 | 12453916.8
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the CAMPBELL 4 to GLENHAM4 230kV line 1 | TBD | Rebuild the existing CAMPBELL 4 to GLENHAM4 230 kV line 1 (14 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 12369126
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the AURORA 7 to FLANDRU7 115kV line 1 | TBD | Rebuild the existing AURORA 7 to FLANDRU7 115 kV line 1 (17.05 miles) to a standard rating of 239 MVA | BEPC, WAPA | 36 | 12119822
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the CHADRON7 to WAYSIDE7 115kV line 1 | TBD | Rebuild the existing CHADRON7 to WAYSIDE7 115 kV line 1 (16.2 miles) to a standard rating of 239 MVA | BEPC, WAPA | 36 | 11515608
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new Maurine 345/230 kV transformer 1 | TBD | Build Maurine 345/230kV Transformer Ckt 1 | BEPC, WAPA | 36 | 8302968
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new Oahe 345/230 kV transformer 1 | TBD | Build Oahe 345/230kV Transformer Ckt 1 | BEPC, WAPA | 36 | 8302968
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new Broadland 345/230 kV transformer 2 | TBD | Build Broadland 345/230kV Transformer Ckt 2 | BEPC, WAPA | 36 | 8302968
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the AURORA 7 to BROOKNG7 115kV line 1 | TBD | Rebuild the existing AURORA 7 to BROOKNG7 115 kV line 1 (11 miles) to a standard rating of 239 MVA | BEPC, WAPA | 36 | 7819240
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the ELKCRK 7 to RAPIDCY7 115kV line 1 | TBD | Rebuild the existing ELKCRK 7 to RAPIDCY7 115 kV line 1 (10 miles) to a standard rating of 239 MVA | BEPC, WAPA | 36 | 7108400
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new Wayside 230/115 kV transformer 2 | TBD | Build Wayside 230/115kV Transformer Ckt 2 | BEPC, WAPA | 36 | 6621188
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the SCOTBLF7 to VICTRYH7 115kV line 1 | TBD | Rebuild the existing SCOTBLF7 to VICTRYH7 115 kV line 1 (8.09 miles) to a standard rating of 239 MVA | BEPC, WAPA | 36 | 5750695.6
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2 | TBD | Build a new IRVSIMM7 to G23-066-TAP 115 kV line 2 (5.25 miles) to a standard rating of 239 MVA | MRES, WAPA | 36 | 4718526.75
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 | TBD | Build a new SHEYNNE4 to FARGO 4 230 kV line 2 (4.2 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 4862281.2
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | TBD | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line 1 (4.2 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 3710737.8
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the RAPIDCY7 to RUSHMORE-RM7 115kV line 1 | TBD | Rebuild the existing RAPIDCY7 to RUSHMORE-RM7 115 kV line 1 (4.99 miles) to a standard rating of 239 MVA | BEPC, WAPA | 36 | 3547091.6
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the SIDNEY___TS4 to SIDNEY__-MB4 230kV line 1 | TBD | Rebuild the existing SIDNEY___TS4 to SIDNEY__-MB4 230 kV line 1 (4 miles) to a standard rating of 796 MVA | BEPC, WAPA | 36 | 3534036
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new Fargo 115/69 kV transformer 2 | TBD | Build Fargo 115/69kV Transformer Ckt 2 | BEPC, WAPA | 36 | 2777743
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 1 | TBD | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 1 (0.72 miles) to a standard rating of 1792 MVA | BEPC, WAPA | 36 | 823999.68
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the G20-021-TAP to G22-020-PROX 345kV line 2 | TBD | Rebuild the existing G20-021-TAP to G22-020-PROX 345 kV line 2 (0.71 miles) to a standard rating of 1792 MVA | BEPC, WAPA | 36 | 812555.24
Current Study | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the FARGO 8 to DELVO 8 69kV line 1 | TBD | Rebuild the existing FARGO 8 to DELVO 8 69 kV line 1 (0.01 miles) to a standard rating of 71 MVA | BEPC, WAPA | 36 | 9089.49
Current Study | Steady State | 01 NORTH/02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1 | TBD | Rebuild the existing OGALALA4 to SIDNEY___TS4 230 kV line 1 (68.85 miles) to a standard rating of 796 MVA | NPPD | 36 | 60829594.65
Current Study | Steady State | 01 NORTH/02 NEBRASKA/03 CENTRAL/04 SOUTHEAST/05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the FINNEY 7 to HOLCOMB7 345kV line 2 | TBD | Rebuild the existing FINNEY 7 to HOLCOMB7 345 kV line 2 (0.75 miles) to a standard rating of 1792 MVA | SPS/SUNC | 36 | 858333
Current Study | Steady State | 01 NORTH/03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the SIBLEY 5 to SIBLEYPL 161kV line 1 | TBD | Rebuild the existing SIBLEY 5 to SIBLEYPL 161 kV line 1 (1.19 miles) to a standard rating of 557 MVA | KCPL | 36 | 1164086.56
Contingent | Steady State | 02 NEBRASKA | 2021 ITP | ERIS | New Line - S3454 - S3740 345 kV | 143660 /143661 /143662 | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1 (NTC 210680) | OPPD | 36 | 64071687
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | BUILD GENTLMN3 KEYSTONE3 345kV CKT2 | TBD | Build a new line from GENTLMN3 to KEYSTONE3 345kV line 1 (29.84 miles) to a standard rating of 1792 MVA | NPPD | 36 | 44747914.8
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the MINGO 7 to G22-015-TAP 345kV line 1 | TBD | Rebuild the existing MINGO 7 to G22-015-TAP 345 kV line 1 (37.4 miles) to a standard ratings of 1792 MVA | NPPD/ SUNC | 36 | 42802205.6
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the GENTLMN3 to KEYSTON3 345kV line 1 | TBD | Rebuild the existing GENTLMN3 to KEYSTON3 345 kV line 1 (29.84 miles) to a standard ratings of 1792 MVA | NPPD | 36 | 34150208.96
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 1 | TBD | Build a new line from TURTLE.CRK 3 to G19-069TAP 345kV line 1 (20.2 miles) to a standard rating of 1792 MVA | NPPD | 36 | 30291819
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | BUILD TURTLE.CRK 3 G19-069TAP 345kV CKT 2 | TBD | Build a new line from TURTLE.CRK 3 to G19-069TAP 345kV line 2 (20.2 miles) to a standard rating of 1792 MVA | NPPD | 36 | 30291819
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | BUILD KEYSTON3 G21-037-TAP 345kV CKT 2 | TBD | Build a new line from KEYSTON3 to G21-037-TAP 345kV line 2 (19.54 miles) to a standard rating of 1792 MVA | NPPD | 36 | 29257098.45
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the S3455 to S3740 345kV line 1 | TBD | Rebuild the S3455 to S3740 345kV line CKT1 (20.15 miles) to a standard rating of 1792 MVA | OPPD | 36 | 23060546.6
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the TEKAMAH5 to S1226 5 161kV line 1 | TBD | Rebuild the existing TEKAMAH5 to S1226 5 161 kV line 1 (20.87 miles) to a standard ratings of 557 MVA | OPPD | 36 | 20415534.88
Contingent | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Rebuild the MORRILL7 to GERINGT_-TS7 115kV line 1 (non-SPP) | TBD | Rebuild the existing MORRILL7 to GERINGT_-TS7 115 kV line 1 (24.19 miles) to a standard ratings of 239 MVA (non-SPP) (Facility Owner to address) | WAPA RMR | 36 | 17195219.6
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | NRIS | Build a new BPSSUB7 to SHELDON7 115kV line 2 | TBD | Build a new BPSSUB7 to SHELDON7 138kV line CKT2 (16.8504 miles) to a standard rating of 398 MVA | NPPD | 36 | 14049256.91
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Build a new BPSSUB7 to HARBINE7 115kV line 1 | TBD | Build a new BPSSUB7 to HARBINE7 115kV line CKT1 (14.58 miles) to a standard rating of 239 MVA | NPPD | 36 | 13104022.86
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the BPSSUB7 to SHELDON7 115kV line 1 | TBD | Rebuild the BPSSUB7 to SHELDON7 115kV line CKT1 (16.85 miles) to a standard rating of 398 MVA | NPPD | 36 | 11977654
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the MALONEY7 to SUTHLND7 115kV line 1 | TBD | Rebuild the existing MALONEY7 to SUTHLND7 115 kV line 1 (15.46 miles) to a standard ratings of 239 MVA | NPPD | 36 | 10989586.4
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the BEATRCE7 to HARBINE7 115kV line 1 | TBD | Rebuild the existing BEATRCE7 to HARBINE7 115 kV line 1 (14.08 miles) to a standard ratings of 239 MVA | NPPD | 36 | 10008627.2
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the CLATONA7 to SHELDON 7 115kV line 1 | TBD | Rebuild the CLATONA7 to SHELDON 7 115kV line CKT1 (12.41 miles) to a standard rating of 398 MVA | NPPD | 36 | 8821524.4
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the PILE 3 to SCOTCTY3 115kV line 1 | TBD | Rebuild the existing PILE 3 to SCOTCTY3 115 kV line 1 (11.88 miles) to a standard ratings of 398 MVA | SUNC | 36 | 8444779.2
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the SUTHLND7 to PAXTON__-TS7 115kV line 1 | TBD | Rebuild the existing SUTHLND7 to PAXTON__-TS7 115 kV line 1 (10.21 miles) to a standard ratings of 239 MVA | NPPD | 36 | 7257676.4
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | NRIS | Build a new HOSKINST1 230/115 kV transformer 2 | TBD | Build a new HOSKINST1 230/115 kV transformer 2 to a standard rating of 229 MVA | NPPD | 36 | 6621188
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the BPSSUB7 to CLATONA7 115kV line 1 | TBD | Rebuild the BPSSUB7 to CLATONA7 115kV line CKT1 (8.96 miles) to a standard rating of 398 MVA | NPPD | 36 | 6369126.4
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | BUILD TEKAMAH5 G17-105TAP 161kV CKT2 | TBD | Build a new line from TEKAMAH5 to G17-105TAP 161kV line (3.71 miles) to a standard rating of 557 MVA | OPPD/ MEC | 36 | 3879706.53
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the TEKAMAH5 to G17-105TAP 161kV line 1 | TBD | Rebuild the existing TEKAMAH5 to G17-105TAP 161 kV line 1 (3.71 miles) to a standard ratings of 557 MVA | OPPD/ MEC | 36 | 3629211.04
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the BPSSUB7 to BEATRCE7 115kV line 1 | TBD | Rebuild the BPSSUB7 to BEATRCE7 115kV line CKT1 (4.18 miles) to a standard rating of 398 MVA | NPPD | 36 | 2971311.2
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the BPSSUB7 to BEATRCE7 115kV line 2 | TBD | Rebuild the BPSSUB7 to BEATRCE7 115kV line CKT2 (4.18 miles) to a standard rating of 398 MVA | NPPD | 36 | 2971311.2
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the PAXTON__-TS7 to G23-071-TAP 115kV line 1 | TBD | Rebuild the existing PAXTON__-TS7 to G23-071-TAP 115 kV line 1 (3.92 miles) to a standard ratings of 239 MVA | BEPC | 36 | 2786492.8
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | NRIS | Build a new FREMONT7 115/69 kV transformer 3 | TBD | Build a new FREMONT7 115/69 kV transformer 3 to a standard rating of 33 MVA | NPPD | 36 | 2777743
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the MALONEY7 to N.PLATT7 115kV line 1 | TBD | Rebuild the existing MALONEY7 to N.PLATT7 115 kV line 1 (3.47 miles) to a standard ratings of 239 MVA | NPPD | 36 | 2466614.8
Current Study | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the ELSIETP_-TS7 to G23-071-TAP 115kV line 1 | TBD | Rebuild the existing ELSIETP_-TS7 to G23-071-TAP 115 kV line 1 (3.08 miles) to a standard ratings of 239 MVA | BEPC | 36 | 2189387.2
Current Study | Steady State | 02 NEBRASKA/03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the REDWILO3 to G22-015-TAP 345kV line 1 | TBD | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a standard rating of 1792 MVA | NPPD/ SUNC | 36 | 43786427.44
Current Study | Steady State | 02 NEBRASKA/03 CENTRAL | DISIS-2023-001 | ERIS | Build a new Setab 345/115 kV transformer 2 | TBD | Build a new Setab 345/115 kV transformer 2 | SUNC | 36 | 8302968
Current Study | Steady State | 02 NEBRASKA/03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the SCOTCTY3 to SETAB 3 115kV line 1 | TBD | Rebuild the existing SCOTCTY3 to SETAB 3 115 kV line 1 (2.77 miles) to a standard rating of 398 MVA | SUNC | 36 | 1969026.8
Contingent | Steady State | 03 CENTRAL | 2019 ITP | ERIS | Blackberry - Wolf Creek 345 kV | 122598 | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA (NTC 210626) | NEET | 36 | 87298154
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the G20-076-TAP to G21-096-TAP 345kV line 1 | TBD | Rebuild the existing G20-076-TAP to G21-096-TAP 345 kV line 1 (61.1 miles) to a standard rating of 1792 MVA | WERE | 36 | 69925528.4
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new LACYGNE7 to PHILL 7 345kV line 1 | TBD | Build a new LACYGNE7 to PHILL 7 345 kV line 1 (43.2 miles) to a standard rating of 1792 MVA | KCPL | 36 | 64782504
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 2 | TBD | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 2 (43.1 miles) to a standard rating of 557 MVA | SWPA/EMDE | 36 | 42161454.4
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the SPRGFLD5 to LAR382 5 161kV line 1 | TBD | Rebuild the existing SPRGFLD5 to LAR382 5 161 kV line 1 (43.1 miles) to a standard rating of 557 MVA | SWPA/EMDE | 36 | 42161454.4
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345kV line 1 | TBD | Rebuild the existing 7BLACKBERRY to NEOSHO 7 345 kV line 1 (31.46 miles) to a standard rating of 1792 MVA | AECI/WERE | 36 | 36004208.24
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the ROSEHIL7 to LATHAMS7 345kV line 1 | TBD | Rebuild the existing ROSEHIL7 to LATHAMS7 345 kV line 1 (30.44 miles) to a standard rating of 1792 MVA | WERE | 36 | 34836875.36
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the MARYVLE5 to CLRNDA 5 161kV line 1 | TBD | Rebuild the existing MARYVLE5 to CLRNDA 5 161 kV line 1 (29.3 miles) to a standard rating of 557 MVA | KCPL/MEC | 36 | 28661963.2
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new G23-025-TAP to LITCH 5 161kV line 1 | TBD | Build a new G23-025-TAP to LITCH 5 161 kV line 1 (24 miles) to a standard rating of 557 MVA | WERE | 36 | 25097832
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the NEO SPA5 to CARTHAG5 161kV line 1 | TBD | Rebuild the existing NEO SPA5 to CARTHAG5 161 kV line 1 (22.9 miles) to a standard rating of 557 MVA | SWPA | 36 | 22401329.6
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the SPEARVL6 to G19-053-TAP 230kV line 1 | TBD | Rebuild the existing SPEARVL6 to G19-053-TAP 230 kV line 1 (24.46 miles) to a standard rating of 796 MVA | SUNC | 36 | 21610630.14
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 5OVERTON 2 to G23-115-TAP 161kV line 1 | TBD | Rebuild the existing 5OVERTON 2 to G23-115-TAP 161 kV line 1 (20.5 miles) to a standard rating of 557 MVA | AMMO/KCPL | 36 | 20053592
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the BENTON 7 to ROSEHIL7 345kV line 1 | TBD | Rebuild the existing BENTON 7 to ROSEHIL7 345 kV line 1 (15.48 miles) to a standard rating of 1792 MVA | WERE | 36 | 17715993.12
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the DELWARE7 to G22-176-TAP 345kV line 1 | TBD | Rebuild the existing DELWARE7 to G22-176-TAP 345 kV line 1 (15.27 miles) to a standard rating of 1792 MVA | AEPW | 36 | 17475659.88
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the SEDEAST5 to G22-100-TAP 161kV line 1 | TBD | Rebuild the existing SEDEAST5 to G22-100-TAP 161 kV line 1 (16.89 miles) to a standard rating of 557 MVA | KCPL | 36 | 16522203.36
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the LAR382 5 to MON383 5 161kV line 1 | TBD | Rebuild the existing LAR382 5 to MON383 5 161 kV line 1 (15.56 miles) to a standard rating of 557 MVA | EMDE | 36 | 15221165.44
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the RDS295 5 to G19-035-TAP 161kV line 1 | TBD | Rebuild the existing RDS295 5 to G19-035-TAP 161 kV line 1 (15.41 miles) to a standard rating of 557 MVA | EMDE | 36 | 15074431.84
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the FRANKLIN5 to G23-025-TAP 161kV line 1 | TBD | Rebuild the existing FRANKLIN5 to G23-025-TAP 161 kV line 1 (14.57 miles) to a standard rating of 557 MVA | WERE | 36 | 14252723.68
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new G20-079-TAP to STL439 5 161kV line 1 | TBD | Build a new G20-079-TAP to STL439 5 161 kV line 1 (12.24 miles) to a standard rating of 557 MVA | EMDE | 36 | 12799894.32
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the AUR124 5 to MON383 5 161kV line 1 | TBD | Rebuild the existing AUR124 5 to MON383 5 161 kV line 1 (11.51 miles) to a standard rating of 557 MVA | EMDE | 36 | 11259358.24
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the ROSEHIL4 to STEARMN4 138kV line 1 | TBD | Rebuild the existing ROSEHIL4 to STEARMN4 138 kV line 1 (11.64 miles) to a standard rating of 478 MVA | WERE | 36 | 11222810.76
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the HICKOCK3 to PIONEER3 115kV line 1 | TBD | Rebuild the existing HICKOCK3 to PIONEER3 115 kV line 1 (12.96 miles) to a standard rating of 239 MVA | SUNC | 36 | 9212486.4
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new Spearville 345/230 kV transformer 2 | TBD | Build a new Spearville 345/230 kV transformer 2 | SUNC | 36 | 8302968
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new Sibley 345/161 kV transformer 2 | TBD | Build a new Sibley 345/161 kV transformer 2 | KCPL | 36 | 8302968
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the SEDALIA5 to SEDEAST5 161kV line 1 | TBD | Rebuild the existing SEDALIA5 to SEDEAST5 161 kV line 1 (8.32 miles) to a standard rating of 557 MVA | KCPL | 36 | 8138823.68
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the AUR124 5 to G19-035-TAP 161kV line 1 | TBD | Rebuild the existing AUR124 5 to G19-035-TAP 161 kV line 1 (8.3 miles) to a standard rating of 557 MVA | EMDE | 36 | 8119259.2
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the ELPASO 4 to ROSEHIL4 138kV line 1 | TBD | Rebuild the existing ELPASO 4 to ROSEHIL4 138 kV line 1 (8.37 miles) to a standard rating of 478 MVA | WERE | 36 | 8070010.83
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new 300 MVAR cap bank at DELWARE7 | TBD | Build a new 300 MVAR cap bank at DELWARE7 345 kV | AEPW | 36 | 7467300
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the WEAVER 4 to ROSEHIL4 138kV line 1 | TBD | Rebuild the existing WEAVER 4 to ROSEHIL4 138 kV line 1 (7.51 miles) to a standard rating of 478 MVA | WERE | 36 | 7240834.09
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the LITCH 5 to ASB349 5 161kV line 1 | TBD | Rebuild the existing LITCH 5 to ASB349 5 161 kV line 1 (6.8 miles) to a standard rating of 557 MVA | WERE/EMDE | 36 | 6651923.2
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the BLUMILS5 to ECKLES-161 161kV line 1 | TBD | Rebuild the existing BLUMILS5 to ECKLES-161 161 kV line 1 (6.5 miles) to a standard rating of 557 MVA | KCPL/INDN | 36 | 6358456
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the OAK 2 to STROTHR2 69kV line 1 | TBD | Rebuild the existing OAK 2 to STROTHR2 69 kV line 1 (6.75 miles) to a local TO rating of 108 MVA | WERE | 36 | 6135405.75
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the LITCH 5 to FRANKLIN5 161kV line 1 | TBD | Rebuild the existing LITCH 5 to FRANKLIN5 161 kV line 1 (6.22 miles) to a standard rating of 557 MVA | WERE | 36 | 6084553.28
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 5MOCITYB1 to ECKLES-161 161kV line 1 | TBD | Rebuild the existing 5MOCITYB1 to ECKLES-161 161 kV line 1 (6.07 miles) to a standard rating of 557 MVA | AECI/INDN | 36 | 5937819.68
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the FLINTCR5 to DEC392 5 161kV line 1 | TBD | Rebuild the existing FLINTCR5 to DEC392 5 161 kV line 1 (6.03 miles) to a standard rating of 557 MVA | AEPW/EMDE | 36 | 5898690.72
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new RIV4525 to G20-079-TAP 161kV line 2 | TBD | Build a new RIV4525 to G20-079-TAP 161 kV line 2 (5.47 miles) to a standard rating of 557 MVA | EMDE | 36 | 5720214.21
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Rebuild the LEVEE5 to NEASTN 161kV line 1 | TBD | Rebuild the LEVEE5 to NEASTN 161kV line CKT1 (5.19 miles) to a standard rating of 557 MVA | KCPL | 36 | 5076982.56
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the BLUMILS5 to BLUVLY-161 161kV line 1 | TBD | Rebuild the existing BLUMILS5 to BLUVLY-161 161 kV line 1 (4.7 miles) to a standard rating of 557 MVA | KCPL/INDN | 36 | 4597652.8
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new CARTHAG5 to CAR395 5 161kV line 2 | TBD | Build a new CARTHAG5 to CAR395 5 161 kV line 2 (4.14 miles) to a standard rating of 557 MVA | SWPA/EMDE | 36 | 4329376.02
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the CARTHAG5 to CAR395 5 161kV line 1 | TBD | Rebuild the existing CARTHAG5 to CAR395 5 161 kV line 1 (4.14 miles) to a standard rating of 557 MVA | SWPA/EMDE | 36 | 4049847.36
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161kV line 1 | TBD | Rebuild the existing LBRTYST5 to BRMGHAM5 161 kV line 1 (4.03 miles) to a standard rating of 557 MVA | KCPL | 36 | 3942242.72
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the SIBLEYRD5 to NOL435 5 161kV line 1 | TBD | Rebuild the existing SIBLEYRD5 to NOL435 5 161 kV line 1 (3.93 miles) to a standard rating of 557 MVA | EMDE | 36 | 3844420.32
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 7SPORTSMAN to GRDA1 7 345kV line 1 | TBD | Rebuild the existing 7SPORTSMAN to GRDA1 7 345 kV line 1 (3.23 miles) to a standard rating of 1792 MVA | AECI/GRDA | 36 | 3696554.12
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Replace Neosho TX-4 161/138 kV transformer 1 | TBD | Replace existing Neosho TX-4 161/138 kV transformer 1 | WERE | 36 | 3606166
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the LLAN ET4 to E41ST_W4 138kV line 1 | TBD | Rebuild the existing LLAN ET4 to E41ST_W4 138 kV line 1 (3.46 miles) to a standard rating of 286 MVA | AEPW | 36 | 3335990.14
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the SIBLEYPL to ECKLES-161 161kV line 1 | TBD | Rebuild the existing SIBLEYPL to ECKLES-161 161 kV line 1 (3.09 miles) to a standard rating of 557 MVA | KCPL/INDN | 36 | 3022712.16
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the LLAN ET4 to CATOOSA4 138kV line 1 | TBD | Rebuild the existing LLAN ET4 to CATOOSA4 138 kV line 1 (2.84 miles) to a standard rating of 286 MVA | AEPW | 36 | 2738211.56
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the MAYO--N4 to E41ST_W4 138kV line 1 | TBD | Rebuild the existing MAYO--N4 to E41ST_W4 138 kV line 1 (2.6 miles) to a standard rating of 286 MVA | AEPW | 36 | 2506813.4
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the STROTHR2 to WINFLD 2 69kV line 1 | TBD | Rebuild the existing STROTHR2 to WINFLD 2 69 kV line 1 (2.3 miles) to a local TO rating of 108 MVA | WERE | 36 | 2090582.7
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the OAK 2 to PRAIRIJ2 69kV line 1 | TBD | Rebuild the existing OAK 2 to PRAIRIJ2 69 kV line 1 (1.97 miles) to a local TO rating of 108 MVA | WERE | 36 | 1790629.53
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the CATOOSA4 to LLANETP4 138kV line 1 | TBD | Rebuild the existing CATOOSA4 to LLANETP4 138 kV line 1 (1.8 miles) to a standard rating of 286 MVA | AEPW | 36 | 1735486.2
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the MINGO-N4 to MAYO--N4 138kV line 1 | TBD | Rebuild the existing MINGO-N4 to MAYO--N4 138 kV line 1 (1.75 miles) to a standard rating of 286 MVA | AEPW | 36 | 1687278.25
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new FINNEY to HOLCOMB7 345kV line 3 | TBD | Build a new FINNEY to HOLCOMB7 345 kV line 3 (0.75 miles) to a standard rating of 1792 MVA | SPS/SUNC | 36 | 1124696.25
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new 30 MVAR cap bank at TV1MNDV4 | TBD | Build a new 30 MVAR cap bank at TV1MNDV4 138 kV | WERE | 36 | 898410
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new LACYGNE7 to G20-007-TAP 345kV line 2 | TBD | Build a new LACYGNE7 to G20-007-TAP 345 kV line 2 (0.59 miles) to a standard rating of 1792 MVA | KCPL | 36 | 884761.05
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the G22-100-TAP to G23-115-TAP 161kV line 1 | TBD | Rebuild the existing G22-100-TAP to G23-115-TAP 161 kV line 1 (0.8 miles) to a standard rating of 557 MVA | KCPL | 36 | 782579.2
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 5MANSFDMN to G23-085-TAP 161kV line 1 | TBD | Rebuild the existing 5MANSFDMN to G23-085-TAP 161 kV line 1 (0.8 miles) to a standard rating of 557 MVA | AECI/SWPA | 36 | 782579.2
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new LANG 3 to G22-007-TAP 115kV line 2 | TBD | Build a new LANG 3 to G22-007-TAP 115 kV line 2 (0.41 miles) to a standard rating of 239 MVA | WERE | 36 | 368494.47
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 5MOCITYB2 to G23-169-TAP 161kV line 1 | TBD | Rebuild the existing 5MOCITYB2 to G23-169-TAP 161 kV line 1 (0.35 miles) to a standard rating of 557 MVA | AECI/KCPL | 36 | 342378.4
Current Study | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build a new 10 MVAR cap bank at HUDSON-2 | TBD | Build a new 10 MVAR cap bank at HUDSON-2 69 kV | WERE | 36 | 340100
Current Study | Steady State | 03 CENTRAL / 04 SOUTHEAST | DISIS-2023-001 | NRIS | Build a new CARTHAG5 161/69 kV transformer 3 | TBD | Build a new CARTHAG5 161/69 kV transformer 3 to a standard rating of 84 MVA | UTILITY/SWPA | 36 | 3606166
Current Study | Steady State | 03 CENTRAL/04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the G22-013-TAP to G23-231-TAP 345kV line 1 | TBD | Rebuild the existing G22-013-TAP to G23-231-TAP 345 kV line 1 (24.8 miles) to a standard rating of 1792 MVA | WERE | 36 | 28382211.2
Current Study | Steady State | 03 CENTRAL/04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345kV line 1 | TBD | Rebuild the existing NEOSHO 7 to G23-231-TAP 345 kV line 1 (15.3 miles) to a standard rating of 1792 MVA | WERE | 36 | 17509993.2
Current Study | Steady State | 03 CENTRAL/04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ORO110 5 to RIV4525 161kV line 1 | TBD | Rebuild the existing ORO110 5 to RIV4525 161 kV line 1 (11.9 miles) to a standard rating of 557 MVA | EMDE | 36 | 11640865.6
Current Study | Steady State | 03 CENTRAL/04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the LACYGNE7 to G17-209-TAP 345kV line 1 | TBD | Rebuild the existing LACYGNE7 to G17-209-TAP 345 kV line 1 (8.35 miles) to a standard rating of 1792 MVA | KCPL | 36 | 9556107.4
Current Study | Steady State | 03 CENTRAL/04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new Grove 161/138 kV transformer 2 | TBD | Build a new Grove 161/138 kV transformer 2 | AEPW | 36 | 3606166
Current Study | Steady State | 03 CENTRAL/05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the MINGO 7 to SETAB 7 345kV line 1 | TBD | Rebuild the existing MINGO 7 to SETAB 7 345 kV line 1 (57.95 miles) to a standard rating of 1792 MVA | SUNC | 36 | 66320529.8
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new ELKCITY to G22-145-TAP 138kV line 1 | TBD | Build a new ELKCITY to G22-145-TAP 138kV line CKT1 (49.812 miles) to a standard rating of 286 MVA | AEPW | 36 | 41531452.37
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the G17-209-TAP to G22-013-TAP 345kV line 1 | TBD | Rebuild the G17-209-TAP to G22-013-TAP 345kV line CKT1 (35.05 miles) to a standard rating of 1792 MVA | KCPL/WERE | 36 | 40112762.2
Contingent | Steady State | 04 SOUTHEAST | 2021 ITP | ERIS | Multi - Rocky Point - OG&E Marietta - WFEC Marietta 138 kV Rebuild | 143806 /143815 /143816 /143817 /144173 | Build new 2.1 mile 138 kV line from Marietta Tap (OKGE) – Marietta Switchyard (WFEC). Convert the Marietta 2 substation from 69 kV to 138 kV and install terminal equipment to support a new 138 kV line from Marietta 4. Rebuild the existing 69 kV line from Rocky Point to Marietta 2 as a 138 kV line. Replace the existing relays at Rocky Point. Install terminal equipment at WFEC Marietta Switch to support a new 138 kV line from OG&E Marietta. (NTC 210656 & 210657) | OKGE | 36 | 34759778
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ANADARK4 to CHERRYRD4 138kV line 1 | TBD | Rebuild the ANADARK4 to CHERRYRD4 138kV line CKT1 (25.15 miles) to a standard rating of 478 MVA | WFEC | 36 | 24248598.85
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the NEO1845 to NOL4355 161kV line 1 | TBD | Rebuild the NEO1845 to NOL4355 161kV line CKT1 (23.13 miles) to a standard rating of 557 MVA | EMDE | 36 | 22626321.12
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ALLEN4 to TUPELO4 138kV line 1 | TBD | Rebuild the ALLEN4 to TUPELO4 138kV line CKT1 (19.4 miles) to a standard rating of 286 MVA | SWPA | 36 | 18704684.6
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the RUSSEL4 to G23-148-TAP 138kV line 1 | TBD | Rebuild the RUSSEL4 to G23-148-TAP 138kV line CKT1 (19.25 miles) to a standard rating of 286 MVA | WFEC/AEPW | 36 | 18560060.75
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new HANNA to WELEETK 138kV line 1 | TBD | Build a new HANNA to WELEETK 138kV line CKT1 (21.204 miles) to a standard rating of 478 MVA | SWPA/WFEC | 36 | 17679131.86
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the LAKE4WPT to G23-148-TAP 138kV line 1 | TBD | Rebuild the LAKE4WPT to G23-148-TAP 138kV line CKT1 (18.2 miles) to a standard rating of 286 MVA | AEPW | 36 | 17547693.8
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ADAIR2 to VINITA 2 line 69kV | TBD | Rebuild the ADAIR2 to VINITA 2 line 69kV (19.11 miles) to a standard rating of 71 MVA | AEPW | 36 | 17370015.39
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the MDCPRK4 to CACHEJ4 138kV line 1 | TBD | Rebuild the MDCPRK4 to CACHEJ4 138kV line CKT1 (16.97 miles) to a standard rating of 478 MVA | WFEC | 36 | 16361778.23
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the WELEETK4 to GREASYC4 138kV line 1 | TBD | Rebuild the WELEETK4 to GREASYC4 138kV line CKT1 (16.28 miles) to a standard rating of 286 MVA | SWPA | 36 | 15696508.52
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the GORE5 to MUSKTAP5 161kV line 1 | TBD | Rebuild the GORE5 to MUSKTAP5 161kV line CKT1 (16 miles) to a standard rating of 557 MVA | SWPA | 36 | 15651584
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the LAKEP2WT to ELDORADO2 69kV line 1 | TBD | Rebuild the LAKEP2WT to ELDORADO2 69kV line CKT1 (16.32 miles) to a standard rating of 71 MVA | AEPW/WFEC | 36 | 14834047.68
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the EXPLOR4 to ALLEN4 138kV line 1 | TBD | Rebuild the EXPLOR4 to ALLEN4 138kV line CKT1 (14.8 miles) to a standard rating of 286 MVA | SWPA | 36 | 14269553.2
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new AFTON5 to MIAMI5 161kV line 2 | TBD | Build a new AFTON5 to MIAMI5 161kV line CKT2 (13.5 miles) to a standard rating of 557 MVA | GRDA | 36 | 14117530.5
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the SBROWN4 to G23-020-TAP 138kV line 1 | TBD | Rebuild the SBROWN4 to G23-020-TAP 138kV line CKT1 (14.17 miles) to a standard rating of 478 MVA | SWPA/WFEC | 36 | 13662133.03
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the SNYDER2 to TOMSTEED2 69kV line 1 | TBD | Rebuild the SNYDER2 to TOMSTEED2 69kV line CKT1 (15.01 miles) to a standard rating of 71 MVA | AEPW | 36 | 13643324.49
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the MCGEETP2 to ANTLTAP2 69kV line 1 | TBD | Rebuild the MCGEETP2 to ANTLTAP2 69kV line CKT1 (14.83 miles) to a standard rating of 71 MVA | AEPW | 36 | 13479713.67
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the GREENLF2 to MUSKSW2 69kV line 1 | TBD | Rebuild the GREENLF2 to MUSKSW2 69kV line CKT1 (14.73 miles) to a standard rating of 71 MVA | GRDA | 36 | 13388818.77
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the MIAMI5 to AFTON5 161kV line 1 | TBD | Rebuild the MIAMI5 to AFTON5 161kV line CKT1 (13.5 miles) to a standard rating of 557 MVA | GRDA | 36 | 13206024
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the 4WOODY to PHAROAH4 138kV line 1 | TBD | Rebuild the 4WOODY to PHAROAH4 138kV line CKT1 (13.36 miles) to a standard rating of 286 MVA | AECI/WFEC | 36 | 12881164.24
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the AFTON5 to KETCHUM5 161kV line 1 | TBD | Rebuild the AFTON5 to KETCHUM5 161kV line CKT1 (12.8 miles) to a standard rating of 557 MVA | GRDA | 36 | 12521267.2
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the HLDTNTP4 to LOCO4 138kV line 1 | TBD | Rebuild the HLDTNTP4 to LOCO4 138kV line CKT1 (12.85 miles) to a standard rating of 286 MVA | WFEC | 36 | 12389443.15
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the NWT-BNT4 to G18-003-TAP 138kV line 1 | TBD | Rebuild the NWT-BNT4 to G18-003-TAP 138kV line CKT1 (12.49 miles) to a standard rating of 478 MVA | AEPW | 36 | 12042345.91
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the 2CHECDST to SUMMIT2 69kV line 1 | TBD | Rebuild the 2CHECDST to SUMMIT2 69kV line CKT1 (12.9 miles) to a standard rating of 71 MVA | AECI/GRDA | 36 | 11725442.1
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the RUSSET-4 to STIRLNG4 138kV line 1 | TBD | Rebuild the RUSSET-4 to STIRLNG4 138kV line CKT1 (12.11 miles) to a standard rating of 286 MVA | OKGE | 36 | 11675965.49
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the PAYNESW4 to PAOLI4 138kV line 1 | TBD | Rebuild the PAYNESW4 to PAOLI4 138kV line CKT1 (12 miles) to a standard rating of 286 MVA | WFEC | 36 | 11569908
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the CANEYCK4 to LTLCITY4 138kV line 1 | TBD | Rebuild the CANEYCK4 to LTLCITY4 138kV line CKT1 (11.79 miles) to a standard rating of 478 MVA | OKGE | 36 | 11367434.61
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the HUGO-2 to VALYTIM2 69kV line 1 | TBD | Rebuild the HUGO-2 to VALYTIM2 69kV line CKT1 (12.22 miles) to a standard rating of 71 MVA | AEPW | 36 | 11107356.78
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new FIXCT4 to MAUD4 138kV line 1 | TBD | Build a new FIXCT4 to MAUD4 138kV line CKT1 (13.2 miles) to a standard rating of 286 MVA | AEPW/OKGE | 36 | 11005684.8
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the AVOCA5 to BEAVER5 161kV line 1 | TBD | Rebuild the AVOCA5 to BEAVER5 161kV line CKT1 (11 miles) to a standard rating of 557 MVA | AEPW/SWPA | 36 | 10760464
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ELDORDJ2 to ELDORDO2 69kV line 1 | TBD | Rebuild the ELDORDJ2 to ELDORDO2 69kV line CKT1 (11.49 miles) to a standard rating of 71 MVA | WFEC | 36 | 10443824.01
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the GROVE4 to G23-162-TAP 138kV line 1 | TBD | Rebuild the GROVE4 to G23-162-TAP 138kV line CKT1 (10.53 miles) to a standard rating of 286 MVA | AEPW | 36 | 10152594.27
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the DUSTIN4 to HANNA4 138kV line 1 | TBD | Rebuild the DUSTIN4 to HANNA4 138kV line CKT1 (10.37 miles) to a standard rating of 478 MVA | WFEC | 36 | 9998328.83
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the JOHNCO4 to RUSSET4 138kV line 1 | TBD | Rebuild the JOHNCO4 to RUSSET4 138kV line CKT1 (9.84 miles) to a standard rating of 478 MVA | OKGE | 36 | 9487324.56
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the OKAYGR2 to MUSKSW2 69kV line 1 | TBD | Rebuild the OKAYGR2 to MUSKSW2 69kV line CKT1 (10.16 miles) to a standard rating of 71 MVA | GRDA | 36 | 9234921.84
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new RIV4525 to HOC4045 161kV line 1 | TBD | Build a new RIV4525 to HOC4045 161kV line CKT1 (8.64 miles) to a standard rating of 557 MVA | EMDE | 36 | 9035219.52
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the GORE5 to G23-145-TAP 161kV line 1 | TBD | Rebuild the GORE5 to G23-145-TAP 161kV line CKT1 (9.2 miles) to a standard rating of 557 MVA | SWPA | 36 | 8999660.8
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the AOCPT2 to LULA2 69kV line 1 | TBD | Rebuild the AOCPT2 to LULA2 69kV line CKT1 (9.27 miles) to a standard rating of 143 MVA | OKGE | 36 | 8425957.23
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new HUGO7 345/138 kV transformer 2 | TBD | Build a new HUGO7 345/138 kV transformer 2 to a standard rating of 500 MVA | WFEC | 36 | 8302968
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new CHAMSPR5 345/161 kV transformer 2 | TBD | Build a new CHAMSPR5 345/161 kV transformer 2 to a standard rating of 675 MVA | UTILITY/AEPW | 36 | 8302968
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new TONTITN7 345/161 kV transformer 2 | TBD | Build a new TONTITN7 345/161 kV transformer 2 to a standard rating of 675 MVA | UTILITY/AEPW | 36 | 8302968
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the RUSSET4 to GLASSES4 138kV line 1 | TBD | Rebuild the RUSSET4 to GLASSES4 138kV line CKT1 (8.33 miles) to a standard rating of 286 MVA | OKGE | 36 | 8031444.47
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ATOKA-4 to LEHIGH-4 138kV line 1 | TBD | Rebuild the ATOKA-4 to LEHIGH-4 138kV line CKT1 (7.99 miles) to a standard rating of 286 MVA | AEPW | 36 | 7703630.41
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the BROWNTP4 to BODLE4 138kV line 1 | TBD | Rebuild the BROWNTP4 to BODLE4 138kV line CKT1 (7.56 miles) to a standard rating of 286 MVA | OKGE | 36 | 7289042.04
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the MUSKTAP5 to FTGIB5 161kV line 1 | TBD | Rebuild the MUSKTAP5 to FTGIB5 161kV line CKT1 (7.4 miles) to a standard rating of 557 MVA | SWPA | 36 | 7238857.6
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ATOKA-2 to LANE2 69kV line 1 | TBD | Rebuild the ATOKA-2 to LANE2 69kV line CKT1 (7.93 miles) to a standard rating of 71 MVA | AEPW | 36 | 7207965.57
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the LASALLE4 to LATTAJT4 138kV line 1 | TBD | Rebuild the LASALLE4 to LATTAJT4 138kV line CKT1 (7.1 miles) to a standard rating of 286 MVA | WFEC | 36 | 6845528.9
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ELDORDJ2 to GYPSUM2 69kV line 1 | TBD | Rebuild the ELDORDJ2 to GYPSUM2 69kV line CKT1 (7.51 miles) to a standard rating of 71 MVA | WFEC | 36 | 6826206.99
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ROKHILL4 to G23-059-TAP 138kV line 1 | TBD | Rebuild the ROKHILL4-138 to G23-059-TAP 138kV line CKT1 (7 miles) to a standard rating of 286 MVA | AEPW | 36 | 6749113
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the RIV4525 to STL4395 161kV line 1 | TBD | Rebuild the RIV4525 to STL4395 161kV line CKT1 (6.82 miles) to a standard rating of 557 MVA | EMDE | 36 | 6671487.68
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the GREASYC4 to EXPLOR4 138kV line 1 | TBD | Rebuild the GREASYC4 to EXPLOR4 138kV line CKT1 (6.91 miles) to a standard rating of 286 MVA | SWPA | 36 | 6662338.69
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the RSKERR5 to SUNSTCN5 161kV line 1 | TBD | Rebuild the RSKERR5 to SUNSTCN5 161kV line CKT1 (6.8 miles) to a standard rating of 557 MVA | SWPA/OKGE | 36 | 6651923.2
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the PRY-JCT4 to G23-027-TAP 138kV line 1 | TBD | Rebuild the PRY-JCT4 to G23-027-TAP line CKT1 (6.77 miles) to a standard rating of 286 MVA | AEPW | 36 | 6527356.43
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the PENSA5 to G23-049-TAP 161kV line 1 | TBD | Rebuild the PENSA5 to G23-049-TAP 161kV line CKT1 (6.5 miles) to a standard rating of 557 MVA | GRDA | 36 | 6358456
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the DUNCNJT2 to HARISBG2 69kV line 1 | TBD | Rebuild the DUNCNJT2 to HARISBG2 69kV line CKT1 (6.99 miles) to a standard rating of 71 MVA | WFEC | 36 | 6353553.51
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the LTLCITY4 to BROWNTP4 138kV line 1 | TBD | Rebuild the LTLCITY4 to BROWNTP4 138kV line CKT1 (6.37 miles) to a standard rating of 478 MVA | OKGE | 36 | 6141692.83
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the LASALLE4 to STNWLTP4 138kV line 1 | TBD | Rebuild the LASALLE4 to STNWLTP4 138kV line CKT1 (6.3 miles) to a standard rating of 286 MVA | WFEC | 36 | 6074201.7
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new KERRGR5 to MAID5 161kV line 3 | TBD | Build a new KERRGR5 to MAID5 161kV line CKT3 (5.6 miles) to a standard rating of 198 MVA | GRDA | 36 | 5856160.8
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the FTGIB5 to OKAYGR5 161kV line 1 | TBD | Rebuild the FTGIB5 to OKAYGR5 161kV line CKT1 (5.9 miles) to a standard rating of 557 MVA | SWPA/GRDA | 36 | 5771521.6
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the LANE2 to G23-070-TAP 69kV line 1 | TBD | Rebuild the LANE2 to G23-070-TAP 69kV line CKT1 (6.3 miles) to a standard rating of 71 MVA | AEPW | 36 | 5726378.7
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the AVOCA5 to EROGERS5 161kV line 1 | TBD | Rebuild the AVOCA5 to EROGERS5 161kV line CKT1 (5.81 miles) to a standard rating of 557 MVA | AEPW | 36 | 5683481.44
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the BASELIN2 to VELMA2 69kV line 1 | TBD | Rebuild the BASELIN2 to VELMA2 69kV line CKT1 (5.67 miles) to a standard rating of 71 MVA | WFEC | 36 | 5153740.83
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the MADINDT4 to CANEYCK4 138kV line 1 | TBD | Rebuild the MADINDT4 to CANEYCK4 138kV line CKT1 (5.29 miles) to a standard rating of 286 MVA | OKGE | 36 | 5100401.11
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the DRYGULCH5 to G23-028-TAP 161kV line 1 | TBD | Rebuild the DRYGULCH5 to G23-028-TAP 161kV line CKT1 (4.82 miles) to a standard rating of 557 MVA | GRDA | 36 | 4715039.68
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the PENSA5 to KETCHUM5 161kV line 1 | TBD | Rebuild the PENSA5 to KETCHUM5 161kV line CKT1 (4.8 miles) to a standard rating of 557 MVA | GRDA | 36 | 4695475.2
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the 2J6 to AFTPTP2 69kV line 1 | TBD | Rebuild the 2J6 to AFTPTP2 69kV line CKT1 (5.13 miles) to a standard rating of 122 MVA | AECI/GRDA | 36 | 4662908.37
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the LATTAJT4 to OILCRTP4 138kV line 1 | TBD | Rebuild the LATTAJT4 to OILCRTP4 138kV line CKT1 (4.55 miles) to a standard rating of 286 MVA | WFEC | 36 | 4386923.45
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the RUSSETT4 to G23-020-TAP 138kV line 1 | TBD | Rebuild the RUSSETT4 to G23-020-TAP 138kV line CKT1 (4.45 miles) to a standard rating of 478 MVA | WFEC | 36 | 4290507.55
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the PRY-JCT2 to PRYORC12 69kV line 1 | TBD | Rebuild the PRY-JCT2 to PRYORC12 69kV line CKT1 (4.65 miles) to a standard rating of 122 MVA | AEPW/GRDA | 36 | 4226612.85
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the MCGEETP2 to G23-070-TAP 69kV line 1 | TBD | Rebuild the MCGEETP2 to G23-070-TAP 69kV line CKT1 (4.59 miles) to a standard rating of 71 MVA | AEPW | 36 | 4172075.91
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the LULA4 to STNWLSW4 138kV line 1 | TBD | Rebuild the LULA4 to STNWLSW4 138kV line CKT1 (3.94 miles) to a standard rating of 478 MVA | OKGE/WFEC | 36 | 3798786.46
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the CACHEJ5 to G20-016-TAP 138kV 1 | TBD | Rebuild the CACHEJ5 to G20-016-TAP 138kV CKT1 (3.94 miles) to a standard rating of 286 MVA | WFEC | 36 | 3798786.46
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new RUSSETT4 to G23-020-TAP 138kV line 2 | TBD | Build a new RUSSETT4 to G23-020-TAP 138kV line CKT2 (4.45 miles) to a standard rating of 478 MVA | WFEC | 36 | 3710249.8
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the HRSBGSW2 to HARISBG2 69kV line 1 | TBD | Rebuild the HRSBGSW2 to HARISBG2 69kV line CKT1 (4.05 miles) to a standard rating of 71 MVA | WFEC | 36 | 3681243.45
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the WELEETK5 161/138 kV transformer 1 | TBD | Upgrade the WELEETK5 161/138 kV transformer 1 to a standard rating of 200 MVA | SWPA | 36 | 3606166
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new GROVE 161/138 kV transformer 3 | TBD | Build a new GROVE 161/138 kV transformer 3 to a standard rating of 112 MVA | AEPW | 36 | 3606166
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new HOC404 161/138 kV transformer 3 | TBD | Build a new HOC404 161/138 kV transformer 3 to a standard rating of 165 MVA | EMDE | 36 | 3606166
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the VBI 161/69 kV transformer 2 | TBD | Upgrade the VBI 161/69 kV transformer 2 to a standard rating of 250 MVA | OKGE | 36 | 3606166
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the SNYDER-4 to SNYDER4 138kV line 1 | TBD | Rebuild the SNYDER-4 to SNYDER4 138kV line CKT1 (3.7 miles) to a standard rating of 286 MVA | AEPW/WFEC | 36 | 3567388.3
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the DUKE2 to GYPSUM2 69kV line 1 | TBD | Rebuild the DUKE2 to GYPSUM2 69kV line CKT1 (3.6 miles) to a standard rating of 71 MVA | WFEC | 36 | 3272216.4
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ILLINOTP2 to GREENLF2 69kV line 1 | TBD | Rebuild the ILLINOTP2 to GREENLF2 69kV line CKT1 (3.51 miles) to a standard rating of 71 MVA | GRDA | 36 | 3190410.99
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the VALYTIM2 to ANTLTAP2 69kV line 1 | TBD | Rebuild the VALYTIM2 to ANTLTAP2 69kV line CKT1 (3.5 miles) to a standard rating of 71 MVA | AEPW | 36 | 3181321.5
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the LULA4 138/69 kV transformer 1 | TBD | Upgrade the LULA4 138/69 kV transformer 1 to a standard rating of 250 MVA | OKGE | 36 | 3128743
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the GRANFLD2 138/69 kV transformer 1 | TBD | Upgrade the GRANFLD2 138/69 kV transformer 1 to a standard rating of 250 MVA | WFEC | 36 | 3128743
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the ATOKA-4 138/69 kV transformer 1 | TBD | Upgrade the ATOKA-4 138/69 kV transformer 1 to a standard rating of 250 MVA | AEPW | 36 | 3128743
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the RUSSELL2 138/69 kV transformer 1 | TBD | Upgrade the RUSSELL2 138/69 kV transformer 1 to a standard rating of 250 MVA | WFEC | 36 | 3128743
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the BASELIN2 138/69 kV transformer 1 | TBD | Upgrade the BASELIN2 138/69 kV transformer 1 to a standard rating of 250 MVA | WFEC | 36 | 3128743
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the MDCPRK4 to PARADSE4 138kV line 1 | TBD | Rebuild the MDCPRK4 to PARADSE4 138kV line CKT1 (3.2 miles) to a standard rating of 478 MVA | WFEC | 36 | 3085308.8
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the ACOPA2 to ACOPT2 69kV line 1 | TBD | Rebuild the ACOPA2 to ACOPT2 69kV line CKT1 (3.28 miles) to a standard rating of 143 MVA | OKGE | 36 | 2981352.72
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the PCP-TAP2 to HUNTAP-2 69kV line 1 | TBD | Rebuild the PCP-TAP2 to HUNTAP-2 161kV line CKT1 (3.07 miles) to a standard rating of 71 MVA | AEPW | 36 | 2790473.43
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the PCP-TAP2 to PRYORC12 69kV line 1 | TBD | Rebuild the PCP-TAP2 to PRYORC12 69kV line CKT1 (3.03 miles) to a standard rating of 71 MVA | AEPW/GRDA | 36 | 2754115.47
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the HRSBGSW2 to VELMA2 69kV line 1 | TBD | Rebuild the HRSBGSW2 to VELMA2 69kV line CKT1 (2.95 miles) to a standard rating of 71 MVA | WFEC | 36 | 2681399.55
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the PARKLN2 to ADAINDU2 69kV line 1 | TBD | Rebuild the PARKLN2 to ADAINDU2 69kV line CKT1 (2.87 miles) to a standard rating of 143 MVA | OKGE | 36 | 2608683.63
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the WELEETK4 to WELETK4 138kV line 1 | TBD | Rebuild the WELEETK4 to WELETK4 138kV line CKT1 (2.62 miles) to a standard rating of 478 MVA | SWPA/AEPW | 36 | 2526096.58
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the PARADSE4 to CHERRYRD4 138kV line 1 | TBD | Rebuild the PARADSE4 to CHERRYRD4 138kV line CKT1 (2.6 miles) to a standard rating of 478 MVA | WFEC | 36 | 2506813.4
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the FNDTION4 to SPRNDAL4 138kV line 1 | TBD | Rebuild the FNDTION4 to SPRNDAL4 138kV line CKT1 (2.58 miles) to a standard rating of 286 MVA | OKGE | 36 | 2487530.22
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the OKMULGE4 to KELCO4 138kV line 1 | TBD | Rebuild the OKMULGE4 to KELCO4 138kV line CKT1 (2.24 miles) to a standard rating of 286 MVA | AEPW | 36 | 2159716.16
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the DRPSPRG4 to STIRLNG4 138kV line 1 | TBD | Rebuild the DRPSPRG4 to STIRLNG4 138kV line CKT1 (2.23 miles) to a standard rating of 286 MVA | OKGE | 36 | 2150074.57
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the RSKERR5 to G23-064-TAP 161kV line 1 | TBD | Rebuild the RSKERR5 to G23-064-TAP 161kV line CKT1 (2 miles) to a standard rating of 557 MVA | SWPA | 36 | 1956448
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the 2J6 to VINEOTP2 69kV line 1 | TBD | Rebuild the 2J6 to VINEOTP2 69kV line CKT1 (2.1 miles) to a standard rating of 122 MVA | AECI/GRDA | 36 | 1908792.9
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the FNDTION4 to CHIKSAW4 138kV line 1 | TBD | Rebuild the FNDTION4 to CHIKSAW4 138kV line CKT1 (1.72 miles) to a standard rating of 286 MVA | OKGE | 36 | 1658353.48
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the NNBOSTN4 to G18-003-TAP 138kV line 1 | TBD | Rebuild the NNBOSTN4 to G18-003-TAP 138kV line CKT1 (1.7 miles) to a standard rating of 478 MVA | AEPW | 36 | 1639070.3
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the 5HEBERN# to GREERSF5 161kV line 1 | TBD | Rebuild the 5HEBERN# to GREERSF5 161kV line CKT1 (1.66 miles) to a standard rating of 557 MVA | EES-EAI/SWPA | 36 | 1623851.84
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the TARBY5 to SHAD-PT5 161kV line 1 | TBD | Rebuild the TARBY5 to SHAD-PT5 161kV line CKT1 (1.53 miles) to a standard rating of 557 MVA | OKGE | 36 | 1496682.72
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the VALLYU2 to AOCPA2 69kV line 1 | TBD | Rebuild the VALLYU2 to AOCPA2 69kV line CKT1 (1.62 miles) to a standard rating of 143 MVA | OKGE | 36 | 1472497.38
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line 1 | TBD | Rebuild the SPRNDAL4 to DRPSPRG4 138kV line CKT1 (1.25 miles) to a standard rating of 286 MVA | OKGE | 36 | 1205198.75
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the NEWBOST2 to NNBOSTN2 69kV line 1 | TBD | Rebuild the NEWBOST2 to NNBOSTN2 69kV line CKT1 (1.3 miles) to a standard rating of 122 MVA | AEPW | 36 | 1181633.7
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the TUPELO4 to STNWLSW4 138kV line 1 | TBD | Rebuild the TUPELO4 to STNWLSW4 138kV line CKT1 (1.18 miles) to a standard rating of 478 MVA | SWPA/WFEC | 36 | 1137707.62
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the COLBRT-4 to COLBERT4 138kV line 1 | TBD | Rebuild the COLBRT-4 to COLBERT4 138kV line CKT1 (1.01 miles) to a standard rating of 478 MVA | OKGE/WFEC | 36 | 973800.59
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | REPLACE the breaker at DUKE | TBD | Replace the existing breaker at DUKE with a standard rating of 71 MVA | WFEC | 36 | 566485
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new HUGOITC4 to HUGOPP4 138kV line 2 | TBD | Build a new HUGOITC4 to HUGOPP4 138kV line CKT2 (0.64 miles) to a standard rating of 478 MVA | WFEC | 36 | 533608.96
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the GOREGR2 to ILLINOTP2 69kV line 1 | TBD | Rebuild the GOREGR2 to ILLINOTP2 69kV line CKT1 (0.52 miles) to a standard rating of 71 MVA | GRDA | 36 | 472653.48
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the TUPELO4 to ALLENGT4 138kV line 1 | TBD | Rebuild the TUPELO4 to ALLENGT4 138kV line CKT1 (0.37 miles) to a standard rating of 286 MVA | SWPA/AEPW | 36 | 356738.83
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the AFTPTP2 to EXPLTP2 69kV line 1 | TBD | Rebuild the AFTPTP2 to EXPLTP2 69kV line CKT1 (0.3 miles) to a standard rating of 122 MVA | GRDA | 36 | 272684.7
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the BROWNTP4 to STRRDTP4 138kV line 1 | TBD | Rebuild the BROWNTP4 to STRRDTP4 138kV line CKT1 (0.27 miles) to a standard rating of 478 MVA | OKGE | 36 | 260322.93
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the VANBUR5 to VBI5 161kV line Z1 | TBD | Rebuild the VANBUR5 to VBI5 161kV line CKTZ1 (0.22 miles) to a standard rating of 557 MVA | SWPA/OKGE | 36 | 215209.28
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line 1 | TBD | Rebuild the CANEYCK4 to TEXOMAJ4 138kV line CKT1 (0.17 miles) to a standard rating of 286 MVA | OKGE/WFEC | 36 | 163907.03
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the BROWN4 to STRRDTP4 138kV line 1 | TBD | Rebuild the BROWN4 to STRRDTP4 138kV line CKT1 (0.09 miles) to a standard rating of 478 MVA | OKGE | 36 | 86774.31
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the RUSSET-4 to RUSSETT4 138kV line 1 | TBD | Rebuild the RUSSET-4 to RUSSETT4 138kV line CKT1 (0.08 miles) to a standard rating of 478 MVA | OKGE/WFEC | 36 | 77132.72
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 2 | TBD | Build a new RUSSET-4 to RUSSETT4 138kV line CKT2 (0.08 miles) to a standard rating of 478 MVA | OKGE/WFEC | 36 | 66701.12
Current Study | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new RUSSET-4 to RUSSETT4 138kV line 3 | TBD | Build a new RUSSET-4 to RUSSETT4 138kV line CKT3 (0.08 miles) to a standard rating of 478 MVA | OKGE/WFEC | 36 | 66701.12
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the DRAPER7 to SEMINOL7 345kV line 2 | TBD | Rebuild the DRAPER7 to SEMINOL7 345kV line CKT2 (44.14 miles) to a standard rating of 1792 MVA | OKGE | 36 | 50515758.16
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new TOLK to NEEDMORE 230kV line 2 | TBD | Build a new TOLK to NEEDMORE 230kV line CKT2 (13.65 miles) to a standard rating of 796 MVA | SPS | 36 | 15802413.9
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the PRINGLE3 to RIVERVIEW3 115kV line 1 | TBD | Rebuild the PRINGLE3 to RIVERVIEW3 115kV line CKT1 (20.25 miles) to a standard rating of 239 MVA | SPS | 36 | 14394510
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new POTTER_CO to HARRNG_MID6 230kV line 1 | TBD | Build a new POTTER_CO to HARRNG_MID6 230kV line CKT1 (11.2 miles) to a standard rating of 796 MVA | SPS | 36 | 12966083.2
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the TOLK to NEEDMORE 230 kV line 1 | TBD | Rebuild the TOLK to NEEDMORE 230 kV line CKT1 (13.65 miles) to a standard rating of 796 MVA | SPS | 36 | 12059897.85
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new DUMAS19ST to MOORE_W 115kV line 1 | TBD | Build a new DUMAS19ST to MOORE_W 115kV line CKT1 (12.18 miles) to a standard rating of 239 MVA | SPS | 36 | 10946982.06
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new POTTERCO 345/230 kV transformer 4 | TBD | Build a new POTTERCO 345/230 kV transformer 4 to a standard rating of 559 MVA | UTILITY/SPS | 36 | 8302968
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | NRIS | Rebuild the RED_BLUFF3 to RDRUNNER3 115kV line 1 | TBD | Rebuild the RED_BLUFF3 to RDRUNNER3 115kV line CKT1 (11.54 miles) to a standard rating of 239 MVA | SPS | 36 | 8203093.6
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Upgrade the PLANTX 230/115kV transformer 1 | TBD | Upgrade the PLANTX 230/115kV transformer 1 to a standard rating of 308 MVA | SPS | 36 | 6621188
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Upgrade the PRINGLE 230/115 kV transformer 1 | TBD | Upgrade the PRINGLE 230/115 kV transformer 1 to a standard rating of 308 MVA | SPS | 36 | 6621188
Current Study | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the TAYLOR to W_BENDER 115kV line 1 | TBD | Rebuild the TAYLOR to W_BENDER 115kV line CKT1 (6.4 miles) to a standard rating of 239 MVA | SPS | 36 | 4549376
Current Study | Steady State | WECC | DISIS-2023-001 | ERIS | Columbus 230kV Subsystem Reconfiguration | TBD | Reconfigure Columbus 230kV substation to add a breaker between Shorey Road to Stillwater Wind 230kV line | NORTHWESTERN | 36 | 4606938
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Chevron Green 115 kV Substation ASGI-2023-001 Interconnection (TOIF) (SPS) | 158656 | Interconnection upgrades and cost estimates needed to interconnect ASGI-2023-001 (20MW/Solar), into Chevron Green 115 kV Substation ($0 assigned because request is not interconnecting to SPP facilities) | SPS | NA | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Chevron Green 115 kV Substation ASGI-2023-001 Interconnection (Non-Shared NU) (SPS) | 158657 | Interconnection upgrades and cost estimates needed to interconnect ASGI-2023-001 (20MW/Solar), into Chevron Green 115 kV Substation ($0 assigned because request is not interconnecting to SPP facilities) | SPS | NA | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Buckner 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | 158658 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-089/090/091 (250/250/504MW/Wind), into Buckner 345 kV Substation | SEPC | 48 | 17500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Buffalo Flats 345 kV Substation Interconnection (DISIS-2023-001) (Evergy) | 158659 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-111/118 (200/200MW/Solar/Wind), into Buffalo Flats 345 kV Substation | EVERGY | 56 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carpenter 345 kV Substation Interconnection (DISIS-2023-001) (SPS) | 158660 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-039/068/093/094 (250MW/Wind), into Carpenter 345 kV Substation | SPS | 48 | 5074514
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Chappelle Creek 345 kV Substation Interconnection (DISIS-2023-001) (BEPC) | 158661 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-105/106 (249/504MW/Wind), into Chappelle Creek 345 kV Substation | BEPC | 66 | 9637935
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Degrasse 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | 158662 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100/102 (300/475MW/Hybrid), into Degrasse 345 kV Substation | OGE | 36 | 4884856
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Delaware - Neosho 345 kV Interconnection (DISIS-2023-001) (Evergy) | 158663 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075/076 (200/100MW/Wind), into Delaware - Neosho 345 kV | EVERGY | 56 | 26369942
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | 158664 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164/165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | OGE | 48 | 4584856
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Groton - Leland Olds 345 kV Line Interconnection (DISIS-2023-001) (BEPC) | 158665 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-181/182 (100/300MW/Battery/Storage/Wind), into Groton - Leland Olds 345 kV Line | BEPC | 66 | 19903604
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Holcomb 345 kV Interconnection (DISIS-2023-001) (SUNC) | 158666 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172/173 (200/100MW/Wind), into Holcomb 345 kV | SEPC | 48 | 16000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Keystone 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | 158667 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116/117 (500/300MW/Wind), into Keystone 345 kV Substation | NPPD | 36 | 10000000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Leland Olds to Groton 345 kV Line Interconnection (DISIS-2023-001) (BEPC) | 158668 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-013/014 (200MW/Wind), into Leland Olds to Groton 345 kV Line | BEPC | 66 | 19903604
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Needmore - Yoakum 230 kV Line Interconnection (DISIS-2023-001) (SPS) | 158669 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158/159 (335/200MW/Solar/Battery/Storage), into Needmore - Yoakum 230 kV Line | SPS | 42 | 11422523
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | New Beatrice Power Station 345 kV Interconnection (DISIS-2023-001) (NPPD) | 158670 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222/223 (478/239MW/Thermal), into New Beatrice Power Station 345 kV | NPPD | 36 | 76000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Olive Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | 158671 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224/225 (478/217MW/Thermal), into Olive Creek 345 kV Substation | NPPD | 36 | 5000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | 158672 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | SPS | 42 | 80800000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Roosevelt - Tolk 230 kV line tap Interconnection (DISIS-2023-001) (SPS) | 158673 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-195/196 (250/150MW/Solar/Battery/Storage), into Roosevelt - Tolk 230 kV line tap | SPS | 42 | 11391157
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rose Hill 345 kV Substation Interconnection (DISIS-2023-001) (Evergy) | 158674 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-052/073 (300/400MW/Hybrid/Battery/Storage), into Rose Hill 345 kV Substation | EVERGY | 56 | 14112308
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | 158675 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043/044/045/046/047/048/107 (200/200/250/250/250/300MW/Solar/Wind), into Setab 345 kV Substation | SEPC | 48 | 25000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | 158676 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (303MW/Thermal), into Substation 3740 345 kV | OPPD | 48 | 19955637
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Turtle Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | 158678 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216/217/218 (200MW/Wind), into Turtle Creek 345 kV Substation | NPPD | 36 | 7000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | T14 Circuit 115 V Line GEN-2023-001 Interconnection (TOIF) (SPS) | 158679 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-001 (230MW/Solar), into T14 Circuit 115 V Line | SPS | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | T14 Circuit 115 V Line GEN-2023-001 Interconnection (Non-Shared NU) (SPS) | 158680 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-001 (230MW/Solar), into T14 Circuit 115 V Line | SPS | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Greasy Creek 138kV Switchyard GEN-2023-003 Interconnection (TOIF) (SWPA) | 158681 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-003 (200.6MW/Wind), into Greasy Creek 138kV Switchyard | SWPA | 48 | 1200000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Greasy Creek 138kV Switchyard GEN-2023-003 Interconnection (Non-Shared NU) (SWPA) | 158682 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-003 (200.6MW/Wind), into Greasy Creek 138kV Switchyard | SWPA | 48 | 89700000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Greasy Creek 138kV Switchyard GEN-2023-003 Interconnection (TOIF) (WFEC) | 158683 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-003 (200.6MW/Wind), into Greasy Creek 138kV Switchyard | WFEC | 48 | 299999
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Greasy Creek 138kV Switchyard GEN-2023-003 Interconnection (Non-Shared NU) (WFEC) | 158684 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-003 (200.6MW/Wind), into Greasy Creek 138kV Switchyard | WFEC | 48 | 600000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-005 Interconnection (TOIF) (SPS) | 158685 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005 (256MW/Solar), into Plant X 230kV Substation | SPS | 42 | 1700000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Wolf Creek- Blackberry 345 kV Line Break GEN-2023-006 Interconnection (TOIF) (NEET) | 158686 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-006 (202MW/Wind), into Wolf Creek- Blackberry 345 kV Line Break | NEET | 56 | 4001600
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Wolf Creek- Blackberry 345 kV Line Break GEN-2023-006 Interconnection (Non-Shared NU) (NEET) | 158687 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-006 (202MW/Wind), into Wolf Creek- Blackberry 345 kV Line Break | NEET | 56 | 20081200
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco - Carlisle 230 kV line GEN-2023-008 Interconnection (TOIF) (SPS) | 158688 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-008 (75MW/Solar), into Tuco - Carlisle 230 kV line | SPS | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco - Carlisle 230 kV line GEN-2023-008 Interconnection (Non-Shared NU) (SPS) | 158689 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-008 (75MW/Solar), into Tuco - Carlisle 230 kV line | SPS | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Hugo 138 kV Substation GEN-2023-009 Interconnection (TOIF) (WFEC) | 158690 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-009 (250MW/Battery/Storage), into Hugo 138 kV Substation | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Hugo 138 kV Substation GEN-2023-009 Interconnection (Non-Shared NU) (WFEC) | 158691 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-009 (250MW/Battery/Storage), into Hugo 138 kV Substation | WFEC | 48 | 1000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Moore Co 230 kV Substation GEN-2023-010 Interconnection (TOIF) (SPS) | 158692 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-010 (280MW/Wind), into Moore Co 230 kV Substation | SPS | 42 | 1700000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Moore Co 230 kV Substation GEN-2023-010 Interconnection (Non-Shared NU) (SPS) | 158693 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-010 (280MW/Wind), into Moore Co 230 kV Substation | SPS | 42 | 2485000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Harbine 115 kV Substation GEN-2023-011 Interconnection (TOIF) (NPPD) | 158694 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-011 (190MW/Wind), into Harbine 115 kV Substation | NPPD | 36 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Harbine 115 kV Substation GEN-2023-011 Interconnection (Non-Shared NU) (NPPD) | 158695 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-011 (190MW/Wind), into Harbine 115 kV Substation | NPPD | 36 | 1500000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Kingsbury County 115kV Substation GEN-2023-012 Interconnection (TOIF) (EREP) | 158696 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-012 (98.6MW/Wind), into Kingsbury County 115kV Substation | EREC | 18 | 5135000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Kingsbury County 115kV Substation GEN-2023-012 Interconnection (Non-Shared NU) (EREP) | 158697 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-012 (98.6MW/Wind), into Kingsbury County 115kV Substation | EREC | 0 | 0
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Leland Olds to Groton 345 kV Line GEN-2023-013 Interconnection (TOIF) (BEPC) | 158698 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-013 (200MW/Wind), into Leland Olds to Groton 345 kV Line | BEPC | 66 | 3685159
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Leland Olds to Groton 345 kV Line GEN-2023-014 Interconnection (TOIF) (BEPC) | 158699 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-014 (200MW/Wind), into Leland Olds to Groton 345 kV Line | BEPC | 6 | 120000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (TOIF) (SPS) | 158700 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | SPS | 48 | 1900000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (Non-Shared NU) (SPS) | 158701 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | SPS | 48 | 16806895
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tupelo-Brown 138 kV Line GEN-2023-016 Interconnection (TOIF) (SWPA) | 158702 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-016 (130MW/Solar), into Tupelo-Brown 138 kV Line | SWPA | 48 | 800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tupelo-Brown 138 kV Line GEN-2023-016 Interconnection (Non-Shared NU) (SWPA) | 158703 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-016 (130MW/Solar), into Tupelo-Brown 138 kV Line | SWPA | 48 | 8600000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carl Junction Northeast 161 kV Substation GEN-2023-017 Interconnection (TOIF) (EDE) | 158704 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-017 (150MW/Battery/Storage), into Carl Junction Northeast 161 kV Substation | EDE | 48 | 1871112
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carl Junction Northeast 161 kV Substation GEN-2023-017 Interconnection (Non-Shared NU) (EDE) | 158705 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-017 (150MW/Battery/Storage), into Carl Junction Northeast 161 kV Substation | EDE | 48 | 21509480.76
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Cherry Road 138 kV Substation GEN-2023-019 Interconnection (TOIF) (WFEC) | 158706 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-019 (200MW/Battery/Storage), into Cherry Road 138 kV Substation | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Cherry Road 138 kV Substation GEN-2023-019 Interconnection (Non-Shared NU) (WFEC) | 158707 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-019 (200MW/Battery/Storage), into Cherry Road 138 kV Substation | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Russett-S Brown 138 kV GEN-2023-020 Interconnection (TOIF) (WFEC) | 158708 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-020 (220MW/Solar), into Russett-S Brown 138 kV | WFEC | 48 | 499999
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Russett-S Brown 138 kV GEN-2023-020 Interconnection (Non-Shared NU) (WFEC) | 158709 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-020 (220MW/Solar), into Russett-S Brown 138 kV | WFEC | 48 | 4999999
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Blue Mills 161kV Substation GEN-2023-021 Interconnection (TOIF) (Evergy) | 158710 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-021 (200MW/Battery/Storage), into Blue Mills 161kV Substation | EVERGY | 36 | 848027
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Blue Mills 161kV Substation GEN-2023-021 Interconnection (Non-Shared NU) (Evergy) | 158711 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-021 (200MW/Battery/Storage), into Blue Mills 161kV Substation | EVERGY | 36 | 12224014
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | CaN/Adian River 345 kV Substation GEN-2023-022 Interconnection (TOIF) (OGE) | 158712 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-022 (250MW/Wind), into CaN/Adian River 345 kV Substation | OGE | 48 | 1591654
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | CaN/Adian River 345 kV Substation GEN-2023-022 Interconnection (Non-Shared NU) (OGE) | 158713 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-022 (250MW/Wind), into CaN/Adian River 345 kV Substation | OGE | 48 | 1790488
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Center City 161 kV Substation GEN-2023-023 Interconnection (TOIF) (KACY) | 158714 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-023 (200MW/Battery/Storage), into Center City 161 kV Substation | KACY | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Center City 161 kV Substation GEN-2023-023 Interconnection (Non-Shared NU) (KACY) | 158715 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-023 (200MW/Battery/Storage), into Center City 161 kV Substation | KACY | 40 | 4998381
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rose Hill 138 kV Substation GEN-2023-024 Interconnection (TOIF) (Evergy) | 158716 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-024 (200MW/Battery/Storage), into Rose Hill 138 kV Substation | EVERGY | 36 | 737196
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rose Hill 138 kV Substation GEN-2023-024 Interconnection (Non-Shared NU) (Evergy) | 158717 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-024 (200MW/Battery/Storage), into Rose Hill 138 kV Substation | EVERGY | 36 | 792459
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Franklin - Jayhawk 161 kV Line GEN-2023-025 Interconnection (TOIF) (Evergy) | 158718 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-025 (200MW/Battery/Storage), into Franklin - Jayhawk 161 kV Line | EVERGY | 36 | 751752
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Franklin - Jayhawk 161 kV Line GEN-2023-025 Interconnection (Non-Shared NU) (Evergy) | 158719 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-025 (200MW/Battery/Storage), into Franklin - Jayhawk 161 kV Line | EVERGY | 36 | 12481952
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | LaCygne - Wolf Creek 345 kV Line GEN-2023-026 Interconnection (TOIF) (Evergy) | 158720 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-026 (300MW/Battery/Storage), into LaCygne - Wolf Creek 345 kV Line | EVERGY | 56 | 1680753
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | LaCygne - Wolf Creek 345 kV Line GEN-2023-026 Interconnection (Non-Shared NU) (Evergy) | 158721 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-026 (300MW/Battery/Storage), into LaCygne - Wolf Creek 345 kV Line | EVERGY | 56 | 40560386
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Bird Hollow (Langley) - Pryor Junction 138 kV Line GEN-2023-027 Interconnection (TOIF) (AEP) | 158722 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-027 (150MW/Hybrid), into Bird Hollow (Langley) - Pryor Junction 138 kV Line | AEP | 36 | 2125000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Bird Hollow (Langley) - Pryor Junction 138 kV Line GEN-2023-027 Intercon (Non-Shared NU) (AEP) | 158723 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-027 (150MW/Hybrid), into Bird Hollow (Langley) - Pryor Junction 138 kV Line | AEP | 36 | 11500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-028 Interconnection (TOIF) (GRDA) | 158724 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-028 (230MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | GRDA | 24 | 1057500
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-028 Interconnection (Non-Shared NU) (GRDA) | 158725 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-028 (230MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | GRDA | 24 | 5800735
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Adair - Pryor 69 kV Line GEN-2023-029 Interconnection (TOIF) (AEP) | 158726 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-029 (50MW/Solar), into Adair - Pryor 69 kV Line | AEP | 36 | 1775000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Adair - Pryor 69 kV Line GEN-2023-029 Interconnection (Non-Shared NU) (AEP) | 158727 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-029 (50MW/Solar), into Adair - Pryor 69 kV Line | AEP | 36 | 10750000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap between 345 kV SW Shreveport-Dolet Hills Subs GEN-2023-030 Interconnection (TOIF) (AEP) | 158728 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-030 (25MW/Solar), into Tap between 345 kV SW Shreveport-Dolet Hills Subs | AEP | 36 | 200000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap between 345 kV SW Shreveport-Dolet Hills SubsGEN-2023-030 Interconnection (Non-Shared NU) (AEP) | 158729 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-030 (25MW/Solar), into Tap between 345 kV SW Shreveport-Dolet Hills Subs | AEP | 18 | 250000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Washburn 230 kV Substation GEN-2023-031 Interconnection (TOIF) (WAPA) | 158730 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-031 (200MW/Solar), into Washburn 230 kV Substation | WAPA | 74 | 598000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Washburn 230 kV Substation GEN-2023-031 Interconnection (Non-Shared NU) (WAPA) | 158731 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-031 (200MW/Solar), into Washburn 230 kV Substation | WAPA | 74 | 28097000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Odessa and Lexington 161 kV Line GEN-2023-032 Interconnection (TOIF) (Evergy) | 158732 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-032 (200MW/Solar), into Odessa and Lexington 161 kV Line | EVERGY | 36 | 751752
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Odessa and Lexington 161 kV Line GEN-2023-032 Interconnection (Non-Shared NU) (Evergy) | 158733 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-032 (200MW/Solar), into Odessa and Lexington 161 kV Line | EVERGY | 36 | 15889780
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (TOIF) (Evergy) | 158734 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | EVERGY | 36 | 751752
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (Non-Shared NU) (Evergy) | 158735 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | EVERGY | 36 | 887099
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (TOIF) (Evergy) | 158736 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | EVERGY | 36 | 745228
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (Non-Shared NU) (Evergy) | 158737 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | EVERGY | 36 | 13079166
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (TOIF) (WFEC) | 158738 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (Non-Shared NU) (WFEC) | 158739 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | WFEC | 48 | 5000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Eckles Road 161 kV Substation GEN-2023-036 Interconnection (TOIF) (INDN) | 158740 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-036 (200MW/Battery/Storage), into Eckles Road 161 kV Substation. | INDN | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Eckles Road 161 kV Substation GEN-2023-036 Interconnection (Non-Shared NU) (INDN) | 158741 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-036 (200MW/Battery/Storage), into Eckles Road 161 kV Substation. | INDN | 48 | 3200000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Quindaro Bluffs 161 kV Substation GEN-2023-037 Interconnection (TOIF) (KACY) | 158742 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Quindaro Bluffs 161 kV Substation | KACY | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Quindaro Bluffs 161 kV Substation GEN-2023-037 Interconnection (Non-Shared NU) (KACY) | 158743 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Quindaro Bluffs 161 kV Substation | KACY | 40 | 3357305
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (TOIF) (OGE) | 158744 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | OGE | 36 | 1877533
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (Non-Shared NU) (OGE) | 158745 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | OGE | 36 | 1676256
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carpenter 345 kV Substation GEN-2023-039 Interconnection (TOIF) (SPS) | 158746 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-039 (250MW/Wind), into Carpenter 345 kV Substation | SPS | 48 | 950000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Carleton Junction 115 kV Substation GEN-2023-040 Interconnection (TOIF) (NPPD) | 158747 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-040 (105MW/Solar), into Carleton Junction 115 kV Substation | NPPD | 36 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Carleton Junction 115 kV Substation GEN-2023-040 Interconnection (Non-Shared NU) (NPPD) | 158748 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-040 (105MW/Solar), into Carleton Junction 115 kV Substation | NPPD | 36 | 1500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Noel Southwest 161 kV Substation GEN-2023-042 Interconnection (TOIF) (EDE) | 158749 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-042 (200MW/Solar), into Noel Southwest 161 kV Substation | EDE | 48 | 1713303.4
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Noel Southwest 161 kV Substation GEN-2023-042 Interconnection (Non-Shared NU) (EDE) | 158750 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-042 (200MW/Solar), into Noel Southwest 161 kV Substation | EDE | 48 | 9592156.56
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation GEN-2023-043 Interconnection (TOIF) (SUNC) | 158751 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-043 (200MW/Solar), into Setab 345 kV Substation | SEPC | 48 | 666667
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation GEN-2023-044 Interconnection (TOIF) (SUNC) | 158752 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-044 (200MW/Solar), into Setab 345 kV Substation | SEPC | 48 | 666667
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation GEN-2023-045 Interconnection (TOIF) (SUNC) | 158753 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-045 (250MW/Wind), into Setab 345 kV Substation | SEPC | 48 | 333333
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation GEN-2023-046 Interconnection (TOIF) (SUNC) | 158754 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-046 (250MW/Wind), into Setab 345 kV Substation | SEPC | 48 | 333333
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation GEN-2023-047 Interconnection (TOIF) (SUNC) | 158755 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-047 (250MW/Wind), into Setab 345 kV Substation | SEPC | 48 | 333333
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation GEN-2023-048 Interconnection (TOIF) (SUNC) | 158756 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-048 (250MW/Wind), into Setab 345 kV Substation | SEPC | 48 | 333333
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-049 Interconnection (TOIF) (GRDA) | 158757 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-049 (150MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | GRDA | 24 | 682500
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-049 Interconnection (Non-Shared NU) (GRDA) | 158758 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-049 (150MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | GRDA | 24 | 6176735
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Neosho 345 kV Substation GEN-2023-050 Interconnection (TOIF) (Evergy) | 158759 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-050 (400MW/Hybrid), into Neosho 345 kV Substation | EVERGY | 56 | 1325114
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Neosho 345 kV Substation GEN-2023-050 Interconnection (Non-Shared NU) (Evergy) | 158760 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-050 (400MW/Hybrid), into Neosho 345 kV Substation | EVERGY | 56 | 2764794
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Red Rock Road - Weatherford Junction 138 kV Line GEN-2023-051 Interconnection (TOIF) (AEP) | 158761 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-051 (150MW/Hybrid), into Red Rock Road - Weatherford Junction 138 kV Line | AEP | 36 | 2125000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Red Rock Road - Weatherford Junction 138 kV Line GEN-2023-051 Interconnection (Non-Shared NU) (AEP) | 158762 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-051 (150MW/Hybrid), into Red Rock Road - Weatherford Junction 138 kV Line | AEP | 36 | 11500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rose Hill 345 kV Substation GEN-2023-052 Interconnection (TOIF) (Evergy) | 158763 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-052 (300MW/Hybrid), into Rose Hill 345 kV Substation | EVERGY | 56 | 1325114
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pittsburg - Valiant 345kV line GEN-2023-053 Interconnection (TOIF) (AEP) | 158764 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-053 (212MW/Wind), into Pittsburg - Valiant 345kV line | AEP | 42 | 3275000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pittsburg - Valiant 345kV line GEN-2023-053 Interconnection (Non-Shared NU) (AEP) | 158765 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-053 (212MW/Wind), into Pittsburg - Valiant 345kV line | AEP | 42 | 18100000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | LeLand Olds-Fort Thompson 345kV line GEN-2023-054 Interconnection (TOIF) (BEPC) | 158766 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-054 (400MW/Solar), into LeLand Olds-Fort Thompson 345kV line | BEPC | 66 | 3685159
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | LeLand Olds-Fort Thompson 345kV line GEN-2023-054 Interconnection (Non-Shared NU) (BEPC) | 158767 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-054 (400MW/Solar), into LeLand Olds-Fort Thompson 345kV line | BEPC | 66 | 19903604
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (TOIF) (GRDA) | 158768 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | GRDA | 24 | 2406249
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (Non-Shared NU) (GRDA) | 158769 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | GRDA | 24 | 1750000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Van Buren 161 kV GEN-2023-056 Interconnection (TOIF) (SWPA) | 158770 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-056 (150MW/Battery/Storage), into Van Buren 161 kV | SWPA | 48 | 775000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Van Buren 161 kV GEN-2023-056 Interconnection (Non-Shared NU) (SWPA) | 158771 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-056 (150MW/Battery/Storage), into Van Buren 161 kV | SWPA | 48 | 4400000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (TOIF) (GRDA) | 158772 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | GRDA | 18 | 970399
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (Non-Shared NU) (GRDA) | 158773 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | GRDA | 18 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (TOIF) (AEP) | 158774 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | AEP | 36 | 2125000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (Non-Shared NU) (AEP) | 158775 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | AEP | 36 | 11500000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-060 Interconnection (TOIF) (SPS) | 158776 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-060 (256MW/Solar), into Plant X 230kV Substation | SPS | 42 | 1700000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (TOIF) (SWPA) | 158777 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | SWPA | 48 | 700000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (Non-Shared NU) (SWPA) | 158778 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | SWPA | 48 | 4200000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | REN 115 kV Substation GEN-2023-062 Interconnection (TOIF) (LYREC) | 158779 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-062 (98MW/Thermal), into REN 115 kV Substation | BEPC | 66 | 407172
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | REN 115 kV Substation GEN-2023-062 Interconnection (Non-Shared NU) (LYREC) | 158780 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-062 (98MW/Thermal), into REN 115 kV Substation | BEPC | 66 | 4940802
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (TOIF) (AEP) | 158781 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | AEP | 36 | 2125000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (Non-Shared NU) (AEP) | 158782 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | AEP | 36 | 11500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (TOIF) (SWPA) | 158783 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | SWPA | 48 | 800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (Non-Shared NU) (SWPA) | 158784 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | SWPA | 48 | 8600000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Halstead 69 kV Substation GEN-2023-065 Interconnection (TOIF) (Evergy) | 158785 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-065 (140MW/Battery/Storage), into Halstead 69 kV Substation | EVERGY | 36 | 724451
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Halstead 69 kV Substation GEN-2023-065 Interconnection (Non-Shared NU) (Evergy) | 158786 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-065 (140MW/Battery/Storage), into Halstead 69 kV Substation | EVERGY | 36 | 846415
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Tap Pierre - Midland 115 kV line GEN-2023-066 Interconnection (TOIF) (WAPA) | 158787 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-066 (130MW/Hybrid), into Tap Pierre - Midland 115 kV line | WAPA | 60 | 355000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Tap Pierre - Midland 115 kV line GEN-2023-066 Interconnection (Non-Shared NU) (WAPA) | 158788 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-066 (130MW/Hybrid), into Tap Pierre - Midland 115 kV line | WAPA | 60 | 16835000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Sulphur 115 kV Substation GEN-2023-067 Interconnection (TOIF) (WAPA) | 158789 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-067 (41MW/Wind), into Sulphur 115 kV Substation | WAPA | 58 | 232000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Sulphur 115 kV Substation GEN-2023-067 Interconnection (Non-Shared NU) (WAPA) | 158790 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-067 (41MW/Wind), into Sulphur 115 kV Substation | WAPA | 58 | 2137600
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carpenter 345 kV Substation GEN-2023-068 Interconnection (TOIF) (SPS) | 158791 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-068 (250MW/Wind), into Carpenter 345 kV Substation | SPS | 48 | 950000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (TOIF) (WFEC) | 158792 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (Non-Shared NU) (WFEC) | 158793 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | WFEC | 48 | 5000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lane - McGee Creek Tap 69 kV GEN-2023-070 Interconnection (TOIF) (AEP) | 158794 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-070 (50MW/Hybrid), into Lane - McGee Creek Tap 69 kV | AEP | 36 | 1975000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lane - McGee Creek Tap 69 kV GEN-2023-070 Interconnection (Non-Shared NU) (AEP) | 158795 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-070 (50MW/Hybrid), into Lane - McGee Creek Tap 69 kV | AEP | 36 | 10750000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Elsie Tap - Paxton 115 kV Line GEN-2023-071 Interconnection (TOIF) (Tri-State) | 158796 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-071 (200MW/Hybrid), into Elsie Tap - Paxton 115 kV Line | TSGT | 36 | 1500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Elsie Tap - Paxton 115 kV Line GEN-2023-071 Interconnection (Non-Shared NU) (Tri-State) | 158797 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-071 (200MW/Hybrid), into Elsie Tap - Paxton 115 kV Line | TSGT | 36 | 6500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | McAlister 138 kV Substation GEN-2023-072 Interconnection (TOIF) (WFEC) | 158798 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-072 (250MW/Wind), into McAlister 138 kV Substation | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | McAlister 138 kV Substation GEN-2023-072 Interconnection (Non-Shared NU) (WFEC) | 158799 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-072 (250MW/Wind), into McAlister 138 kV Substation | WFEC | 48 | 5000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rose Hill 345 kV Substation GEN-2023-073 Interconnection (TOIF) (Evergy) | 158800 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-073 (400MW/Battery/Storage), into Rose Hill 345 kV Substation | EVERGY | 56 | 1325114
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Delaware - Neosho 345 kV GEN-2023-075 Interconnection (TOIF) (Evergy) | 158801 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075 (200MW/Wind), into Delaware - Neosho 345 kV | EVERGY | 56 | 1325114
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Delaware - Neosho 345 kV GEN-2023-076 Interconnection (TOIF) (Evergy) | 158802 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-076 (100MW/Wind), into Delaware - Neosho 345 kV | EVERGY | 56 | 112911
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Substation 3740 345 kV GEN-2023-077 Interconnection (TOIF) (OPPD) | 158803 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077 (303MW/Thermal), into Substation 3740 345 kV | OPPD | 42 | 2644098
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Substation 3740 345 kV GEN-2023-078 Interconnection (TOIF) (OPPD) | 158804 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-078 (303MW/Thermal), into Substation 3740 345 kV | OPPD | 42 | 2775000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Substation 3740 345 kV GEN-2023-079 Interconnection (TOIF) (OPPD) | 158805 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-079 (303MW/Thermal), into Substation 3740 345 kV | OPPD | 42 | 2775000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lydia - Northwest TexarkaN/A 345 kV GEN-2023-080 Interconnection (TOIF) (AEP) | 158806 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-080 (200MW/Hybrid), into Lydia - Northwest TexarkaN/A 345 kV | AEP | 42 | 3475000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lydia - Northwest TexarkaN/A 345 kV GEN-2023-080 Interconnection (Non-Shared NU) (AEP) | 158807 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-080 (200MW/Hybrid), into Lydia - Northwest TexarkaN/A 345 kV | AEP | 42 | 18100000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-081 Interconnection (TOIF) (NEET) | 158808 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-081 (625MW/Hybrid), into Crossroads - Hobbs 345 kV Line | NEET | 56 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-081 Interconnection (Non-Shared NU) (NEET) | 158809 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-081 (625MW/Hybrid), into Crossroads - Hobbs 345 kV Line | NEET | 56 | 27767200
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | White 115 kV Substation GEN-2023-082 Interconnection (TOIF) (WAPA) | 158810 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-082 (175MW/Battery/Storage), into White 115 kV Substation | WAPA | 58 | 4105000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | White 115 kV Substation GEN-2023-082 Interconnection (Non-Shared NU) (WAPA) | 158811 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-082 (175MW/Battery/Storage), into White 115 kV Substation | WAPA | 58 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Laramie River -Sidney 345 kV Line GEN-2023-083 Interconnection (TOIF) (BEPC) | 158812 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-083 (200MW/Hybrid), into Laramie River -Sidney 345 kV Line | BEPC | 66 | 3685159
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Laramie River -Sidney 345 kV Line GEN-2023-083 Interconnection (Non-Shared NU) (BEPC) | 158813 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-083 (200MW/Hybrid), into Laramie River -Sidney 345 kV Line | BEPC | 66 | 19903604
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Groton South 115 kV Substation GEN-2023-084 Interconnection (TOIF) (WAPA) | 158814 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-084 (100MW/Hybrid), into Groton South 115 kV Substation | WAPA | 60 | 260000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Groton South 115 kV Substation GEN-2023-084 Interconnection (Non-Shared NU) (WAPA) | 158815 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-084 (100MW/Hybrid), into Groton South 115 kV Substation | WAPA | 60 | 3255000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Mansfield - Logan 161 kV Line GEN-2023-085 Interconnection (TOIF) (SWPA) | 158816 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-085 (150MW/Wind), into Mansfield - Logan 161 kV Line | SWPA | 48 | 800000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Mansfield - Logan 161 kV Line GEN-2023-085 Interconnection (Non-Shared NU) (SWPA) | 158817 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-085 (150MW/Wind), into Mansfield - Logan 161 kV Line | SWPA | 48 | 8600000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Potter - Newhart 230 kV line GEN-2023-086 Interconnection (TOIF) (SPS) | 158818 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-086 (300MW/Hybrid), into Potter - Newhart 230 kV line | SPS | 42 | 1700000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Potter - Newhart 230 kV line GEN-2023-086 Interconnection (Non-Shared NU) (SPS) | 158819 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-086 (300MW/Hybrid), into Potter - Newhart 230 kV line | SPS | 42 | 11573021
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Archie 161 kV Substation GEN-2023-087 Interconnection (TOIF) (Evergy) | 158820 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-087 (200MW/Solar), into Archie 161 kV Substation | EVERGY | 36 | 884472
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Archie 161 kV Substation GEN-2023-087 Interconnection (Non-Shared NU) (Evergy) | 158821 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-087 (200MW/Solar), into Archie 161 kV Substation | EVERGY | 36 | 22572276
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (TOIF) (WFEC) | 158822 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (Non-Shared NU) (WFEC) | 158823 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | WFEC | 48 | 500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Buckner 345 kV Substation GEN-2023-089 Interconnection (TOIF) (SUNC) | 158824 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-089 (250MW/Wind), into Buckner 345 kV Substation | SEPC | 48 | 833333
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Buckner 345 kV Substation GEN-2023-090 Interconnection (TOIF) (SUNC) | 158825 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-090 (250MW/Wind), into Buckner 345 kV Substation | SEPC | 48 | 833333
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Buckner 345 kV Substation GEN-2023-091 Interconnection (TOIF) (SUNC) | 158826 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-091 (504MW/Wind), into Buckner 345 kV Substation | SEPC | 48 | 833333
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (TOIF) (WFEC) | 158827 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | WFEC | 48 | 499999
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (Non-Shared NU) (WFEC) | 158828 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | WFEC | 48 | 5000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carpenter 345 kV Substation GEN-2023-093 Interconnection (TOIF) (SPS) | 158829 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-093 (250MW/Wind), into Carpenter 345 kV Substation | SPS | 48 | 11573021
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carpenter 345 kV Substation GEN-2023-094 Interconnection (TOIF) (SPS) | 158830 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-094 (250MW/Wind), into Carpenter 345 kV Substation | SPS | 48 | 950000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Judson 345 kV Substation GEN-2023-097 Interconnection (TOIF) (BEPC) | 158833 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-097 (250MW/Battery/Storage), into Judson 345 kV Substation | BEPC | 66 | 2909909
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Judson 345 kV Substation GEN-2023-097 Interconnection (Non-Shared NU) (BEPC) | 158834 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-097 (250MW/Battery/Storage), into Judson 345 kV Substation | BEPC | 66 | 3039889
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Bison - Maurine 230 kV Line GEN-2023-098 Interconnection (TOIF) (WAPA) | 158835 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-098 (200MW/Hybrid), into Bison - Maurine 230 kV Line | WAPA | 70 | 595000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Bison - Maurine 230 kV Line GEN-2023-098 Interconnection (Non-Shared NU) (WAPA) | 158836 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-098 (200MW/Hybrid), into Bison - Maurine 230 kV Line | WAPA | 70 | 21760000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (TOIF) (Evergy) | 158837 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | EVERGY | 56 | 112910
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (Non-Shared NU) (Evergy) | 158838 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | EVERGY | 56 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Degrasse 345 kV Substation GEN-2023-100 Interconnection (TOIF) (OGE) | 158839 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100 (300MW/Hybrid), into Degrasse 345 kV Substation | OGE | 36 | 2756115
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap Stateline Demarc - Wheeler 230 kV Line GEN-2023-101 Interconnection (TOIF) (SPS) | 158840 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-101 (150MW/Hybrid), into Tap Stateline Demarc - Wheeler 230 kV Line | SPS | 42 | 1700000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap Stateline Demarc - Wheeler 230 kV Line GEN-2023-101 Interconnection (Non-Shared NU) (SPS) | 158841 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-101 (150MW/Hybrid), into Tap Stateline Demarc - Wheeler 230 kV Line | SPS | 42 | 11369957
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Degrasse 345 kV Substation GEN-2023-102 Interconnection (TOIF) (OGE) | 158842 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-102 (475MW/Hybrid), into Degrasse 345 kV Substation | OGE | 48 | 2756115
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Northeastern 138 kV Substation GEN-2023-103 Interconnection (TOIF) (AEP) | 158843 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-103 (200MW/Battery/Storage), into Northeastern 138 kV Substation | AEP | 30 | 2325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Northeastern 138 kV Substation GEN-2023-103 Interconnection (Non-Shared NU) (AEP) | 158844 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-103 (200MW/Battery/Storage), into Northeastern 138 kV Substation | AEP | 30 | 2050000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (TOIF) (WFEC) | 158845 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (Non-Shared NU) (WFEC) | 158846 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | WFEC | 48 | 5000000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Chappelle Creek 345 kV Substation GEN-2023-105 Interconnection (TOIF) (BEPC) | 158847 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-105 (249MW/Wind), into Chappelle Creek 345 Kv Substation | BEPC | 66 | 1673527
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Chappelle Creek 345 kV Substation GEN-2023-106 Interconnection (TOIF) (BEPC) | 158848 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-106 (504MW/Wind), into Chappelle Creek 345 kV Substation | BEPC | 6 | 120000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation GEN-2023-107 Interconnection (TOIF) (SUNC) | 158849 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-107 (300MW/Wind), into Setab 345 kV | SEPC | 48 | 1333333
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Dumas and 19th Street 115 kV Substation GEN-2023-109 Interconnection (TOIF) (SPS) | 158850 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-109 (65MW/Solar), into Dumas and 19th Street 115 kV Substation | SPS | 42 | 1900000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Dumas and 19th Street 115 kV Substation GEN-2023-109 Interconnection (Non-Shared NU) (SPS) | 158851 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-109 (65MW/Solar), into Dumas and 19th Street 115 kV Substation | SPS | 42 | 12536957
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tap Border to Tuco 345 kV Line GEN-2023-110 Interconnection (TOIF) (SPS) | 158852 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-110 (250MW/Solar), into Tap Border to Tuco 345 kV Line | SPS | 48 | 1900000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tap Border to Tuco 345 kV Line GEN-2023-110 Interconnection (Non-Shared NU) (SPS) | 158853 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-110 (250MW/Solar), into Tap Border to Tuco 345 kV Line | SPS | 48 | 16856930
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Buffalo Flats 345 kV Substation GEN-2023-111 Interconnection (TOIF) (Evergy) | 158854 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-111 (200MW/Solar), into Buffalo Flats 345 kV Substation | EVERGY | 56 | 112909
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Jamestown 230 kV Substation GEN-2023-114 Interconnection (TOIF) (WAPA) | 158855 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-114 (425MW/Wind), into Jamestown 230 kV Substation | WAPA | 68 | 100000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Jamestown 230 kV Substation GEN-2023-114 Interconnection (Non-Shared NU) (WAPA) | 158856 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-114 (425MW/Wind), into Jamestown 230 kV Substation | WAPA | 68 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Tap Georgetown Overton to Sedalia East 161 kV Line GEN-2023-115 Interconnection (TOIF) (Evergy) | 158857 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-115 (300MW/Solar), into Tap Georgetown Overton to Sedalia East 161 kV Line | EVERGY | 36 | 751752
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Tap Georgetown Overton to Sedalia East 161 kV Line GEN-2023-115 Intercon (Non-Shared NU) (Evergy) | 158858 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-115 (300MW/Solar), into Tap Georgetown Overton to Sedalia East 161 kV Line | EVERGY | 36 | 12461515
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Keystone 345 kV Substation GEN-2023-116 Interconnection (TOIF) (NPPD) | 158859 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116 (500MW/Wind), into Keystone 345 kV Substation | NPPD | 36 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Keystone 345 kV Substation GEN-2023-117 Interconnection (TOIF) (NPPD) | 158860 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-117 (300MW/Wind), into Keystone 345 kV Substation | NPPD | 36 | 1000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Buffalo Flats 345 kV Substation GEN-2023-118 Interconnection (TOIF) (Evergy) | 158861 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-118 (200MW/Wind), into Buffalo Flats 345 kV Substation | EVERGY | 56 | 112911
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (TOIF) (SPS) | 158862 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | SPS | 42 | 1200000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (Non-Shared NU) (SPS) | 158863 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | SPS | 42 | 5412393
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Tie 69 kV Substation GEN-2023-121 Interconnection (TOIF) (GridLiance) | 158864 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-121 (50MW/Solar), into Tie 69 kV Substation | GHP | NA | 250000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Tie 69 kV Substation GEN-2023-121 Interconnection (Non-Shared NU) (GridLiance) | 158865 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-121 (50MW/Solar), into Tie 69 kV Substation | GHP | NA | 1550000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Wolf Creek - LaCygne 345 kV Line GEN-2023-122 Interconnection (TOIF) (Evergy) | 158866 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-122 (250MW/Solar), into Wolf Creek - LaCygne 345 kV Line | EVERGY | 56 | 1325114
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Wolf Creek - LaCygne 345 kV Line GEN-2023-122 Interconnection (Non-Shared NU) (Evergy) | 158867 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-122 (250MW/Solar), into Wolf Creek - LaCygne 345 kV Line | EVERGY | 56 | 32873895
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Pringle Interchange 230 kV Substation GEN-2023-123 Interconnection (TOIF) (SPS) | 158868 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-123 (285MW/Wind), into Pringle Interchange 230 kV Substation | SPS | 42 | 900000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Pringle Interchange 230 kV Substation GEN-2023-123 Interconnection (Non-Shared NU) (SPS) | 158869 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-123 (285MW/Wind), into Pringle Interchange 230 kV Substation | SPS | 42 | 9010000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Spearman Interchange 115 kV Substation GEN-2023-124 Interconnection (TOIF) (SPS) | 158870 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-124 (200MW/Wind), into Spearman Interchange 115 kV Substation | SPS | 42 | 1200000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Spearman Interchange 115 kV Substation GEN-2023-124 Interconnection (Non-Shared NU) (SPS) | 158871 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-124 (200MW/Wind), into Spearman Interchange 115 kV Substation | SPS | 42 | 6767393
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Whitlock 230 kV Substation GEN-2023-130 Interconnection (TOIF) (BEPC) | 158872 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-130 (96MW/Hybrid), into Whitlock 230 kV Substation | BEPC | 66 | 2112076
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Whitlock 230 kV Substation GEN-2023-130 Interconnection (Non-Shared NU) (BEPC) | 158873 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-130 (96MW/Hybrid), into Whitlock 230 kV Substation | BEPC | 66 | 2498712
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (TOIF) (SWPA) | 158874 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | SWPA | 48 | 800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (Non-Shared NU) (SWPA) | 158875 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | SWPA | 48 | 8600000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Sweetwater 345 kV Substation GEN-2023-133 Interconnection (TOIF) (NPPD) | 158876 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-133 (250MW/Wind), into Sweetwater 345 kV Substation | NPPD | 36 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Sweetwater 345 kV Substation GEN-2023-133 Interconnection (Non-Shared NU) (NPPD) | 158877 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-133 (250MW/Wind), into Sweetwater 345 kV Substation | NPPD | 36 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Fixico Tap to Weleetka 138 kV Line GEN-2023-134 Interconnection (TOIF) (AEP) | 158878 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-134 (252MW/Wind), into Fixico Tap to Weleetka 138 kV Line | AEP | 36 | 1925000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Fixico Tap to Weleetka 138 kV Line GEN-2023-134 Interconnection (Non-Shared NU) (AEP) | 158879 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-134 (252MW/Wind), into Fixico Tap to Weleetka 138 kV Line | AEP | 36 | 11500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (TOIF) (AEP) | 158880 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | AEP | 18 | 200000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (Non-Shared NU) (AEP) | 158881 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | AEP | 18 | 250000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Vinita Junction - Hockerville 138 kV GEN-2023-136 Interconnection (TOIF) (AEP) | 158882 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-136 (150MW/Hybrid), into Vinita Junction - Hockerville 138 Kv | AEP | 36 | 2125000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Vinita Junction - Hockerville 138 kV GEN-2023-136 Interconnection (Non-Shared NU) (AEP) | 158883 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-136 (150MW/Hybrid), into Vinita Junction - Hockerville 138 kV | AEP | 36 | 11500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | North Boston - Bann 138 kV Line Tap GEN-2023-137 Interconnection (TOIF) (AEP) | 158884 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-137 (150MW/Battery/Storage), into North Boston - Bann 138 kV Line Tap | AEP | 18 | 200000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | North Boston - Bann 138 kV Line Tap GEN-2023-137 Interconnection (Non-Shared NU) (AEP) | 158885 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-137 (150MW/Battery/Storage), into North Boston - Bann 138 kV Line Tap | AEP | 18 | 250000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | GRDA1 - Tonece7 345 kV Line GEN-2023-138 Interconnection (TOIF) (GRDA) | 158886 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-138 (250MW/Wind), into GRDA1 - Tonece7 345 kV Line | GRDA | 28 | 1531872
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | GRDA1 - Tonece7 345 kV Line GEN-2023-138 Interconnection (Non-Shared NU) (GRDA) | 158887 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-138 (250MW/Wind), into GRDA1 - Tonece7 345 kV Line | GRDA | 28 | 10070786
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-142 Interconnection (TOIF) (SPS) | 158888 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-142 (275MW/Solar), into Plant X 230 kV Substation | SPS | 42 | 850000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-143 Interconnection (TOIF) (SPS) | 158889 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-143 (200MW/Battery/Storage), into Plant X 230 kV Substation | SPS | 42 | 850000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Bismarck - Jamestown 230 kV GEN-2023-144 Interconnection (TOIF) (WAPA) | 158890 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-144 (265MW/Solar), into Bismarck - Jamestown 230 kV | WAPA | 70 | 595000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Bismarck - Jamestown 230 kV GEN-2023-144 Interconnection (Non-Shared NU) (WAPA) | 158891 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-144 (265MW/Solar), into Bismarck - Jamestown 230 kV | WAPA | 70 | 21800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Eufaula - Gore 161 kV Line GEN-2023-145 Interconnection (TOIF) (SWPA) | 158892 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-145 (180MW/Solar), into Eufaula - Gore 161 kV Line | SWPA | 48 | 800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Eufaula - Gore 161 kV Line GEN-2023-145 Interconnection (Non-Shared NU) (SWPA) | 158893 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-145 (180MW/Solar), into Eufaula - Gore 161 kV Line | SWPA | 48 | 35300000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Seward 115 kV Substation GEN-2023-146 Interconnection (TOIF) (NPPD) | 158894 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-146 (125MW/Solar), into Seward 115 kV Substation | NPPD | 36 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Seward 115 kV Substation GEN-2023-146 Interconnection (Non-Shared NU) (NPPD) | 158895 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-146 (125MW/Solar), into Seward 115 kV Substation | NPPD | 36 | 3500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Victory Hill - Crawford 115 kV Line GEN-2023-147 Interconnection (TOIF) (NPPD) | 158896 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-147 (85MW/Wind), into Victory Hill - Crawford 115 kV Line | NPPD | 36 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Victory Hill - Crawford 115 kV Line GEN-2023-147 Interconnection (Non-Shared NU) (NPPD) | 158897 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-147 (85MW/Wind), into Victory Hill - Crawford 115 kV Line | NPPD | 36 | 16000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Russell - Lake Pauline 138 kV Line GEN-2023-148 Interconnection (TOIF) (AEP) | 158898 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-148 (110MW/Hybrid), into Russell - Lake Pauline 138 kV Line | AEP | 36 | 2125000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Russell - Lake Pauline 138 kV Line GEN-2023-148 Interconnection (Non-Shared NU) (AEP) | 158899 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-148 (110MW/Hybrid), into Russell - Lake Pauline 138 kV Line | AEP | 36 | 11500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | LaCygne - Stilwell 345 kV Line GEN-2023-149 Interconnection (TOIF) (Evergy) | 158900 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-149 (300MW/Battery/Storage), into LaCygne - Stilwell 345 kV Line | EVERGY | 56 | 1325114
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | LaCygne - Stilwell 345 kV Line GEN-2023-149 Interconnection (Non-Shared NU) (Evergy) | 158901 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-149 (300MW/Battery/Storage), into LaCygne - Stilwell 345 kV Line | EVERGY | 56 | 28791748
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 138 kV Substation GEN-2023-150 Interconnection (TOIF) (OGE) | 158902 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-150 (150MW/Solar), into Gracemont 138 kV Substation | OGE | 36 | 2663387
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 138 kV Substation GEN-2023-150 Interconnection (Non-Shared NU) (OGE) | 158903 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-150 (150MW/Solar), into Gracemont 138 kV Substation | OGE | 36 | 2262110
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | South N/Ashville - South Murfreesboro 138kV GEN-2023-151 Interconnection (TOIF) (AEP) | 158904 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-151 (100MW/Hybrid), into South N/Ashville - South Murfreesboro 138kV | AEP | 36 | 2125000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | South N/Ashville - South Murfreesboro 138kV GEN-2023-151 Interconnection (Non-Shared NU) (AEP) | 158905 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-151 (100MW/Hybrid), into South N/Ashville - South Murfreesboro 138kV | AEP | 36 | 11500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Allen NG4 138 kV Substation GEN-2023-152 Interconnection (TOIF) (AEP) | 158906 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-152 (140MW/Solar), into Allen NG4 138 kV Substation | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Allen NG4 138 kV Substation GEN-2023-152 Interconnection (Non-Shared NU) (AEP) | 158907 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-152 (140MW/Solar), into Allen NG4 138 kV Substation | AEP | 36 | 10725000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (TOIF) (Tri-State) | 158908 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | TSGT | 36 | 1250000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (Non-Shared NU) (Tri-State) | 158909 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | TSGT | 36 | 5250000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Fort Thompson - Huron 230 kV Tap GEN-2023-154 Interconnection (TOIF) (WAPA) | 158910 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-154 (200MW/Solar), into Fort Thompson - Huron 230 kV Tap | WAPA | 70 | 8683000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Fort Thompson - Huron 230 kV Tap GEN-2023-154 Interconnection (Non-Shared NU) (WAPA) | 158911 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-154 (200MW/Solar), into Fort Thompson - Huron 230 kV Tap | WAPA | 70 | 592000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Longwood - Lieberman 138 kV GEN-2023-155 Interconnection (TOIF) (AEP) | 158912 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-155 (200MW/Solar), into Longwood - Lieberman 138 kV | AEP | 36 | 1925000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Longwood - Lieberman 138 kV GEN-2023-155 Interconnection (Non-Shared NU) (AEP) | 158913 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-155 (200MW/Solar), into Longwood - Lieberman 138 kV | AEP | 36 | 11500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Between South Wilson - Ringling 138 kV Line GEN-2023-156 Interconnection (TOIF) (WFEC) | 158914 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-156 (200MW/Hybrid), into Between South Wilson - Ringling 138 kV Line | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Between South Wilson - Ringling 138 kV Line GEN-2023-156 Interconnection (Non-Shared NU) (WFEC) | 158915 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-156 (200MW/Hybrid), into Between South Wilson - Ringling 138 kV Line | WFEC | 48 | 5000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Bucyrus 161 kV Substation GEN-2023-157 Interconnection (TOIF) (Evergy) | 158916 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-157 (150MW/Battery/Storage), into Bucyrus 161 kV Substation | EVERGY | 36 | 884672
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Bucyrus 161 kV Substation GEN-2023-157 Interconnection (Non-Shared NU) (Evergy) | 158917 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-157 (150MW/Battery/Storage), into Bucyrus 161 kV Substation | EVERGY | 36 | 17609254
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Needmore - Yoakum 230 kV Line GEN-2023-158 Interconnection (TOIF) (SPS) | 158918 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158 (335MW/Solar), into Needmore - Yoakum 230 kV Line | SPS | 42 | 850000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Needmore - Yoakum 230 kV Line GEN-2023-159 Interconnection (TOIF) (SPS) | 158919 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-159 (200MW/Battery/Storage), into Needmore - Yoakum 230 kV Line | SPS | 42 | 850000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Belfield - Rhame 230 kV Line GEN-2023-160 Interconnection (TOIF) (BEPC) | 158920 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-160 (300MW/Hybrid), into Belfield - Rhame 230 kV Line | BEPC | 66 | 3311556
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Belfield - Rhame 230 kV Line GEN-2023-160 Interconnection (Non-Shared NU) (BEPC) | 158921 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-160 (300MW/Hybrid), into Belfield - Rhame 230 kV Line | BEPC | 66 | 16601046
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (TOIF) (OGE) | 158922 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | OGE | 36 | 1231357
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (Non-Shared NU) (OGE) | 158923 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | OGE | 36 | 1540091
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Grove - Jay 138 kV Line GEN-2023-162 Interconnection (TOIF) (AEP) | 158924 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-162 (100MW/Hybrid), into Grove - Jay 138 kV Line | AEP | 36 | 2125000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Grove - Jay 138 kV Line GEN-2023-162 Interconnection (Non-Shared NU) (AEP) | 158925 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-162 (100MW/Hybrid), into Grove - Jay 138 kV Line | AEP | 36 | 11500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Midway - Avenue City 161 kV GEN-2023-163 Interconnection (TOIF) (Evergy) | 158926 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-163 (150MW/Solar), into Midway - Avenue City 161 kV | EVERGY | 36 | 884672
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Midway - Avenue City 161 kV GEN-2023-163 Interconnection (Non-Shared NU) (Evergy) | 158927 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-163 (150MW/Solar), into Midway - Avenue City 161 kV | EVERGY | 36 | 13604270
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 345 kV Substation GEN-2023-164 Interconnection (TOIF) (OGE) | 158928 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164 (210MW/Battery/Storage), into Gracemont 345 kV Substation | OGE | 48 | 1960313
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 345 kV Substation GEN-2023-165 Interconnection (TOIF) (OGE) | 158929 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | OGE | 48 | 1960313
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | 84th Street - Tennessee Tap 138 kV Line GEN-2023-166 Interconnection (TOIF) (OGE) | 158930 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-166 (150MW/Battery/Storage), into 84th Street - Tennessee Tap 138 kV Line | OGE | 36 | 3500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | 84th Street - Tennessee Tap 138 kV Line GEN-2023-166 Interconnection (Non-Shared NU) (OGE) | 158931 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-166 (150MW/Battery/Storage), into 84th Street - Tennessee Tap 138 kV Line | OGE | 36 | 10000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Washington Park 138 kV Substation GEN-2023-167 Interconnection (TOIF) (OGE) | 158932 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-167 (250MW/Battery/Storage), into Washington Park 138 kV Substation | OGE | 36 | 981357
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Washington Park 138 kV Substation GEN-2023-167 Interconnection (Non-Shared NU) (OGE) | 158933 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-167 (250MW/Battery/Storage), into Washington Park 138 kV Substation | OGE | 36 | 1190091
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Classen 138 kV Substation GEN-2023-168 Interconnection (TOIF) (OGE) | 158934 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-168 (175MW/Battery/Storage), into Classen 138 kV Substation | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Classen 138 kV Substation GEN-2023-168 Interconnection (Non-Shared NU) (OGE) | 158935 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-168 (175MW/Battery/Storage), into Classen 138 kV Substation | OGE | 36 | 10000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Missouri City - Liberty South 161 kV Line GEN-2023-169 Interconnection (TOIF) (Evergy) | 158936 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-169 (125MW/Battery/Storage), into Missouri City - Liberty South 161 kV Line | EVERGY | 36 | 884672
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Missouri City - Liberty South 161 kV Line GEN-2023-169 Interconnection (Non-Shared NU) (Evergy) | 158937 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-169 (125MW/Battery/Storage), into Missouri City - Liberty South 161 kV Line | EVERGY | 36 | 14364525
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (TOIF) (Evergy) | 158938 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | EVERGY | 36 | 884672
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (Non-Shared NU) (Evergy) | 158939 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | EVERGY | 36 | 4766925
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (TOIF) (INDN) | 158940 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation. | INDN | 48 | 400000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (Non-Shared NU) (INDN) | 158941 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation. | INDN | 48 | 2500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Holcomb 345 kV GEN-2023-172 Interconnection (TOIF) (SUNC) | 158942 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172 (200MW/Wind), into Holcomb 345 kV | SEPC | 48 | 1250000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Holcomb 345 kV GEN-2023-173 Interconnection (TOIF) (SUNC) | 158943 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-173 (100MW/Wind), into Holcomb 345 kV | SEPC | 48 | 1250000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Paoli West 138 kV Substation GEN-2023-174 Interconnection (TOIF) (WFEC) | 158944 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-174 (150MW/Battery/Storage), into Paoli West 138 kV Substation | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Paoli West 138 kV Substation GEN-2023-174 Interconnection (Non-Shared NU) (WFEC) | 158945 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-174 (150MW/Battery/Storage), into Paoli West 138 kV Substation | WFEC | 48 | 10000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Hickock 115 kV Substation GEN-2023-175 Interconnection (TOIF) (SUNC) | 158946 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-175 (200MW/Battery/Storage), into Hickock 115 kV Substation | SEPC | 36 | 2500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Hickock 115 kV Substation GEN-2023-175 Interconnection (Non-Shared NU) (SUNC) | 158947 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-175 (200MW/Battery/Storage), into Hickock 115 kV Substation | SEPC | 36 | 1000000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-176 Interconnection (TOIF) (SPS) | 158948 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-176 (300MW/Wind), into Plant X 230 kV Substation | SPS | 42 | 1700000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (TOIF) (OGE) | 158949 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | OGE | 36 | 3924886
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (Non-Shared NU) (OGE) | 158950 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | OGE | 36 | 2338281
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Roosevelt 230kV Substation GEN-2023-178 Interconnection (TOIF) (SPS) | 158951 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-178 (200MW/Solar), into Roosevelt 230kV Substation | SPS | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Roosevelt 230kV Substation GEN-2023-178 Interconnection (Non-Shared NU) (SPS) | 158952 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-178 (200MW/Solar), into Roosevelt 230kV Substation | SPS | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Hackett - N Huntington 161 kV Line Tap GEN-2023-180 Interconnection (TOIF) (AEP) | 158953 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-180 (150MW/Solar), into Hackett - N Huntington 161 kV Line Tap | AEP | 36 | 1950000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Hackett - N Huntington 161 kV Line Tap GEN-2023-180 Interconnection (Non-Shared NU) (AEP) | 158954 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-180 (150MW/Solar), into Hackett - N Huntington 161 kV Line Tap | AEP | 36 | 11650000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Groton - Leland Olds 345 kV Line GEN-2023-181 Interconnection (TOIF) (BEPC) | 158955 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-181 (100MW/Battery/Storage), into Groton - Leland Olds 345 kV Line | BEPC | 66 | 3685159
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Groton - Leland Olds 345 kV Line GEN-2023-182 Interconnection (TOIF) (BEPC) | 158956 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-182 (300MW/Wind), into Groton - Leland Olds 345 kV Line | BEPC | 6 | 120000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco 345kV GEN-2023-183 Interconnection (TOIF) (SPS) | 158957 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-183 (217MW/Thermal), into Tuco 345kV | SPS | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco 345kV GEN-2023-183 Interconnection (Non-Shared NU) (SPS) | 158958 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-183 (217MW/Thermal), into Tuco 345kV | SPS | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Phantom 115 kV Substation GEN-2023-184 Interconnection (TOIF) (SPS) | 158959 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-184 (200MW/Solar), into Phantom 115 kV Substation | SPS | 42 | 1200000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Phantom 115 kV Substation GEN-2023-184 Interconnection (Non-Shared NU) (SPS) | 158960 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-184 (200MW/Solar), into Phantom 115 kV Substation | SPS | 42 | 5780000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Nichols - Amarillo 230 kV line tap GEN-2023-185 Interconnection (TOIF) (SPS) | 158961 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-185 (150MW/Solar), into Nichols - Amarillo 230 kV line tap | SPS | 42 | 1700000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Nichols - Amarillo 230 kV line tap GEN-2023-185 Interconnection (Non-Shared NU) (SPS) | 158962 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-185 (150MW/Solar), into Nichols - Amarillo 230 kV line tap | SPS | 42 | 11470657
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Murray Gill 138 kV Substation GEN-2023-186 Interconnection (TOIF) (Evergy) | 158963 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-186 (200MW/Hybrid), into Murray Gill 138 kV Substation | EVERGY | 36 | 850069
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Murray Gill 138 kV Substation GEN-2023-186 Interconnection (Non-Shared NU) (Evergy) | 158964 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-186 (200MW/Hybrid), into Murray Gill 138 kV Substation | EVERGY | 36 | 846415
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Oklaunion - Lawton 345 kV Line GEN-2023-188 Interconnection (TOIF) (AEP) | 158965 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-188 (160MW/Hybrid), into Oklaunion - Lawton 345 kV Line | AEP | 42 | 3475000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Oklaunion - Lawton 345 kV Line GEN-2023-188 Interconnection (Non-Shared NU) (AEP) | 158966 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-188 (160MW/Hybrid), into Oklaunion - Lawton 345 kV Line | AEP | 42 | 18700000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | NW 68th - Holdrege 345 kV Substation GEN-2023-189 Interconnection (TOIF) (LES) | 158967 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-189 (200MW/Battery/Storage), into NW 68th - Holdrege 345 kV Substation | LES | 72 | 2768522
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | NW 68th - Holdrege 345 kV Substation GEN-2023-189 Interconnection (Non-Shared NU) (LES) | 158968 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-189 (200MW/Battery/Storage), into NW 68th - Holdrege 345 kV Substation | LES | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Hockersville 138 kV Substation GEN-2023-191 Interconnection (TOIF) (EDE) | 158969 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-191 (74MW/Battery/Storage), into Hockersville 138 kV Substation | EDE | 48 | 1927444.2
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Hockersville 138 kV Substation GEN-2023-191 Interconnection (Non-Shared NU) (EDE) | 158970 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-191 (74MW/Battery/Storage), into Hockersville 138 kV Substation | EDE | 48 | 9295029
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (TOIF) (AEP) | 158971 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | AEP | 36 | 2125000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (Non-Shared NU) (AEP) | 158972 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | AEP | 36 | 11500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Riverton - Neosho 161 kV Line Tap GEN-2023-194 Interconnection (TOIF) (EDE) | 158973 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-194 (225MW/Solar), into Riverton - Neosho 161 kV Line Tap | EDE | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Riverton - Neosho 161 kV Line Tap GEN-2023-194 Interconnection (Non-Shared NU) (EDE) | 158974 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-194 (225MW/Solar), into Riverton - Neosho 161 kV Line Tap | EDE | 48 | 1864449
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Roosevelt - Tolk 230 kV line tap GEN-2023-195 Interconnection (TOIF) (SPS) | 158975 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-195 (250MW/Solar), into Roosevelt - Tolk 230 kV line tap | SPS | 42 | 850000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Roosevelt - Tolk 230 kV line tap GEN-2023-196 Interconnection (TOIF) (SPS) | 158976 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-196 (150MW/Battery/Storage), into Roosevelt - Tolk 230 kV line tap | SPS | 42 | 850000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Sub 1366 - Sub 1258 161 kV GEN-2023-197 Interconnection (TOIF) (OPPD) | 158977 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-197 (150MW/Solar), into Sub 1366 - Sub 1258 161 kV | OPPD | 48 | 18111000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Sub 1366 - Sub 1258 161 kV GEN-2023-197 Interconnection (Non-Shared NU) (OPPD) | 158978 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-197 (150MW/Solar), into Sub 1366 - Sub 1258 161 kV | OPPD | 48 | 21200000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Hebron 230 kV Substation GEN-2023-198 Interconnection (TOIF) (WAPA) | 158979 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-198 (250MW/Solar), into Hebron 230 kV Substation | WAPA | 70 | 416000
Interconnection | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Hebron 230 kV Substation GEN-2023-198 Interconnection (Non-Shared NU) (WAPA) | 158980 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-198 (250MW/Solar), into Hebron 230 kV Substation | WAPA | 70 | 6989000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (TOIF) (NPPD) | 158981 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | NPPD | 36 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (Non-Shared NU) (NPPD) | 158982 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | NPPD | 36 | 2500000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Caney River 345 kV Substation GEN-2023-200 Interconnection (TOIF) (Evergy) | 158983 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-200 (300MW/Solar), into Caney River 345 kV Substation | EVERGY | 56 | 1325114
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Caney River 345 kV Substation GEN-2023-200 Interconnection (Non-Shared NU) (Evergy) | 158984 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-200 (300MW/Solar), into Caney River 345 kV Substation | EVERGY | 56 | 1635518
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-201 Interconnection (TOIF) (NEET) | 158985 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-201 (300MW/Hybrid), into Crossroads - Hobbs 345 kV Line | NEET | 56 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-201 Interconnection (Non-Shared NU) (NEET) | 158986 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-201 (300MW/Hybrid), into Crossroads - Hobbs 345 kV Line | NEET | 56 | 24961200
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Tekamah - Raun 161 kV Line GEN-2023-202 Interconnection (TOIF) (OPPD) | 158987 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-202 (150MW/Solar), into Tekamah - Raun 161 kV Line | OPPD | 36 | 3089434
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Tekamah - Raun 161 kV Line GEN-2023-202 Interconnection (Non-Shared NU) (OPPD) | 158988 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-202 (150MW/Solar), into Tekamah - Raun 161 kV Line | OPPD | 48 | 5450000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Hobbs - Ink Basin 230 kV Transmission Line GEN-2023-203 Interconnection (TOIF) (SPS) | 158989 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-203 (300MW/Hybrid), into Hobbs - Ink Basin 230 kV Transmission Line | SPS | 42 | 1700000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Hobbs - Ink Basin 230 kV Transmission Line GEN-2023-203 Interconnection (Non-Shared NU) (SPS) | 158990 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-203 (300MW/Hybrid), into Hobbs - Ink Basin 230 kV Transmission Line | SPS | 42 | 11348902
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (TOIF) (AEP) | 158991 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | AEP | 42 | 3275000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (Non-Shared NU) (AEP) | 158992 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | AEP | 42 | 18100000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (TOIF) (AEP) | 158993 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | AEP | 36 | 1925000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (Non-Shared NU) (AEP) | 158994 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | AEP | 36 | 11500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (TOIF) (OGE) | 158995 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | OGE | 24 | 20000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (Non-Shared NU) (OGE) | 158996 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | OGE | 24 | 20000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Colbert 138 kV Substation GEN-2023-207 Interconnection (TOIF) (WFEC) | 158997 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-207 (50MW/Battery/Storage), into Colbert 138 kV Substation | WFEC | 48 | 50000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Colbert 138 kV Substation GEN-2023-207 Interconnection (Non-Shared NU) (WFEC) | 158998 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-207 (50MW/Battery/Storage), into Colbert 138 kV Substation | WFEC | 48 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rolling Hills 115 kV GEN-2023-208 Interconnection (TOIF) (SPS) | 158999 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-208 (200MW/Battery/Storage), into Rolling Hills 115 kV | SPS | 42 | 1200000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rolling Hills 115 kV GEN-2023-208 Interconnection (Non-Shared NU) (SPS) | 159000 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-208 (200MW/Battery/Storage), into Rolling Hills 115 kV | SPS | 42 | 5005000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Amarillo South 115 kV GEN-2023-209 Interconnection (TOIF) (SPS) | 159001 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-209 (125MW/Battery/Storage), into Amarillo South 115 kV | SPS | 42 | 1200000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Amarillo South 115 kV GEN-2023-209 Interconnection (Non-Shared NU) (SPS) | 159002 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-209 (125MW/Battery/Storage), into Amarillo South 115 kV | SPS | 42 | 9460000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (TOIF) (WFEC) | 159003 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | WFEC | 48 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (Non-Shared NU) (WFEC) | 159004 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | WFEC | 48 | 4999999
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Ranch Road 345 kV Substation GEN-2023-211 Interconnection (TOIF) (OGE) | 159005 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-211 (250MW/Hybrid), into Ranch Road 345 kV Substation | OGE | 24 | 20000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Ranch Road 345 kV Substation GEN-2023-211 Interconnection (Non-Shared NU) (OGE) | 159006 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-211 (250MW/Hybrid), into Ranch Road 345 kV Substation | OGE | 24 | 20000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Northwest TexarkaN/A - Valliant 345 kV Line GEN-2023-212 Interconnection (TOIF) (AEP) | 159007 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-212 (400MW/Hybrid), into Northwest TexarkaN/A - Valliant 345 kV Line | AEP | 42 | 3275000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Northwest TexarkaN/A - Valliant 345 kV Line GEN-2023-212 Interconnection (Non-Shared NU) (AEP) | 159008 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-212 (400MW/Hybrid), into Northwest TexarkaN/A - Valliant 345 kV Line | AEP | 42 | 18100000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Chamber Springs 161 kV Substation GEN-2023-213 Interconnection (TOIF) (AEP) | 159009 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-213 (100MW/Battery/Storage), into Chamber Springs 161 kV Substation | AEP | 30 | 2525000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Chamber Springs 161 kV Substation GEN-2023-213 Interconnection (Non-Shared NU) (AEP) | 159010 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-213 (100MW/Battery/Storage), into Chamber Springs 161 kV Substation | AEP | 30 | 2250000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Brown 138 kV Substation GEN-2023-214 Interconnection (TOIF) (OGE) | 159011 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-214 (100MW/Battery/Storage), into Brown 138 kV Substation | OGE | 36 | 3924886
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Brown 138 kV Substation GEN-2023-214 Interconnection (Non-Shared NU) (OGE) | 159012 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-214 (100MW/Battery/Storage), into Brown 138 kV Substation | OGE | 36 | 2338281
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Turtle Creek 345 kV Substation GEN-2023-216 Interconnection (TOIF) (NPPD) | 159013 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216 (200MW/Wind), into Turtle Creek 345 kV Substation | NPPD | 36 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Turtle Creek 345 kV Substation GEN-2023-217 Interconnection (TOIF) (NPPD) | 159014 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-217 (200MW/Wind), into Turtle Creek 345 kV Substation | NPPD | 36 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Turtle Creek 345 kV Substation GEN-2023-218 Interconnection (TOIF) (NPPD) | 159015 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-218 (200MW/Wind), into Turtle Creek 345 kV Substation | NPPD | 36 | 1000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Reading - Osage Jct 115 kV Line GEN-2023-219 Interconnection (TOIF) (Evergy) | 159016 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-219 (125MW/Solar), into Reading - Osage Jct 115 kV Line | EVERGY | 36 | 749584
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Reading - Osage Jct 115 kV Line GEN-2023-219 Interconnection (Non-Shared NU) (Evergy) | 159017 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-219 (125MW/Solar), into Reading - Osage Jct 115 kV Line | EVERGY | 36 | 12378356
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (TOIF) (Evergy) | 159018 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | EVERGY | 56 | 1325114
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (Non-Shared NU) (Evergy) | 159019 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | EVERGY | 56 | 27848113
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (TOIF) (Evergy) | 159020 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | EVERGY | 56 | 1325114
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (Non-Shared NU) (Evergy) | 159021 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | EVERGY | 56 | 27848113
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | New Beatrice Power Station 345 kV GEN-2023-222 Interconnection (TOIF) (NPPD) | 159022 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222 (478MW/Thermal), into New Beatrice Power Station 345 kV | NPPD | 36 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | New Beatrice Power Station 345 kV GEN-2023-223 Interconnection (TOIF) (NPPD) | 159023 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-223 (239MW/Thermal), into New Beatrice Power Station 345 kV | NPPD | 36 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Olive Creek 345 kV Substation GEN-2023-224 Interconnection (TOIF) (NPPD) | 159024 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224 (478MW/Thermal), into Olive Creek 345 kV Substation | NPPD | 36 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Olive Creek 345 kV Substation GEN-2023-225 Interconnection (TOIF) (NPPD) | 159025 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-225 (217MW/Thermal), into Olive Creek 345 kV Substation | NPPD | 36 | 1000000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | La Russell 161 kV Substation GEN-2023-226 Interconnection (TOIF) (EDE) | 159026 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-226 (200MW/Battery/Storage), into La Russell 161 kV Substation | EDE | 48 | 874473.75
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | La Russell 161 kV Substation GEN-2023-226 Interconnection (Non-Shared NU) (EDE) | 159027 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-226 (200MW/Battery/Storage), into La Russell 161 kV Substation | EDE | 48 | 3203739.01
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Petty to Chapel 138 kV Line GEN-2023-227 Interconnection (TOIF) (AEP) | 159028 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-227 (200MW/Battery/Storage), into Petty to Chapel 138 kV Line | AEP | 36 | 1925000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Petty to Chapel 138 kV Line GEN-2023-227 Interconnection (Non-Shared NU) (AEP) | 159029 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-227 (200MW/Battery/Storage), into Petty to Chapel 138 kV Line | AEP | 36 | 11500000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco-Okalunion 345 kV line GEN-2023-228 Interconnection (TOIF) (SPS) | 159030 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-228 (250MW/Battery/Storage), into Tuco-Okalunion 345 kV line | SPS | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco-Okalunion 345 kV line GEN-2023-228 Interconnection (Non-Shared NU) (SPS) | 159031 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-228 (250MW/Battery/Storage), into Tuco-Okalunion 345 kV line | SPS | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Southwestern Power Station 138 kV Substation (SWS4) GEN-2023-229 Interconnection (TOIF) (AEP) | 159032 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | AEP | 30 | 1825000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Southwestern Power Station 138 kV Sub (SWS4) GEN-2023-229 Interconnection (Non-Shared NU) (AEP) | 159033 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | AEP | 30 | 800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (TOIF) (AEP) | 159034 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | AEP | 30 | 2275000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (Non-Shared NU) (AEP) | 159035 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | AEP | 30 | 1850000
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Neosho - LaCynge 345 kV Line GEN-2023-231 Interconnection (TOIF) (Evergy) | 159036 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-231 (310MW/Hybrid), into Neosho - LaCynge 345 kV Line | EVERGY | 56 | 1325114
Interconnection | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Neosho - LaCynge 345 kV Line GEN-2023-231 Interconnection (Non-Shared NU) (Evergy) | 159037 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-231 (310MW/Hybrid), into Neosho - LaCynge 345 kV Line | EVERGY | 56 | 77041652
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Chamber Springs 345 kV Substation GEN-2023-235 Interconnection (TOIF) (AEP) | 159038 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-235 (250MW/Battery/Storage), into Chamber Springs 345 kV Substation | AEP | 36 | 2825000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Chamber Springs 345 kV Substation GEN-2023-235 Interconnection (Non-Shared NU) (AEP) | 159039 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-235 (250MW/Battery/Storage), into Chamber Springs 345 kV Substation | AEP | 36 | 5200000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Hobbs - Yoakum 345 kV GEN-2023-236 Interconnection (TOIF) (SPS) | 159040 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-236 (400MW/Solar), into Hobbs - Yoakum 345 Kv | SPS | 48 | 1900000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Hobbs - Yoakum 345 kV GEN-2023-236 Interconnection (Non-Shared NU) (SPS) | 159041 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-236 (400MW/Solar), into Hobbs - Yoakum 345 kV | SPS | 48 | 17684222
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crawfish Draw 345 kV Substation GEN-2023-237 Interconnection (TOIF) (SPS) | 159042 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-237 (500MW/Wind), into Crawfish Draw 345 kV Substation | SPS | 48 | 1900000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crawfish Draw 345 kV Substation GEN-2023-237 Interconnection (Non-Shared NU) (SPS) | 159043 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-237 (500MW/Wind), into Crawfish Draw 345 kV Substation | SPS | 48 | 18553998
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Potter County 345 kV Substation GEN-2023-238 Interconnection (TOIF) (SPS) | 159044 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-238 (280MW/Solar), into Potter County 345 kV Substation | SPS | 48 | 1900000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Potter County 345 kV Substation GEN-2023-238 Interconnection (Non-Shared NU) (SPS) | 159045 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-238 (280MW/Solar), into Potter County 345 kV Substation | SPS | 48 | 11628280
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rolling Hills 230 kV Substation GEN-2023-239 Interconnection (TOIF) (SPS) | 159046 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-239 (300MW/Solar), into Rolling Hills 230 kV Substation | SPS | 48 | 1700000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rolling Hills 230 kV Substation GEN-2023-239 Interconnection (Non-Shared NU) (SPS) | 159047 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-239 (300MW/Solar), into Rolling Hills 230 kV Substation | SPS | 42 | 9035000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tolk 345 kV Substation GEN-2023-240 Interconnection (TOIF) (SPS) | 159048 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-240 (550MW/Solar), into Tolk 345 kV Substation | SPS | 48 | 1900000
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tolk 345 kV Substation GEN-2023-240 Interconnection (Non-Shared NU) (SPS) | 159049 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-240 (550MW/Solar), into Tolk 345 kV Substation | SPS | 48 | 5975000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (TOIF) (AEP) | 159050 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | AEP | 30 | 2025000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (Non-Shared NU) (AEP) | 159051 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | AEP | 30 | 3425000
Interconnection | Steady State | WECC | DISIS-2023-001 | ERIS | Custer - Rosebud Creek 230 kV Line Tap GEN-2023-074 Interconnection (TOIF) (WAPA) | 159061 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-074 (85MW/Solar/Storage), into Custer - Rosebud Creek 230 kV Line Tap | WAPA | 70 | 595000
Interconnection | Steady State | WECC | DISIS-2023-001 | ERIS | Custer - Rosebud Creek 230 kV Line Tap GEN-2023-074 Interconnection (Non-Shared NU) (WAPA) | 159062 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-074 (85MW/Solar/Storage), into Custer - Rosebud Creek 230 kV Line Tap | WAPA | 70 | 22360000
[5 empty] | 679 |  |  |  |  | 7405205012.82

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 01NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 02NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 03NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | WECC | 2 | 23SP | N/A | None | [7 empty] | None
Voltage | WECC | 2 | 28SP | N/A | None | [7 empty] | None
Voltage | WECC | 2 | 28WP | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 773480 G23-075-TAP 345 | 0.9973 | 0.9376 | 0.0597 | 0.9639 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 773481 GEN-2023-075 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 773501 GEN-2023-076 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0762 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0762 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0762 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-017 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0762 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0357 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0357 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0357 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0357 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0357 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0357 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.032 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.032 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.032 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.032 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0379 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0379 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0379 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0379 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.032 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.032 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0379 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0379 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9918 | 0.9383 | 0.0535 | 0.9639 | 0.95 | 1.05 | 0.0329 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0329 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0329 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0329 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.126 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.126 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.126 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.126 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1319 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1319 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1319 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1319 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1384 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0329 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0329 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.126 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.126 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.1319 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.1319 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1384 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1384 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1384 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9973 | 0.9376 | 0.0597 | 0.9639 | 0.95 | 1.05 | 0.0301 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0301 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0301 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0301 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9918 | 0.9383 | 0.0535 | 0.9639 | 0.95 | 1.05 | 0.0631 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0631 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0631 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0631 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0301 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0301 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0631 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0631 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0856 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0856 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0856 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0856 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0636 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0636 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0636 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0636 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0695 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0695 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0695 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0695 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0761 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0636 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0636 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0695 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0695 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0761 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0761 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0761 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0407 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0407 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0407 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0407 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0427 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0427 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0427 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0427 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0583 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0583 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0583 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0583 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0708 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0583 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0583 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0708 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0708 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.042 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.042 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.042 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.042 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0321 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0321 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0321 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0321 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0321 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0321 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0445 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0445 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 773480 G23-075-TAP 345 | 0.9973 | 0.9376 | 0.0597 | 0.9639 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 773481 GEN-2023-075 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 773501 GEN-2023-076 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0617 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0617 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0617 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-042 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0617 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9973 | 0.9376 | 0.0597 | 0.9639 | 0.95 | 1.05 | 0.0329 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0329 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0329 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0329 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9918 | 0.9383 | 0.0535 | 0.9639 | 0.95 | 1.05 | 0.2957 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.2957 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.2957 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.2957 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0329 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0329 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0306 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0306 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0306 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0306 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.2957 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.2957 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0306 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0306 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.1612 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.1612 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.1612 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.1612 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9918 | 0.9383 | 0.0535 | 0.9639 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 773480 G23-075-TAP 345 | 0.9973 | 0.9376 | 0.0597 | 0.9639 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 773481 GEN-2023-075 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 773501 GEN-2023-076 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0323 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0757 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0757 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0757 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-061 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0757 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 773480 G23-075-TAP 345 | 0.9973 | 0.9376 | 0.0597 | 0.9639 | 0.95 | 1.05 | 0.0545 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 773481 GEN-2023-075 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0545 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0545 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 773501 GEN-2023-076 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0545 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0545 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0545 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0413 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0413 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0413 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-063 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0413 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0598 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0598 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0598 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0598 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0658 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0658 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0658 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0658 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0723 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0598 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0598 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0658 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0658 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0723 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0723 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0723 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9918 | 0.9383 | 0.0535 | 0.9639 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0366 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.1519 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.1578 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1643 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1643 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-085 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0508 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0508 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0508 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0508 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0341 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0324 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0324 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0324 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0324 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0302 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0302 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0383 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0383 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0383 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0383 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0442 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0442 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0442 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0442 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0508 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0383 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0383 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0442 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0442 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0508 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0508 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0508 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0319 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0319 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0319 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0319 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0311 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0311 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0311 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0311 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0498 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0557 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0623 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0623 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0349 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0349 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0349 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0349 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.068 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.068 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.068 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.068 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.074 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.074 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.074 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.074 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0805 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.068 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.068 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.074 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.074 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0805 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0805 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0805 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9918 | 0.9383 | 0.0535 | 0.9639 | 0.95 | 1.05 | 0.0425 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0425 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0425 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0425 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0387 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0387 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0387 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0387 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0447 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0447 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0447 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0447 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0512 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0425 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0425 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0387 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0387 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0447 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0447 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0512 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0512 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0512 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0335 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0335 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0335 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0335 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0384 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0384 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0384 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0384 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0449 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0384 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0384 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0449 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0449 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0449 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0327 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0327 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0327 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0327 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0392 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0327 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0327 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0392 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0392 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0392 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0352 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0352 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0352 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0352 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0418 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0352 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0352 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0418 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0418 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0418 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0312 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0312 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0312 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0312 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0362 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0362 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0362 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0362 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0428 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0362 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0362 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0428 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0428 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0428 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0622 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0622 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0622 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0622 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0682 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0682 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0682 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0682 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0747 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0622 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0622 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0682 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0682 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0747 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0747 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0747 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 773480 G23-075-TAP 345 | 0.9973 | 0.9376 | 0.0597 | 0.9639 | 0.95 | 1.05 | 0.0368 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 773481 GEN-2023-075 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0368 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0368 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 773501 GEN-2023-076 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0368 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0368 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0368 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0802 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0802 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0802 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-191 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0802 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9973 | 0.9376 | 0.0597 | 0.9639 | 0.95 | 1.05 | 0.0343 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0343 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0343 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.0343 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9918 | 0.9383 | 0.0535 | 0.9639 | 0.95 | 1.05 | 0.0506 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0506 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0506 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.0506 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0343 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.0343 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0506 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.0506 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.09 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.09 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.09 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.09 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9918 | 0.9383 | 0.0535 | 0.9639 | 0.95 | 1.05 | 0.1216 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.1216 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.1216 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.1216 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1101 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1101 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1101 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1101 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.116 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.116 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.116 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.116 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.1226 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.1216 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.1216 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.1101 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.1101 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.116 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.116 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1226 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.1226 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.1226 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.6391 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.6391 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.6391 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.6391 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0413 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0413 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0413 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0413 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0538 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0413 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0413 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0538 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0538 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0538 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0471 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0471 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0471 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0471 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0536 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0471 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0471 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0536 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0536 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0536 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0412 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0412 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0412 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.997 | 0.9411 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0412 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0537 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0412 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9969 | 0.9446 | 0.0523 | 0.9664 | 0.95 | 1.05 | 0.0412 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0472 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0537 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0537 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0537 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 773480 G23-075-TAP 345 | 0.9973 | 0.9376 | 0.0597 | 0.9639 | 0.95 | 1.05 | 0.031 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 773481 GEN-2023-075 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.031 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.031 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 773501 GEN-2023-076 345 | 0.9973 | 0.9377 | 0.0596 | 0.9639 | 0.95 | 1.05 | 0.031 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.031 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9664 | 0.95 | 1.05 | 0.031 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0705 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0705 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0705 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-226 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.0705 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9918 | 0.9383 | 0.0535 | 0.9639 | 0.95 | 1.05 | 0.2512 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.2512 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.2512 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9918 | 0.9384 | 0.0534 | 0.9639 | 0.95 | 1.05 | 0.2512 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9971 | 0.9412 | 0.0559 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9972 | 0.9426 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9975 | 0.9427 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9973 | 0.9427 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9975 | 0.9429 | 0.0546 | 0.9639 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9977 | 0.9429 | 0.0548 | 0.9639 | 0.95 | 1.05 | 0.0397 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.2512 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9919 | 0.9433 | 0.0486 | 0.9664 | 0.95 | 1.05 | 0.2512 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.997 | 0.9446 | 0.0524 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9971 | 0.946 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9974 | 0.9461 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9971 | 0.9461 | 0.051 | 0.9664 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0397 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9975 | 0.9462 | 0.0513 | 0.9664 | 0.95 | 1.05 | 0.0397 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9974 | 0.9463 | 0.0511 | 0.9664 | 0.95 | 1.05 | 0.0397 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.1387 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.1387 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.1387 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9972 | 0.9494 | 0.0478 | 0.9639 | 0.95 | 1.05 | 0.1387 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0798 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0798 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0798 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0798 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0798 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0798 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0798 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0798 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0362 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0362 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0362 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0362 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0798 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0362 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0362 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0362 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.1107 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.1107 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.1107 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.1107 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0777 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0777 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0777 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0777 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0362 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0362 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0362 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0362 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.1107 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.1107 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.1107 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.1107 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.1107 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.1107 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0657 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0362 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0362 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0777 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0777 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.1107 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.1107 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.6809 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.6809 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.1781 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.1781 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0735 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0735 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.1087 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.1087 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.183 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.183 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0854 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0854 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0347 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.1473 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.1473 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0622 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0622 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0362 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0362 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0362 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0362 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0798 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0798 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-006 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0766 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-015 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0385 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-015 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0385 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-015 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0385 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-015 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0385 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-015 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0385 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-015 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0385 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-015 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0385 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-015 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0385 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0491 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0491 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0491 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0491 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0491 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0491 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0491 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0491 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0491 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0734 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0734 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0734 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0734 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0735 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0734 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0734 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0784 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0784 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.04 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.04 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0811 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0811 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0403 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0303 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0303 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0491 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0491 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-017 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0532 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0507 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0507 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0507 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0507 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0507 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0507 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0507 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0507 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0336 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0336 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0336 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0336 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0507 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0336 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0336 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0321 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0321 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0467 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0467 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0493 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0493 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.04 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.04 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.04 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.04 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0495 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0495 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0507 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0507 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-021 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0497 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.052 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.052 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.052 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.052 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.052 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.052 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.052 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.052 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.036 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.036 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.036 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.036 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.052 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0302 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.036 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.036 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0424 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0424 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0424 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0424 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0424 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0424 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.035 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.035 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0473 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0473 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0489 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0489 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0335 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0335 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0424 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0424 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0424 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0424 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.052 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.052 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-023 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0511 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1295 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1295 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.1295 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 768820 G22-092-TAP 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0301 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 768821 GEN-2022-092 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0301 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 510380 DELWARE7 345 | 0.9854 | 0.9199 | 0.0655 | 0.9449 | 0.92 | 1.05 | 0.0301 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.1295 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.1295 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.1295 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.1295 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.1353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.1353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.1353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.1353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.1417 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.1417 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.1417 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.1417 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.1295 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.1295 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.1417 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.1353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.1353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.1417 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.1417 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.1417 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.1417 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.1417 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.1417 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0462 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0462 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0462 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0462 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.1417 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.1417 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0462 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0462 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0573 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0573 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0749 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0749 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0462 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0462 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.042 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.042 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.035 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.035 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0438 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0438 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.1417 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.1417 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.1417 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.1417 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533763 HUDSON-2 69 | 0.9219 | 0.9017 | 0.0202 | 0.9852 | 0.93 | 1.05 | 0.0439 | P12:69:WERE:LITC-SPIT-69::FUTURE:HV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533773 SOPITT 2 69 | 0.925 | 0.9049 | 0.0201 | 0.9882 | 0.93 | 1.05 | 0.0439 | P12:69:WERE:LITC-SPIT-69::FUTURE:HV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 768820 G22-092-TAP 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0653 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 768821 GEN-2022-092 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0653 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 510380 DELWARE7 345 | 0.9854 | 0.9199 | 0.0655 | 0.9449 | 0.92 | 1.05 | 0.0653 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0714 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0714 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0714 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0714 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0714 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0714 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0714 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0714 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0653 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0653 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0653 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0653 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0714 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 533760 ERIE 2 69 | 0.9869 | 0.9298 | 0.0571 | 0.9544 | 0.93 | 1.05 | 0.0453 | 533639 MARMATN2 69.0 533647 UN1ELSM2 69.0 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0653 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0653 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0574 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0574 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0574 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0574 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0835 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0574 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0574 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0341 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0341 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0805 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0805 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0439 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0439 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0651 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0651 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0319 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0319 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0714 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0714 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-025 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0796 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0616 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0616 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0616 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.059 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.059 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.059 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.059 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.059 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.059 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0616 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0616 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0616 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0616 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.059 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.059 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0674 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0674 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0674 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0674 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0738 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0738 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0738 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0738 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.059 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0616 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0616 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0738 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0674 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0674 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0738 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0738 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0474 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0474 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0474 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0474 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0738 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0738 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0738 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0738 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.1883 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.1883 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.1883 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.1883 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0474 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0474 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0474 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0474 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0474 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0474 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0738 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0738 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.1883 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.1883 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0419 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0419 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0474 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0474 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.1883 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.1883 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0766 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0766 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.2092 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.2092 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0608 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0608 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0364 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0364 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0532 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0532 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.1185 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.1185 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0738 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0738 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0738 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0738 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0356 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0356 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.059 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.059 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-026 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0578 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0505 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0505 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0505 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0505 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0505 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0505 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0505 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0505 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0318 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0318 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0318 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0318 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0505 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0318 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0318 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0382 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0382 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0382 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0382 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0382 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0382 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0471 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0471 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0504 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0504 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0375 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0375 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0304 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0304 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0304 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0304 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0304 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0304 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0304 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0304 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0304 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0304 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0304 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0304 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0382 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0382 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0382 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0382 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0699 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0699 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0505 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0505 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-032 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0495 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0504 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0504 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0504 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0504 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0504 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0504 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0504 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0504 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.034 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.034 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.034 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.034 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0504 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.034 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.034 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0404 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0404 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0404 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0404 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0404 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0404 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0328 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0328 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0463 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0463 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0483 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0483 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0345 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0345 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0404 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0404 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0404 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0404 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.036 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.036 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0504 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0504 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-033 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0495 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0621 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0621 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0621 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0621 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0621 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0621 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0621 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0679 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0679 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0679 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0679 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0743 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0743 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0743 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0743 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0621 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0621 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0743 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0679 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0679 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0743 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0743 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0743 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0743 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0743 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0743 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0357 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0357 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0357 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0357 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0743 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0743 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0357 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0357 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.1266 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.1266 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.1581 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.1581 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0357 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0357 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0332 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0332 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0346 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0346 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0743 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0743 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0743 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0743 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0505 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0505 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0505 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0505 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0505 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0505 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0505 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0505 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0333 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0333 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0333 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0333 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0505 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0333 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0333 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0396 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0396 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0396 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0396 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0396 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0396 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0316 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0316 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0466 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0466 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0493 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0493 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0355 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0355 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0396 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0396 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0396 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0396 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0542 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0542 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0505 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0505 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-036 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0495 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0519 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0519 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0519 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0519 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0519 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0519 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0519 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0519 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0519 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0351 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0351 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0472 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0472 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0487 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0487 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0334 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0334 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0425 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0425 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0425 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0425 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0519 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0519 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-037 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.051 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-039 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-039 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-039 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-039 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-039 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-039 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-039 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-039 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.1066 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.1066 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.1066 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.1066 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0581 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.1066 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.1066 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.075 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.075 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0319 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0319 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.1143 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.1143 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-042 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0485 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-043 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-043 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-043 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-043 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-043 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-043 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-043 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-043 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-044 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-044 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-044 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-044 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-044 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-044 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-044 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-044 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-045 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-045 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-045 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-045 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-045 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-045 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-045 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-045 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-046 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-046 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-046 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-046 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-046 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-046 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-046 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-046 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-047 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-047 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-047 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-047 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-047 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-047 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-047 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-047 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-048 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-048 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-048 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-048 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-048 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-048 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-048 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-048 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 768820 G22-092-TAP 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.2988 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 768821 GEN-2022-092 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.2988 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 510380 DELWARE7 345 | 0.9854 | 0.9199 | 0.0655 | 0.9449 | 0.92 | 1.05 | 0.2988 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.1794 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.1794 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.1794 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.1794 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.1794 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.1794 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.1794 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.1794 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0325 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0325 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0325 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0325 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.2988 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.2988 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.2988 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.2988 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.1794 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0325 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.159 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.159 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.159 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.159 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0325 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0325 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.2988 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.2988 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.159 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.159 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0592 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0592 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0592 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0592 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0375 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0375 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0375 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0375 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0325 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0325 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0325 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0325 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.159 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.159 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.159 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.159 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0592 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0592 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0592 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0592 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0592 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0592 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.159 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.159 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0325 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0325 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0375 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0375 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0592 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0592 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0961 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0961 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.1985 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.1985 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0455 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0455 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.103 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.103 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0452 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0452 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0391 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.084 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.084 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0682 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0682 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0325 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0325 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0325 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0325 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.1794 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.1794 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-050 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.1711 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 768820 G22-092-TAP 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 768821 GEN-2022-092 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 510380 DELWARE7 345 | 0.9854 | 0.9199 | 0.0655 | 0.9449 | 0.92 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0314 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0314 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0314 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0314 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0314 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0314 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0314 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0314 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0314 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0429 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0429 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0609 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0609 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0497 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0497 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0309 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0309 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0451 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0451 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0375 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0375 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.047 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.047 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.1677 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.1677 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.1677 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.1677 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0314 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0314 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-052 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0307 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0481 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0481 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0481 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0481 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0481 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0481 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0481 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0481 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0481 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.073 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.073 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.073 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.073 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.073 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.073 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.074 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.074 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.074 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.074 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.073 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.073 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.073 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.073 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.073 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.073 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.074 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.074 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.078 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.078 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0398 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0398 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0817 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0817 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0303 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0303 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0481 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0481 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-061 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0521 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0362 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0723 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0723 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.035 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.035 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0708 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.034 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.034 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773480 G23-075-TAP 345 | 0.9951 | 0.9499 | 0.0452 | 0.9518 | 0.95 | 1.05 | 1 | 773240 G23-063-TAP 138 773241 GEN-2023-063 138 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773480 G23-075-TAP 345 | 0.9951 | 0.9499 | 0.0452 | 0.9518 | 0.95 | 1.05 | 1 | 773241 GEN-2023-063 138 773242 G23-063XFMR1 34.5 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773481 GEN-2023-075 345 | 0.9951 | 0.9499 | 0.0452 | 0.9518 | 0.95 | 1.05 | 1 | 773240 G23-063-TAP 138 773241 GEN-2023-063 138 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773481 GEN-2023-075 345 | 0.9951 | 0.9499 | 0.0452 | 0.9518 | 0.95 | 1.05 | 1 | 773241 GEN-2023-063 138 773242 G23-063XFMR1 34.5 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773488 G23-075XFMRH 345 | 0.9951 | 0.9499 | 0.0452 | 0.9519 | 0.95 | 1.05 | 1 | 773240 G23-063-TAP 138 773241 GEN-2023-063 138 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-063 | 773488 G23-075XFMRH 345 | 0.9951 | 0.9499 | 0.0452 | 0.9519 | 0.95 | 1.05 | 1 | 773241 GEN-2023-063 138 773242 G23-063XFMR1 34.5 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0624 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0624 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0624 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0624 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0624 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0624 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0624 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0681 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0681 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0681 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0681 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0624 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0624 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0681 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0681 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0745 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0745 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0745 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0745 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0745 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0745 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0732 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0732 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.095 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.095 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0366 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0366 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0745 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0745 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0745 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0745 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-068 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-068 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-068 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-068 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-068 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-068 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-068 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-068 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 768820 G22-092-TAP 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 768821 GEN-2022-092 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 510380 DELWARE7 345 | 0.9854 | 0.9199 | 0.0655 | 0.9449 | 0.92 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0314 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0314 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0314 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0314 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0314 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0314 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0314 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0314 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0314 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.1555 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.1677 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.1613 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.1677 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0336 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.1677 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0497 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0429 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0429 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0609 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0609 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0497 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0497 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0309 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0309 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0451 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0451 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0375 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0375 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.047 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.047 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.1677 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.1677 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.1677 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.1677 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0314 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0314 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-073 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0307 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0325 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0325 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0325 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0325 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0325 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0325 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0325 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0325 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0325 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0612 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0612 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0612 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0612 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0488 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0612 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0612 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0316 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0316 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0383 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0383 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0689 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0689 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0559 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0559 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0559 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0559 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0559 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0559 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0307 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0559 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0559 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0559 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0559 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0559 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0559 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9945 | 0.9499 | 0.0446 | 0.9518 | 0.95 | 1.05 | 0.0358 | P23:500:EES-EAI:INDEP2:B6126
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0358 | P22:500:EES-EAI:WRIGHT_E:768
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9945 | 0.9499 | 0.0446 | 0.9519 | 0.95 | 1.05 | 0.0358 | P23:500:EES-EAI:INDEP2:B6126
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0358 | P22:500:EES-EAI:WRIGHT_E:768
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9945 | 0.9499 | 0.0446 | 0.9519 | 0.95 | 1.05 | 0.0358 | P23:500:EES-EAI:INDEP2:B6126
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0358 | P23:EHV:EES::8WRIGHTSVLE%:6
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0358 | P22:500:EES-EAI:WRIGHT_E:768
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0358 | P23:EHV:EES::8WRIGHTSVLE%:6
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0358 | P23:EHV:EES::8WRIGHTSVLE%:6
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0332 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0332 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0325 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0325 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-085 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0321 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0549 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0549 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0549 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0549 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0549 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0549 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0549 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0549 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0315 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0315 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0315 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0315 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0379 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0379 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0379 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0379 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0549 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0379 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0315 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0315 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0379 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0379 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0334 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0334 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0334 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0334 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.035 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.035 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.035 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.035 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0379 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0379 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0379 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0379 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0334 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0334 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0334 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0334 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0334 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0334 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0325 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0379 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0379 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.035 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.035 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0334 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0334 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0536 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0536 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.056 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.056 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0427 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0427 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0379 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0379 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0379 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0379 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.1236 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.1236 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0549 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0549 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-087 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0539 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0364 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0364 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0364 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0364 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0317 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0317 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0317 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0364 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0364 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0317 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0324 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-093 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-093 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-093 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-093 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-093 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-093 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-093 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-093 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-094 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-094 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-094 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-094 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-094 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-094 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-094 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-094 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0413 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.039 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.039 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.039 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.039 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.039 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.039 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.039 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.039 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0438 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0438 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0438 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0438 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.039 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.038 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0438 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0438 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0502 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0502 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0502 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0502 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0502 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0502 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0359 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0359 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0532 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0532 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0373 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0373 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0502 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0502 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0502 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0502 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.039 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.039 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-099 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0388 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-107 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-107 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-107 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-107 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-107 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-107 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-107 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-107 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0337 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0683 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0683 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0894 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0894 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0352 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0352 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0646 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0646 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0646 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0646 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0421 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0421 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0421 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0421 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0421 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0421 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0421 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0421 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0421 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0356 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0356 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0356 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0356 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0356 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0356 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0411 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0411 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0439 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0439 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0433 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0433 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0525 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0525 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0525 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0525 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0525 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0525 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0525 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0525 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0525 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0525 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0525 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0525 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9945 | 0.9499 | 0.0446 | 0.9518 | 0.95 | 1.05 | 0.0396 | P23:500:EES-EAI:INDEP2:B6126
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0396 | P22:500:EES-EAI:WRIGHT_E:768
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9945 | 0.9499 | 0.0446 | 0.9519 | 0.95 | 1.05 | 0.0396 | P23:500:EES-EAI:INDEP2:B6126
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0396 | P22:500:EES-EAI:WRIGHT_E:768
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9945 | 0.9499 | 0.0446 | 0.9519 | 0.95 | 1.05 | 0.0396 | P23:500:EES-EAI:INDEP2:B6126
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0396 | P23:EHV:EES::8WRIGHTSVLE%:6
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0396 | P22:500:EES-EAI:WRIGHT_E:768
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0396 | P23:EHV:EES::8WRIGHTSVLE%:6
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0396 | P23:EHV:EES::8WRIGHTSVLE%:6
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0585 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0585 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0421 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0421 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-115 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0411 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0524 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0582 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0646 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0352 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0683 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0683 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0894 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0894 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0352 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0352 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0646 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0646 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0646 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0646 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0338 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0338 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0338 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0338 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0402 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0402 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0402 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0402 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0402 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0338 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0338 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0402 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0402 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0402 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0402 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0402 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0402 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0402 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0402 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0841 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0841 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.035 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.035 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0343 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0343 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0359 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0359 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0402 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0402 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0402 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0402 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0661 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0661 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0661 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0568 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0568 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0568 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0568 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0568 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0568 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0661 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0661 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0661 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0661 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0568 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0568 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0719 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0719 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0719 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0719 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0783 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0783 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0783 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0783 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0568 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0661 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0661 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0783 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0719 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0719 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0783 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0783 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0491 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0491 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0491 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0491 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0783 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0783 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0783 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0783 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.2137 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.2137 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.2137 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.2137 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0491 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0491 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0491 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0491 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0491 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0491 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0783 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0783 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.2137 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.2137 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0434 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0434 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0491 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0491 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.2137 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.2137 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0794 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0794 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.2316 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.2316 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0691 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0691 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0365 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0365 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0591 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0591 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.1035 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.1035 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0783 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0783 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0783 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0783 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0568 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0568 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-122 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0556 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0366 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0366 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0366 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 768820 G22-092-TAP 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0402 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 768821 GEN-2022-092 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0402 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 510380 DELWARE7 345 | 0.9854 | 0.9199 | 0.0655 | 0.9449 | 0.92 | 1.05 | 0.0402 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0704 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0704 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0704 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0704 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0704 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0704 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0366 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0366 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0366 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0366 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0704 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0704 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0424 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0424 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0424 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0424 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0488 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0488 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0488 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0488 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0402 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0402 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0402 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0402 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0704 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0366 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0366 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0488 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0424 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0424 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0488 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0488 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0402 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0402 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0375 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0375 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0375 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0375 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0488 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0488 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0488 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0488 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0485 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0485 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0485 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0485 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0375 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0375 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0375 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0375 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0375 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0375 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0345 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0488 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0488 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0485 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0485 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0339 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0339 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0375 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0375 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0485 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0485 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0608 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0608 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0855 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0855 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0359 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0359 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.1819 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.1819 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0488 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0488 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0488 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0488 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.087 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.087 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0704 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0704 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-149 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0685 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0586 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0586 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0586 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0586 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0586 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0586 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0586 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0586 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0586 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0303 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0361 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0314 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0314 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0314 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0314 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0314 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0314 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0314 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0314 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0314 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0314 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0301 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0425 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0328 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0328 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0314 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0314 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0512 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0512 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0579 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0579 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0365 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0365 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0425 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0425 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0425 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0425 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.1479 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.1479 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0586 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0586 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-157 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0582 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0423 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0423 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0423 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0423 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0423 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0423 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0423 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0423 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0372 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0372 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0372 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0372 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0423 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0372 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0372 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0372 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0372 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0372 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0372 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0372 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0372 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0372 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0316 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0316 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0397 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0397 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0363 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0363 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0316 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0316 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0352 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0352 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0352 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0352 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0352 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0352 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0372 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0372 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0372 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0372 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0423 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0423 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-163 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0414 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0498 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0498 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0498 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0498 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0498 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0498 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0498 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0498 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0395 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0395 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0395 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0395 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0498 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0395 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0395 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0395 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0395 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0395 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0395 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0395 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0395 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0395 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0317 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0317 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.046 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.046 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0482 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0482 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0352 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0395 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0395 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0395 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0395 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0459 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0459 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0498 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0498 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-169 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0489 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0398 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0398 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0398 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0398 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0398 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0398 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0398 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0398 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0398 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0337 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0337 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0337 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0337 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0337 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0337 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0387 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0387 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0412 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0412 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0414 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0414 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0572 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0572 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0572 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0572 | P12:EHV:EES::8ANO%:FTSMITH8%:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0572 | P12:500:EES-EAI:ARK_NU:FTSMTH:1
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9937 | 0.949 | 0.0447 | 0.9558 | 0.95 | 1.05 | 0.0572 | P12:500:OKGE-EESAR:OKGE-EESEAI:BKRBKR317:::
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0572 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0572 | P23:500:EES-EAI:ARK_NU:B5106
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0572 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0572 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0572 | P42:500:OKGE:SB_FTTH8585::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9938 | 0.9492 | 0.0446 | 0.9558 | 0.95 | 1.05 | 0.0572 | P42:500:OKGE:SB_FTTH8581::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9945 | 0.9499 | 0.0446 | 0.9518 | 0.95 | 1.05 | 0.04 | P23:500:EES-EAI:INDEP2:B6126
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.04 | P22:500:EES-EAI:WRIGHT_E:768
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9945 | 0.9499 | 0.0446 | 0.9519 | 0.95 | 1.05 | 0.04 | P23:500:EES-EAI:INDEP2:B6126
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.04 | P22:500:EES-EAI:WRIGHT_E:768
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9945 | 0.9499 | 0.0446 | 0.9519 | 0.95 | 1.05 | 0.04 | P23:500:EES-EAI:INDEP2:B6126
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.04 | P23:EHV:EES::8WRIGHTSVLE%:6
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.04 | P22:500:EES-EAI:WRIGHT_E:768
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.04 | P23:EHV:EES::8WRIGHTSVLE%:6
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.04 | P23:EHV:EES::8WRIGHTSVLE%:6
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0461 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0461 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0398 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0398 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-170 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0387 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0509 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0509 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0509 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0509 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0509 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0509 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0509 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0509 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0342 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0342 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0342 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0342 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0509 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0406 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0342 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0342 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0406 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0406 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0406 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0406 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0406 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0406 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0406 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0328 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0328 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0467 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0467 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0491 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0491 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0347 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0347 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0406 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0406 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0406 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0406 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0413 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0413 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0509 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0509 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-171 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0499 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-172 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-172 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-172 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-172 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-172 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-172 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-172 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-172 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-173 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-173 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-173 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-173 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-173 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-173 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-173 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-173 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0381 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-175 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0378 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-175 | 773480 G23-075-TAP 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0378 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-175 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0378 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-175 | 773481 GEN-2023-075 345 | 0.9947 | 0.9499 | 0.0448 | 0.9518 | 0.95 | 1.05 | 0.0378 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-175 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0378 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-175 | 773488 G23-075XFMRH 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0378 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-175 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0378 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-175 | 773501 GEN-2023-076 345 | 0.9947 | 0.9499 | 0.0448 | 0.9519 | 0.95 | 1.05 | 0.0378 | 523961 POTTER_CO 7 345 525549 TOLK 7 345 2
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0659 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0659 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0659 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0659 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0659 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0659 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0659 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0717 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0717 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0717 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0717 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0781 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0781 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0781 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0781 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0659 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0659 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0781 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0717 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0717 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0781 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0781 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0781 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0781 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0781 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0781 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0781 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0781 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0366 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.1173 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.1173 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.1461 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.1461 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0366 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0366 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0336 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0336 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.035 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.035 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0781 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0781 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0781 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0781 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0413 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0413 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0413 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0413 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0413 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0413 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0413 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0413 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0413 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0739 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0739 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0739 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0739 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0772 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0739 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0739 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0938 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0938 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0358 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0358 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0816 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0816 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.046 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0332 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0332 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0413 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0413 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-191 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0481 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 768820 G22-092-TAP 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0536 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 768821 GEN-2022-092 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.0536 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 510380 DELWARE7 345 | 0.9854 | 0.9199 | 0.0655 | 0.9449 | 0.92 | 1.05 | 0.0536 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.063 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.063 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.063 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.063 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.063 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.063 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.063 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.063 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0536 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.0536 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0536 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.0536 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.063 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0536 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.0536 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0684 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0684 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0684 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0684 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0872 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0684 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0684 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.1026 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.1026 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0387 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0387 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0761 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0761 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.035 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.035 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.063 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.063 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-194 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0694 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1111 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1111 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.1111 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 768820 G22-092-TAP 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.1206 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 768821 GEN-2022-092 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.1206 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 510380 DELWARE7 345 | 0.9854 | 0.9199 | 0.0655 | 0.9449 | 0.92 | 1.05 | 0.1206 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.08 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.08 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.08 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.08 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.08 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.08 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.1111 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.1111 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.1111 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.1111 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.08 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.08 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.1169 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.1169 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.1169 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.1169 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.1233 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.1233 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.1233 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.1233 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.1206 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.1206 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.1206 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.1206 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.08 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.1111 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.1111 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.1233 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.1169 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.1169 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.1233 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.1233 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.1206 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.1206 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0323 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0323 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0323 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0323 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.1233 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.1233 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.1233 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.1233 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0323 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0323 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0323 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0323 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0323 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0323 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.6407 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.1233 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.1233 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0443 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0443 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0323 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0323 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0523 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0523 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0843 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0843 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0641 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0641 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0528 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0528 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0539 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0539 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.1233 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.1233 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.1233 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.1233 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.08 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.08 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-200 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0768 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0387 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0387 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0387 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0387 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0387 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0387 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0387 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0387 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0387 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0391 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0391 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0568 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0568 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0372 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0372 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0533 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0533 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0533 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0533 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0387 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0387 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-219 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0401 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.041 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.041 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.041 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0404 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0404 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0404 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0404 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0404 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0404 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.041 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.041 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.041 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.041 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0404 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0404 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0467 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0467 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0467 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0467 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0404 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.041 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.041 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0467 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0467 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0532 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0532 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0532 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0532 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0532 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0532 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0391 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0391 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0569 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0569 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0313 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0313 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0384 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0384 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0532 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0532 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0532 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0532 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0404 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0404 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-220 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0405 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 768820 G22-092-TAP 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 768821 GEN-2022-092 345 | 0.989 | 0.918 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 510380 DELWARE7 345 | 0.9893 | 0.9188 | 0.0705 | 0.9449 | 0.92 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0402 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0402 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0402 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0402 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0402 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0402 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9897 | 0.9257 | 0.064 | 0.9518 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9897 | 0.9257 | 0.064 | 0.9519 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0402 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0402 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9901 | 0.929 | 0.0611 | 0.9518 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9901 | 0.929 | 0.0611 | 0.9519 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0402 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9904 | 0.9306 | 0.0598 | 0.9558 | 0.95 | 1.05 | 0.0411 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9908 | 0.9338 | 0.057 | 0.9558 | 0.95 | 1.05 | 0.0469 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.993 | 0.9412 | 0.0518 | 0.9518 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.993 | 0.9412 | 0.0518 | 0.9519 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0533 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9936 | 0.9454 | 0.0482 | 0.9558 | 0.95 | 1.05 | 0.0313 | P23:345:WERE:LATH-BKRS:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0393 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9937 | 0.9463 | 0.0474 | 0.9558 | 0.95 | 1.05 | 0.0393 | P12:345:OKGE:BKRBKR400::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0572 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9937 | 0.9467 | 0.047 | 0.9558 | 0.95 | 1.05 | 0.0572 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0313 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9935 | 0.9468 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0313 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0383 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.0383 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0533 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0533 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0533 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0533 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0402 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0402 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-221 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0403 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.0442 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.0442 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0442 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.0442 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.0442 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.0442 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.0442 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.0442 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.0442 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0751 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0751 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0751 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0751 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.0678 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0751 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0751 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0688 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.0688 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0405 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0405 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0389 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0314 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0314 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.0442 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.0442 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-226 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.0467 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 768820 G22-092-TAP 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 768821 GEN-2022-092 345 | 0.9885 | 0.9125 | 0.076 | 0.9449 | 0.92 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 510380 DELWARE7 345 | 0.9888 | 0.9134 | 0.0754 | 0.9449 | 0.92 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 768820 G22-092-TAP 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 768821 GEN-2022-092 345 | 0.9891 | 0.9181 | 0.071 | 0.9449 | 0.92 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 510380 DELWARE7 345 | 0.9894 | 0.9188 | 0.0706 | 0.9449 | 0.92 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 768820 G22-092-TAP 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.2533 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 768821 GEN-2022-092 345 | 0.9849 | 0.9197 | 0.0652 | 0.9449 | 0.92 | 1.05 | 0.2533 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 768820 G22-092-TAP 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 768821 GEN-2022-092 345 | 0.9893 | 0.9197 | 0.0696 | 0.9449 | 0.92 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 510380 DELWARE7 345 | 0.9854 | 0.9199 | 0.0655 | 0.9449 | 0.92 | 1.05 | 0.2533 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9893 | 0.9203 | 0.069 | 0.9518 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9893 | 0.9203 | 0.069 | 0.9519 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533008 TV1MNDV4 138 | 0.9818 | 0.9204 | 0.0614 | 0.9593 | 0.93 | 1.05 | 0.1603 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533008 TV1MNDV4 138 | 0.982 | 0.9209 | 0.0611 | 0.9593 | 0.93 | 1.05 | 0.1603 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533008 TV1MNDV4 138 | 0.9821 | 0.9232 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.1603 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533008 TV1MNDV4 138 | 0.9823 | 0.9234 | 0.0589 | 0.9593 | 0.93 | 1.05 | 0.1603 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533003 LIBERTY4 138 | 0.9855 | 0.9236 | 0.0619 | 0.9631 | 0.93 | 1.05 | 0.1603 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533003 LIBERTY4 138 | 0.9855 | 0.924 | 0.0615 | 0.9631 | 0.93 | 1.05 | 0.1603 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.99 | 0.9254 | 0.0646 | 0.9558 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9898 | 0.9257 | 0.0641 | 0.9518 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9898 | 0.9257 | 0.0641 | 0.9519 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533003 LIBERTY4 138 | 0.9861 | 0.9271 | 0.059 | 0.9631 | 0.93 | 1.05 | 0.1603 | 532793 NEOSHO 7 345 765110 G20-052-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533003 LIBERTY4 138 | 0.9862 | 0.9271 | 0.0591 | 0.9631 | 0.93 | 1.05 | 0.1603 | 765110 G20-052-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.99 | 0.9273 | 0.0627 | 0.9518 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.99 | 0.9273 | 0.0627 | 0.9519 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533008 TV1MNDV4 138 | 0.9862 | 0.9281 | 0.0581 | 0.9593 | 0.93 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0354 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9906 | 0.9291 | 0.0615 | 0.9518 | 0.95 | 1.05 | 0.0354 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0354 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9906 | 0.9291 | 0.0615 | 0.9519 | 0.95 | 1.05 | 0.0354 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.2533 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9856 | 0.9295 | 0.0561 | 0.9518 | 0.95 | 1.05 | 0.2533 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.2533 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9856 | 0.9295 | 0.0561 | 0.9519 | 0.95 | 1.05 | 0.2533 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 533760 ERIE 2 69 | 0.9801 | 0.9298 | 0.0503 | 0.9544 | 0.93 | 1.05 | 0.1603 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9905 | 0.9306 | 0.0599 | 0.9558 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9907 | 0.9322 | 0.0585 | 0.9558 | 0.95 | 1.05 | 0.0354 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9901 | 0.9329 | 0.0572 | 0.9518 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9901 | 0.9329 | 0.0572 | 0.9519 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0354 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9913 | 0.9339 | 0.0574 | 0.9558 | 0.95 | 1.05 | 0.0354 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.2533 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9864 | 0.9352 | 0.0512 | 0.9558 | 0.95 | 1.05 | 0.2533 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9907 | 0.9371 | 0.0536 | 0.9558 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0555 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9914 | 0.9395 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.0555 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0555 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9914 | 0.9395 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.0555 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0358 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9908 | 0.94 | 0.0508 | 0.9518 | 0.95 | 1.05 | 0.0358 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0358 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9908 | 0.94 | 0.0508 | 0.9519 | 0.95 | 1.05 | 0.0358 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0354 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.995 | 0.9409 | 0.0541 | 0.9518 | 0.95 | 1.05 | 0.0354 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.995 | 0.9409 | 0.0541 | 0.9519 | 0.95 | 1.05 | 0.0354 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.995 | 0.941 | 0.054 | 0.9519 | 0.95 | 1.05 | 0.0354 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9929 | 0.941 | 0.0519 | 0.9518 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9929 | 0.941 | 0.0519 | 0.9519 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0555 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.992 | 0.9416 | 0.0504 | 0.9518 | 0.95 | 1.05 | 0.0555 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0555 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.992 | 0.9417 | 0.0503 | 0.9519 | 0.95 | 1.05 | 0.0555 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0555 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9922 | 0.9443 | 0.0479 | 0.9558 | 0.95 | 1.05 | 0.0555 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9935 | 0.9452 | 0.0483 | 0.9558 | 0.95 | 1.05 | 0.1371 | P12:345:WERE:CANR-LATH-345:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0354 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9955 | 0.9453 | 0.0502 | 0.9558 | 0.95 | 1.05 | 0.0354 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0358 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.992 | 0.9457 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0358 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0555 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.993 | 0.9467 | 0.0463 | 0.9558 | 0.95 | 1.05 | 0.0555 | 300739 7BLACKBERRY 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.09 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9939 | 0.9472 | 0.0467 | 0.9558 | 0.95 | 1.05 | 0.09 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.3077 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9909 | 0.9473 | 0.0436 | 0.9558 | 0.95 | 1.05 | 0.3077 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9939 | 0.9474 | 0.0465 | 0.9558 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_WONG7313::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0529 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9924 | 0.9476 | 0.0448 | 0.9558 | 0.95 | 1.05 | 0.0529 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0875 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9934 | 0.9477 | 0.0457 | 0.9558 | 0.95 | 1.05 | 0.0875 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0435 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9942 | 0.9487 | 0.0455 | 0.9558 | 0.95 | 1.05 | 0.0435 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765350 GEN-2021-006 345 | 0.9938 | 0.9491 | 0.0447 | 0.9733 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 532793 NEOSHO 7 345 | 0.9939 | 0.9491 | 0.0448 | 0.9734 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 772981 GEN-2023-050 345 | 0.9939 | 0.9492 | 0.0447 | 0.9734 | 0.95 | 1.05 | 0.0351 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0729 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9939 | 0.9494 | 0.0445 | 0.9558 | 0.95 | 1.05 | 0.0729 | 300045 7MORGAN 345 300949 7JASPER 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0916 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9927 | 0.9498 | 0.0429 | 0.9558 | 0.95 | 1.05 | 0.0916 | 541200 PHILL 7 345 542981 LACYGNE7 345 1
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0354 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9944 | 0.9499 | 0.0445 | 0.9518 | 0.95 | 1.05 | 0.0354 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0354 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9944 | 0.9499 | 0.0445 | 0.9519 | 0.95 | 1.05 | 0.0354 | P11:345:OKGE:BKRBKR_GSU04::::
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0358 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9929 | 0.9499 | 0.043 | 0.9558 | 0.95 | 1.05 | 0.0358 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 768820 G22-092-TAP 345 | 0.9946 | 0.9449 | 0.0497 | 0.9449 | 0.95 | 1.05 | 0.1603 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 510380 DELWARE7 345 | 0.9948 | 0.9449 | 0.0499 | 0.9449 | 0.95 | 1.05 | 0.1603 | System Intact
Voltage | 03ALL | 2 | 27SP | GEN-2023-231 | 770500 G22-176-TAP 345 | 0.9973 | 0.9491 | 0.0482 | 0.9491 | 0.95 | 1.05 | 0.1531 | System Intact
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0356 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0356 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0356 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0356 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0356 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0356 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0361 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0361 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0361 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0361 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0361 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0361 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0361 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0664 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0664 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0664 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0664 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0664 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0664 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773480 G23-075-TAP 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.1104 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773481 GEN-2023-075 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.1104 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.1104 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-006 | 773501 GEN-2023-076 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.1104 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0412 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0412 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0412 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0412 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0412 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0412 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0742 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0742 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0742 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0742 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0742 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-017 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0742 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.033 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.033 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.033 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.033 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0399 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0399 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0399 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0399 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.033 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.033 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0399 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0399 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-021 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0399 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0353 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0423 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-023 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0423 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1279 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1279 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1279 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1279 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1346 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1346 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1346 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1346 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1416 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1416 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1416 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1416 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.1279 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.1279 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.1346 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.1346 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.1416 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.1416 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-024 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.1416 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.038 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.038 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.038 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.038 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.038 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.038 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9823 | 0.9366 | 0.0457 | 0.9597 | 0.95 | 1.05 | 0.0651 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0651 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0651 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0651 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.0651 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.0651 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0842 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0842 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0842 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0842 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0842 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-025 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0842 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.06 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.06 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.06 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.06 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0667 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0667 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0667 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0667 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0737 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0737 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0737 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0737 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.06 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.06 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0667 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0667 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0737 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0737 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0737 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773480 G23-075-TAP 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0471 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773481 GEN-2023-075 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0471 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0471 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-026 | 773501 GEN-2023-076 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0471 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0312 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0312 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0312 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0312 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0312 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0312 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0382 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-032 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0382 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0334 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0334 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0404 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-033 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0404 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0605 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0605 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0605 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0605 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0672 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0672 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0672 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0672 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0742 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0742 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0742 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0742 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0605 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0605 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0672 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0672 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0742 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0742 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-034 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0742 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0326 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0326 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0326 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0326 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0326 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0326 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0396 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-036 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0396 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0354 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0424 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-037 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0424 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0494 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0494 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0494 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0494 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0494 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0494 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0588 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0588 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0588 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0588 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0588 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-042 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0588 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.04 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9823 | 0.9366 | 0.0457 | 0.9597 | 0.95 | 1.05 | 0.2986 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.2986 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.2986 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.2986 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0324 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0324 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0324 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0324 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.2986 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.2986 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0324 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0324 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0324 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.1597 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.1597 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.1597 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.1597 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.1597 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.1597 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773480 G23-075-TAP 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0589 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773481 GEN-2023-075 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0589 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0589 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-050 | 773501 GEN-2023-076 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0589 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9823 | 0.9366 | 0.0457 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-052 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0413 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0413 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0413 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0413 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0413 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0413 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0737 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0737 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0737 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0737 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0737 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-061 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0737 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0717 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0717 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0717 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0717 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0717 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0717 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0369 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0369 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0369 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0369 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0369 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-063 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0369 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0607 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0607 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0607 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0607 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0675 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0675 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0675 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0675 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0607 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0607 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0675 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0675 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0745 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-065 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0745 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9823 | 0.9366 | 0.0457 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.1539 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.1606 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.0334 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.1676 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-073 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.1676 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0495 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0495 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0495 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0495 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0495 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-085 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0495 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0378 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0378 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0378 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0378 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0308 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0378 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0378 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0378 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0332 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0332 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0332 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0332 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0332 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0332 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773480 G23-075-TAP 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0331 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773481 GEN-2023-075 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0331 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0331 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-087 | 773501 GEN-2023-076 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0331 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-089 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-090 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0316 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-091 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0316 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0364 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0364 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0364 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0364 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0432 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0432 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0432 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0432 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0364 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0364 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0432 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0432 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0502 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-099 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0502 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-111 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-115 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0314 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-115 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0314 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-115 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0314 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-115 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0314 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-115 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0314 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-115 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0314 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0508 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0576 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0646 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-118 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0646 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0401 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0401 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0401 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0401 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0331 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0401 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0401 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-121 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0401 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0645 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0645 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0645 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0645 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0712 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0712 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0712 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0712 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0782 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0782 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0782 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0782 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0645 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0645 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0712 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0712 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0782 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0782 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0782 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773480 G23-075-TAP 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0488 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773481 GEN-2023-075 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0488 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0488 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-122 | 773501 GEN-2023-076 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0488 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.035 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.035 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.035 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.035 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9823 | 0.9366 | 0.0457 | 0.9597 | 0.95 | 1.05 | 0.04 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.04 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.04 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.04 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0417 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0417 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0417 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0417 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0487 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0487 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0487 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0487 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.035 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.035 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0417 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0417 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.04 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.04 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0487 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0487 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0487 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0352 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0352 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0352 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0352 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0352 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0352 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773480 G23-075-TAP 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0372 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773481 GEN-2023-075 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0372 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0372 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-149 | 773501 GEN-2023-076 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0372 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0355 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0355 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0355 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0355 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0355 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0355 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0425 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0425 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0307 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773480 G23-075-TAP 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0311 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773481 GEN-2023-075 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0311 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0311 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-157 | 773501 GEN-2023-076 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0311 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0301 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0301 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0301 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0301 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0301 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0301 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0371 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-163 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0371 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0394 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0394 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0394 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0394 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0324 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0394 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0394 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-169 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0394 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0335 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0335 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0335 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0335 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0405 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0405 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0405 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0405 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0335 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0335 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0405 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0405 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-171 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0405 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0711 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0711 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0711 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0711 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.078 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.078 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.078 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.078 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0643 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0711 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0711 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.078 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.078 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-186 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.078 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0469 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0469 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0469 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0469 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0469 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0469 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0779 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0779 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0779 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0779 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0779 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-191 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0779 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0435 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0435 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0435 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0435 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0435 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0435 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9823 | 0.9366 | 0.0457 | 0.9597 | 0.95 | 1.05 | 0.0534 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0534 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0534 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.0534 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.0534 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.0534 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0879 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0879 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0879 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0879 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0879 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-194 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0879 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1095 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1095 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1095 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.1095 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9823 | 0.9366 | 0.0457 | 0.9597 | 0.95 | 1.05 | 0.1204 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.1204 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.1204 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.1204 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1162 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1162 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1162 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.1162 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1232 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1232 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1232 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.1232 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.1095 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.1095 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.1162 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.1162 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.1204 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.1204 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.1232 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.1232 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.1232 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.6414 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.6414 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.6414 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.6414 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.6414 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.6414 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773480 G23-075-TAP 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0319 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773481 GEN-2023-075 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0319 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0319 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-200 | 773501 GEN-2023-076 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0319 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0396 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0396 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0396 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0396 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0463 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0463 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0463 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0463 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0396 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0396 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0463 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0463 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0533 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-219 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0533 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0394 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0394 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0394 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0394 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0461 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0461 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0461 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0461 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0531 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0531 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0531 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0531 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0394 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0394 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0461 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0461 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0531 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0531 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-220 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0531 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9881 | 0.9355 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0395 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0395 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0395 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9881 | 0.9356 | 0.0525 | 0.9597 | 0.95 | 1.05 | 0.0395 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0462 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0462 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0462 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9884 | 0.9378 | 0.0506 | 0.9597 | 0.95 | 1.05 | 0.0462 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0395 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9876 | 0.9385 | 0.0491 | 0.9619 | 0.95 | 1.05 | 0.0395 | P12:345:OKGE:BKRBKR357_1::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0462 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9879 | 0.9407 | 0.0472 | 0.9619 | 0.95 | 1.05 | 0.0462 | P12:345:OKGE:BKRBKR357_2::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0532 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-221 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0532 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0398 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0398 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0398 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.0398 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0398 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.0398 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0685 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0685 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0685 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.0685 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0685 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-226 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.0685 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.036 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.036 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.036 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9875 | 0.9315 | 0.056 | 0.9597 | 0.95 | 1.05 | 0.036 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.036 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9871 | 0.9346 | 0.0525 | 0.9619 | 0.95 | 1.05 | 0.036 | P42:345:OKGE:SB_SOER7383::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9882 | 0.9356 | 0.0526 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9823 | 0.9366 | 0.0457 | 0.9597 | 0.95 | 1.05 | 0.2531 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.2531 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.2531 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9823 | 0.9367 | 0.0456 | 0.9597 | 0.95 | 1.05 | 0.2531 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9883 | 0.9368 | 0.0515 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9883 | 0.9369 | 0.0514 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9886 | 0.9369 | 0.0517 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9886 | 0.9379 | 0.0507 | 0.9597 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0353 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0353 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0353 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9887 | 0.9382 | 0.0505 | 0.9597 | 0.95 | 1.05 | 0.0353 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9877 | 0.9385 | 0.0492 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7313::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9879 | 0.9398 | 0.0481 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_RARD7311::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9882 | 0.9398 | 0.0484 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7319::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9881 | 0.9398 | 0.0483 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7308::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.2531 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.982 | 0.9408 | 0.0412 | 0.9619 | 0.95 | 1.05 | 0.2531 | P12:345:WERE:N345-AECI-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9881 | 0.9408 | 0.0473 | 0.9619 | 0.95 | 1.05 | 0.0353 | P42:345:OKGE:SB_OPKY7388::::
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0353 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9882 | 0.9411 | 0.0471 | 0.9619 | 0.95 | 1.05 | 0.0353 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.1378 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.1378 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.1378 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9894 | 0.9434 | 0.046 | 0.9597 | 0.95 | 1.05 | 0.1378 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765100 GEN-2020-052 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.1378 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 765110 G20-052-TAP 345 | 0.9889 | 0.9457 | 0.0432 | 0.9619 | 0.95 | 1.05 | 0.1378 | P12:345:WERE:LATH-ROSE-345:::EHV:
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773480 G23-075-TAP 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0551 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773481 GEN-2023-075 345 | 0.9898 | 0.9494 | 0.0404 | 0.9597 | 0.95 | 1.05 | 0.0551 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773488 G23-075XFMRH 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0551 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 03ALL | 2 | 27WP | GEN-2023-231 | 773501 GEN-2023-076 345 | 0.9898 | 0.9495 | 0.0403 | 0.9597 | 0.95 | 1.05 | 0.0551 | 300740 7SPORTSMAN 345 910800 GI108_POI 345 1
Voltage | 01ALL | 2 | 27SP | GEN-2023-031 | WAYSIDE4 | 1.0318 | 0.795 | 0.2368 | - | 0.9 | 1.05 | 0.03219 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-066 | WAYSIDE4 | 1.0318 | 0.795 | 0.2368 | - | 0.9 | 1.05 | 0.05852 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | WAYSIDE4 | 1.0318 | 0.795 | 0.2368 | - | 0.9 | 1.05 | 0.12242 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-097 | WAYSIDE4 | 1.0318 | 0.795 | 0.2368 | - | 0.9 | 1.05 | 0.03746 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-098 | WAYSIDE4 | 1.0318 | 0.795 | 0.2368 | - | 0.9 | 1.05 | 0.0866 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-130 | WAYSIDE4 | 1.0318 | 0.795 | 0.2368 | - | 0.9 | 1.05 | 0.04266 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-160 | WAYSIDE4 | 1.0318 | 0.795 | 0.2368 | - | 0.9 | 1.05 | 0.05277 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-198 | WAYSIDE4 | 1.0318 | 0.795 | 0.2368 | - | 0.9 | 1.05 | 0.03946 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | FAITH 7 | 1.0219 | 0.8355 | 0.1864 | - | 0.9 | 1.05 | 0.05498 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-098 | FAITH 7 | 1.0219 | 0.8355 | 0.1864 | - | 0.9 | 1.05 | 0.03045 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | ELKCRK 7 | 1.0162 | 0.781 | 0.2352 | - | 0.9 | 1.05 | 0.39679 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | ELSWRTH7 | 1.0203 | 0.789 | 0.2313 | - | 0.9 | 1.05 | 0.09161 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-066 | MARTIN 7 | 1.0047 | 0.8435 | 0.1612 | - | 0.9 | 1.05 | 0.03262 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | MAURINE7 | 1.0224 | 0.8397 | 0.1827 | - | 0.9 | 1.05 | 0.60321 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | NEWELL 7 | 1.0068 | 0.803 | 0.2038 | - | 0.9 | 1.05 | 0.39679 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-031 | NUNDRWD4 | 1.0283 | 0.8014 | 0.2269 | - | 0.9 | 1.05 | 0.03775 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-054 | NUNDRWD4 | 1.0283 | 0.8014 | 0.2269 | - | 0.9 | 1.05 | 0.03073 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-097 | NUNDRWD4 | 1.0283 | 0.8014 | 0.2269 | - | 0.9 | 1.05 | 0.05437 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-098 | NUNDRWD4 | 1.0283 | 0.8014 | 0.2269 | - | 0.9 | 1.05 | 0.20171 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-144 | NUNDRWD4 | 1.0283 | 0.8014 | 0.2269 | - | 0.9 | 1.05 | 0.03009 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-160 | NUNDRWD4 | 1.0283 | 0.8014 | 0.2269 | - | 0.9 | 1.05 | 0.09882 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-198 | NUNDRWD4 | 1.0283 | 0.8014 | 0.2269 | - | 0.9 | 1.05 | 0.05878 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | NUNDRWD7 | 1.026 | 0.8023 | 0.2237 | - | 0.9 | 1.05 | 0.15026 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | PHILIP 7 | 1.0252 | 0.8848 | 0.1404 | - | 0.9 | 1.05 | 0.04889 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | SULPHUR | 1.0042 | 0.8466 | 0.1576 | - | 0.9 | 1.05 | 1 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-067 | WALL 7 | 1.0229 | 0.8401 | 0.1828 | - | 0.9 | 1.05 | 0.04889 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-031 | MAURINE4 | 1.0369 | 0.8463 | 0.1906 | - | 0.9 | 1.05 | 0.04686 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-054 | MAURINE4 | 1.0369 | 0.8463 | 0.1906 | - | 0.9 | 1.05 | 0.03507 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-097 | MAURINE4 | 1.0369 | 0.8463 | 0.1906 | - | 0.9 | 1.05 | 0.07023 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-098 | MAURINE4 | 1.0369 | 0.8463 | 0.1906 | - | 0.9 | 1.05 | 0.7555 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-114 | MAURINE4 | 1.0369 | 0.8463 | 0.1906 | - | 0.9 | 1.05 | 0.03561 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-144 | MAURINE4 | 1.0369 | 0.8463 | 0.1906 | - | 0.9 | 1.05 | 0.03743 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-160 | MAURINE4 | 1.0369 | 0.8463 | 0.1906 | - | 0.9 | 1.05 | 0.23841 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-198 | MAURINE4 | 1.0369 | 0.8463 | 0.1906 | - | 0.9 | 1.05 | 0.09323 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-031 | G22-066-PROX | 1.0363 | 0.8501 | 0.1862 | - | 0.9 | 1.05 | 0.04686 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-054 | G22-066-PROX | 1.0363 | 0.8501 | 0.1862 | - | 0.9 | 1.05 | 0.03507 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-097 | G22-066-PROX | 1.0363 | 0.8501 | 0.1862 | - | 0.9 | 1.05 | 0.07023 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-098 | G22-066-PROX | 1.0363 | 0.8501 | 0.1862 | - | 0.9 | 1.05 | 0.7555 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-114 | G22-066-PROX | 1.0363 | 0.8501 | 0.1862 | - | 0.9 | 1.05 | 0.03561 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-144 | G22-066-PROX | 1.0363 | 0.8501 | 0.1862 | - | 0.9 | 1.05 | 0.03743 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-160 | G22-066-PROX | 1.0363 | 0.8501 | 0.1862 | - | 0.9 | 1.05 | 0.23841 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-198 | G22-066-PROX | 1.0363 | 0.8501 | 0.1862 | - | 0.9 | 1.05 | 0.09323 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-098 | G23-098-TAP | 1.0363 | 0.8832 | 0.1531 | - | 0.9 | 1.05 | 1 | System Intact
Voltage | 01ALL | 2 | 27SP | GEN-2023-098 | G23-098-TAP | 1.0331 | 0.8832 | 0.1499 | - | 0.9 | 1.05 | 1 | System Intact
Voltage | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 04NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 05NR | 2 | 27L | N/A | None | [7 empty] | None

## Short Circuit Ratio
Study Request | Current Cluster | Cluster Group | Transmission Owner | Capacity | Service Type | Generation Type | Point of Interconnection | GEN Bus # | Gen ID | POI Bus # | DIS231TC00ALL-27SP.sav |  | DIS231TC01ALL-27L.sav |  | DIS231TC01ALL-27SP.sav |  | DIS231TC02ALL-27L.sav |  | DIS231TC02ALL-27SP.sav |  | DIS231TC03ALL-27L.sav |  | DIS231TC03ALL-27SP.sav |  | DIS231TC04ALL-27L.sav |  | DIS231TC04ALL-27SP.sav |  | DIS231TC05ALL-27L.sav |  | DIS231TC05ALL-27SP.sav |  | DIS231TCWECCALL-23L.sav |  | DIS231TCWECCALL-23SP.sav
[11 empty] | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio
ASGI-2023-001 | DIS-23-1 | 05 SOUTHWEST | SPS | 20 | ER/NR | Solar | CHVRN_EDDYS3115.00 | 775724 | 1 | 528252 | 1609.12 | 201.14 | 1437.23 | N/A | 1555.68 | 194.46 | 1437.23 | N/A | 1555.68 | 194.46 | 1437.42 | N/A | 1555.74 | 280.82 | 1438.34 | N/A | 1556 | 194.5 | 1453.29 | N/A | 1575.56 | 78.78 | N/A | N/A | N/A | N/A
GEN-2023-001 | DIS-23-1 | 05 SOUTHWEST | SPS | 230 | ER/NR | Solar | T14 Circuit 115 V Line | 772004 | 1 | 762442 | 4806.47 | 52.24 | 3469.03 | N/A | 4476.35 | 48.66 | 3469.04 | N/A | 4476.35 | 48.66 | 3469.57 | N/A | 4476.51 | 70.26 | 3472.19 | N/A | 4477.16 | 48.66 | 3511.68 | N/A | 4619.43 | 20.08 | N/A | N/A | N/A | N/A
GEN-2023-003 | DIS-23-1 | 04 SOUTHEAST | WFEC & SWPA | 200.6 | ER/NR | Wind | Greasy Creek 138kV Switchyard | 772044 | 1 | 505595 | 1705.25 | 42.5 | 1615.32 | 13.42 | 1670.39 | 41.63 | 1615.32 | 13.42 | 1670.39 | 41.63 | 1615.52 | 13.42 | 1670.5 | 60.12 | 1630.43 | 8.13 | 1687.88 | 8.41 | 1615.83 | 13.42 | 1670.68 | 41.64 | N/A | N/A | N/A | N/A
GEN-2023-005 | DIS-23-1 | 05 SOUTHWEST | SPS | 256 | ER/NR | Solar | Plant X 230kV Substation | 772084 | 1 | 525481 | 11903.14 | 232.48 | 9318.32 | N/A | 11054.92 | 215.92 | 9318.46 | N/A | 11054.99 | 215.92 | 9330.69 | N/A | 11064.55 | 312.04 | 9357.79 | N/A | 11073.79 | 216.28 | 9708.33 | N/A | 11817.82 | 92.33 | N/A | N/A | N/A | N/A
GEN-2023-005 | DIS-23-1 | 05 SOUTHWEST | SPS | 256 | ER/NR | Solar | Plant X 230kV Substation | 772087 | 1 | 525481 | 11903.14 | 232.48 | 9318.32 | N/A | 11054.92 | 215.92 | 9318.46 | N/A | 11054.99 | 215.92 | 9330.69 | N/A | 11064.55 | 312.04 | 9357.79 | N/A | 11073.79 | 216.28 | 9708.33 | N/A | 11817.82 | 92.33 | N/A | N/A | N/A | N/A
GEN-2023-006 | DIS-23-1 | 03 CENTRAL | NEET | 202 | ER | Wind | Wolf Creek- Blackberry 345 kV Line Break | 772104 | 1 | 772100 | 7473.1 | 369.96 | 6614.69 | 109.15 | 7017.88 | 347.42 | 6614.99 | 109.16 | 7017.92 | 347.42 | 6651.2 | 65.85 | 7437 | 73.63 | 6661.45 | 109.92 | 7050.52 | 349.04 | 6616.33 | 109.18 | 7018.29 | 347.44 | N/A | N/A | N/A | N/A
GEN-2023-006 | DIS-23-1 | 03 CENTRAL | NEET | 202 | ER | Wind | Wolf Creek- Blackberry 345 kV Line Break | 772107 | 1 | 772100 | 7473.1 | 369.96 | 6614.69 | 109.15 | 7017.88 | 347.42 | 6614.99 | 109.16 | 7017.92 | 347.42 | 6651.2 | 65.85 | 7437 | 73.63 | 6661.45 | 109.92 | 7050.52 | 349.04 | 6616.33 | 109.18 | 7018.29 | 347.44 | N/A | N/A | N/A | N/A
GEN-2023-008 | DIS-23-1 | 05 SOUTHWEST | SPS | 75 | ER/NR | Solar | Tuco - Carlisle 230 kV line | 772144 | 1 | 768620 | 9301.74 | 310.06 | 7190.1 | N/A | 8771.3 | 292.38 | 7190.19 | N/A | 8771.33 | 292.38 | 7198.33 | N/A | 8776.33 | 422.41 | 7246.54 | N/A | 8803.8 | 293.46 | 7369.17 | N/A | 9146.46 | 121.95 | N/A | N/A | N/A | N/A
GEN-2023-009 | DIS-23-1 | 04 SOUTHEAST | WFEC | 250 | ER/NR | Storage | Hugo 138 kV Substation | 772164 | 1 | 520948 | 6070.19 | 47.83 | 3499.72 | N/A | 5426.53 | N/A | 3499.72 | N/A | 5426.53 | N/A | 3500.38 | N/A | 5428.2 | N/A | 3536.33 | N/A | 5981.61 | 47.13 | 3504.73 | N/A | 5434.34 | N/A | N/A | N/A | N/A | N/A
GEN-2023-009 | DIS-23-1 | 04 SOUTHEAST | WFEC | 250 | ER/NR | Storage | Hugo 138 kV Substation | 772167 | 1 | 520948 | 6070.19 | 49.32 | 3499.72 | N/A | 5426.53 | N/A | 3499.72 | N/A | 5426.53 | N/A | 3500.38 | N/A | 5428.2 | N/A | 3536.33 | N/A | 5981.61 | 48.6 | 3504.73 | N/A | 5434.34 | N/A | N/A | N/A | N/A | N/A
GEN-2023-010 | DIS-23-1 | 05 SOUTHWEST | SPS | 280 | ER/NR | Wind | Moore Co 230 kV Substation | 772184 | 1 | 523309 | 3105.34 | 110.91 | 2927.07 | 34.85 | 3050.29 | 108.94 | 2927.15 | 34.85 | 3050.35 | 108.94 | 2933.62 | 34.92 | 3058.46 | 157.72 | 2935.45 | 34.95 | 3056.56 | 109.16 | 2969.92 | 21.21 | 3091.3 | 22.08 | N/A | N/A | N/A | N/A
GEN-2023-010 | DIS-23-1 | 05 SOUTHWEST | SPS | 280 | ER/NR | Wind | Moore Co 230 kV Substation | 772187 | 1 | 523309 | 3105.34 | 110.91 | 2927.07 | 34.85 | 3050.29 | 108.94 | 2927.15 | 34.85 | 3050.35 | 108.94 | 2933.62 | 34.92 | 3058.46 | 157.72 | 2935.45 | 34.95 | 3056.56 | 109.16 | 2969.92 | 21.21 | 3091.3 | 22.08 | N/A | N/A | N/A | N/A
GEN-2023-011 | DIS-23-1 | 02 NEBRASKA | NPPD | 190 | ER/NR | Wind | Harbine 115 kV Substation | 772204 | 1 | 640208 | 2219.43 | 58.41 | 1686.87 | 14.8 | 2028.27 | 53.38 | 1767.01 | 9.3 | 2114.19 | 11.13 | 1690.58 | 14.83 | 2034.33 | 77.3 | 1686.68 | 14.8 | 2028.24 | 53.37 | 1686.65 | 14.8 | 2028.24 | 53.37 | N/A | N/A | N/A | N/A
GEN-2023-012 | DIS-23-1 | 01 NORTH | EREC | 98.6 | ER/NR | Wind | Kingsbury County 115kV Substation | 772224 | 1 | 655554 | 838.08 | 82.16 | 812.61 | 15.93 | 838.03 | 16.43 | 809.34 | 26.45 | 831.61 | 81.53 | 809.17 | 26.44 | 831.56 | 117.72 | 809.16 | 26.44 | 831.55 | 81.52 | 809.16 | 26.44 | 831.55 | 81.52 | N/A | N/A | N/A | N/A
GEN-2023-012 | DIS-23-1 | 01 NORTH | EREC | 98.6 | ER/NR | Wind | Kingsbury County 115kV Substation | 772227 | 1 | 655554 | 838.08 | 88.03 | 812.61 | 17.07 | 838.03 | 17.61 | 809.34 | 28.34 | 831.61 | 87.35 | 809.17 | 28.33 | 831.56 | 126.13 | 809.16 | 28.33 | 831.55 | 87.35 | 809.16 | 28.33 | 831.55 | 87.35 | N/A | N/A | N/A | N/A
GEN-2023-013 | DIS-23-1 | 01 NORTH | BEPC | 200 | ER/NR | Wind | Leland Olds to Groton 345 kV Line | 772244 | 1 | 772240 | 3600.46 | 90.01 | 3287.74 | 16.44 | 3599.45 | 18 | 3143.7 | 26.2 | 3401.17 | 85.03 | 3142.73 | 26.19 | 3400.85 | 122.77 | 3142.69 | 26.19 | 3400.84 | 85.02 | 3142.69 | 26.19 | 3400.84 | 85.02 | N/A | N/A | N/A | N/A
GEN-2023-014 | DIS-23-1 | 01 NORTH | BEPC | 200 | ER/NR | Wind | Leland Olds to Groton 345 kV Line | 772264 | 1 | 772240 | 3600.46 | 90.01 | 3287.74 | 16.44 | 3599.45 | 18 | 3143.7 | 26.2 | 3401.17 | 85.03 | 3142.73 | 26.19 | 3400.85 | 122.77 | 3142.69 | 26.19 | 3400.84 | 85.02 | 3142.69 | 26.19 | 3400.84 | 85.02 | N/A | N/A | N/A | N/A
GEN-2023-015 | DIS-23-1 | 03 CENTRAL | SPS | 330 | ER/NR | Solar | Finney-Carpenter 345 KV line | 772284 | 1 | 772280 | 9505.67 | 72.01 | 8183.74 | N/A | 9019.28 | 68.33 | 8187.07 | N/A | 9023.88 | 68.36 | 8353.45 | N/A | 9322.62 | 28.25 | 8254 | N/A | 9086.85 | 68.84 | 8327.24 | N/A | 9141.65 | 69.25 | N/A | N/A | N/A | N/A
GEN-2023-016 | DIS-23-1 | 04 SOUTHEAST | SWPA | 130 | ER/NR | Solar | Tupelo-Brown 138 kV Line | 772304 | 1 | 772300 | 1982.12 | 38.12 | 1589.56 | N/A | 1856.17 | 35.7 | 1589.56 | N/A | 1856.17 | 35.7 | 1589.8 | N/A | 1856.72 | 51.56 | 1602.94 | N/A | 1969.53 | 15.15 | 1591.06 | N/A | 1857.86 | 35.73 | N/A | N/A | N/A | N/A
GEN-2023-017 | DIS-23-1 | 03 CENTRAL | EDE | 150 | ER/NR | Storage | Carl Junction Northeast 161 kV Substation | 772324 | 1 | 547485 | 3917.15 | 52.23 | 3071.14 | N/A | 3458.59 | N/A | 3071.17 | N/A | 3458.59 | N/A | 3074.43 | N/A | 3807.72 | 50.77 | 3083.8 | N/A | 3467.22 | N/A | 3071.27 | N/A | 3458.6 | N/A | N/A | N/A | N/A | N/A
GEN-2023-017 | DIS-23-1 | 03 CENTRAL | EDE | 150 | ER/NR | Storage | Carl Junction Northeast 161 kV Substation | 772327 | 1 | 547485 | 3917.15 | 52.23 | 3071.14 | N/A | 3458.59 | N/A | 3071.17 | N/A | 3458.59 | N/A | 3074.43 | N/A | 3807.72 | 50.77 | 3083.8 | N/A | 3467.22 | N/A | 3071.27 | N/A | 3458.6 | N/A | N/A | N/A | N/A | N/A
GEN-2023-019 | DIS-23-1 | 04 SOUTHEAST | WFEC | 200 | ER/NR | Storage | Cherry Road 138 kV Substation | 772364 | 1 | 521129 | 1764.79 | 17.65 | 1445.2 | N/A | 1506.19 | N/A | 1445.2 | N/A | 1506.19 | N/A | 1445.5 | N/A | 1506.32 | N/A | 1478.14 | N/A | 1755.12 | 17.55 | 1447.08 | N/A | 1508.46 | N/A | N/A | N/A | N/A | N/A
GEN-2023-019 | DIS-23-1 | 04 SOUTHEAST | WFEC | 200 | ER/NR | Storage | Cherry Road 138 kV Substation | 772367 | 1 | 521129 | 1764.79 | 17.65 | 1445.2 | N/A | 1506.19 | N/A | 1445.2 | N/A | 1506.19 | N/A | 1445.5 | N/A | 1506.32 | N/A | 1478.14 | N/A | 1755.12 | 17.55 | 1447.08 | N/A | 1508.46 | N/A | N/A | N/A | N/A | N/A
GEN-2023-020 | DIS-23-1 | 04 SOUTHEAST | WFEC | 220 | ER/NR | Solar | Russett-S Brown 138 kV | 772384 | 1 | 772380 | 2835.43 | 32.22 | 2202.63 | N/A | 2528.35 | 28.73 | 2202.64 | N/A | 2528.35 | 28.73 | 2203.21 | N/A | 2532.17 | 41.55 | 2243.18 | N/A | 2773.04 | 12.6 | 2207.6 | N/A | 2537.3 | 28.83 | N/A | N/A | N/A | N/A
GEN-2023-021 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Storage | Blue Mills 161kV Substation | 772404 | 1 | 543004 | 5350.06 | 53.5 | 3915.03 | N/A | 4675.51 | N/A | 3917.26 | N/A | 4676.37 | N/A | 3964.68 | N/A | 5240.07 | 52.4 | 3916.44 | N/A | 4675.6 | N/A | 3915.02 | N/A | 4675.51 | N/A | N/A | N/A | N/A | N/A
GEN-2023-021 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Storage | Blue Mills 161kV Substation | 772407 | 1 | 543004 | 5350.06 | 53.5 | 3915.03 | N/A | 4675.51 | N/A | 3917.26 | N/A | 4676.37 | N/A | 3964.68 | N/A | 5240.07 | 52.4 | 3916.44 | N/A | 4675.6 | N/A | 3915.02 | N/A | 4675.51 | N/A | N/A | N/A | N/A | N/A
GEN-2023-022 | DIS-23-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Wind | Canadian River 345 kV Substation | 772424 | 1 | 515422 | 8980.59 | 179.61 | 7503.98 | 50.03 | 8574.23 | 171.48 | 7504.02 | 50.03 | 8574.24 | 171.48 | 7509.32 | 50.06 | 8581.22 | 247.81 | 7751.4 | 31.01 | 8919.55 | 35.68 | 7521.96 | 50.15 | 8592.27 | 171.85 | N/A | N/A | N/A | N/A
GEN-2023-023 | DIS-23-1 | 03 CENTRAL | KACY | 200 | ER/NR | Storage | Center City 161 kV Substation | 772444 | 1 | 546659 | 4011.71 | 40.12 | 3146.28 | N/A | 3641.34 | N/A | 3147.65 | N/A | 3641.75 | N/A | 3178.15 | N/A | 3997.28 | 39.97 | 3147.5 | N/A | 3641.43 | N/A | 3146.34 | N/A | 3641.35 | N/A | N/A | N/A | N/A | N/A
GEN-2023-023 | DIS-23-1 | 03 CENTRAL | KACY | 200 | ER/NR | Storage | Center City 161 kV Substation | 772447 | 1 | 546659 | 4011.71 | 40.12 | 3146.28 | N/A | 3641.34 | N/A | 3147.65 | N/A | 3641.75 | N/A | 3178.15 | N/A | 3997.28 | 39.97 | 3147.5 | N/A | 3641.43 | N/A | 3146.34 | N/A | 3641.35 | N/A | N/A | N/A | N/A | N/A
GEN-2023-024 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Storage | Rose Hill 138 kV Substation | 772464 | 1 | 533062 | 8698.23 | 43.49 | 7265.54 | N/A | 7935.83 | N/A | 7266.27 | N/A | 7936.09 | N/A | 7476 | N/A | 8596.79 | 42.98 | 7388.17 | N/A | 8024.02 | N/A | 7281.6 | N/A | 7944.05 | N/A | N/A | N/A | N/A | N/A
GEN-2023-025 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Storage | Franklin - Jayhawk 161 kV Line | 772484 | 1 | 772480 | 2427.35 | 12.14 | 2092.6 | N/A | 2153.63 | N/A | 2092.62 | N/A | 2153.63 | N/A | 2094.3 | N/A | 2422.39 | 12.11 | 2095.35 | N/A | 2155.04 | N/A | 2092.65 | N/A | 2153.63 | N/A | N/A | N/A | N/A | N/A
GEN-2023-026 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Storage | LaCygne - Wolf Creek 345 kV Line | 772504 | 1 | 772500 | 10094.23 | 33.65 | 8180.53 | N/A | 9192.22 | N/A | 8181.7 | N/A | 9192.39 | N/A | 8253.14 | N/A | 10069.58 | 33.57 | 8216.53 | N/A | 9209.28 | N/A | 8184.54 | N/A | 9193.64 | N/A | N/A | N/A | N/A | N/A
GEN-2023-027 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Solar | Bird Hollow (Langley) - Pryor Junction 138 kV Line | 772524 | 1 | 772520 | 1877.31 | 43.8 | 1430.88 | N/A | 1647.52 | 24.58 | 1430.88 | N/A | 1647.52 | 24.58 | 1431.23 | N/A | 1650.51 | 35.55 | 1433.53 | N/A | 1873.81 | 24.98 | 1430.94 | N/A | 1647.52 | 24.58 | N/A | N/A | N/A | N/A
GEN-2023-027 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Storage | Bird Hollow (Langley) - Pryor Junction 138 kV Line | 772527 | 1 | 772520 | 1877.31 | 17.52 | 1430.88 | N/A | 1647.52 | N/A | 1430.88 | N/A | 1647.52 | N/A | 1431.23 | N/A | 1650.51 | N/A | 1433.53 | N/A | 1873.81 | 24.98 | 1430.94 | N/A | 1647.52 | N/A | N/A | N/A | N/A | N/A
GEN-2023-028 | DIS-23-1 | 04 SOUTHEAST | GRDA | 230 | ER/NR | Solar | Dry Gulch - Pensacola 161 kV Line | 772544 | 1 | 772540 | 4365.16 | 66.43 | 3527.83 | N/A | 4042.06 | 40.2 | 3527.84 | N/A | 4042.06 | 40.2 | 3529.9 | N/A | 4052.19 | 58.19 | 3539.54 | N/A | 4349.55 | 37.82 | 3528.12 | N/A | 4042.1 | 40.2 | N/A | N/A | N/A | N/A
GEN-2023-028 | DIS-23-1 | 04 SOUTHEAST | GRDA | 230 | ER/NR | Storage | Dry Gulch - Pensacola 161 kV Line | 772547 | 1 | 772540 | 4365.16 | 26.57 | 3527.83 | N/A | 4042.06 | N/A | 3527.84 | N/A | 4042.06 | N/A | 3529.9 | N/A | 4052.19 | N/A | 3539.54 | N/A | 4349.55 | 37.82 | 3528.12 | N/A | 4042.1 | N/A | N/A | N/A | N/A | N/A
GEN-2023-029 | DIS-23-1 | 04 SOUTHEAST | AEP | 50 | ER/NR | Solar | Adair - Pryor 69 kV Line | 772564 | 1 | 772560 | 791.73 | 39.59 | 711.38 | N/A | 777.69 | 38.88 | 711.38 | N/A | 777.69 | 38.88 | 711.48 | N/A | 778.32 | 56.19 | 712.04 | N/A | 791.07 | 15.82 | 711.39 | N/A | 777.7 | 38.89 | N/A | N/A | N/A | N/A
GEN-2023-030 | DIS-23-1 | 04 SOUTHEAST | AEP | 25 | ER/NR | Solar | Tap between 345 kV SW Shreveport to Dolet Hills Substations | 772584 | 1 | 769140 | 7167.15 | 716.71 | 6231.7 | N/A | 6959.42 | 695.94 | 6231.7 | N/A | 6959.42 | 695.94 | 6231.75 | N/A | 6959.43 | 1004.83 | 6233.99 | N/A | 7144.02 | 285.76 | 6231.99 | N/A | 6959.47 | 695.95 | N/A | N/A | N/A | N/A
GEN-2023-031 | DIS-23-1 | 01 NORTH | WAPA | 200 | ER/NR | Solar | Washburn 230 kV Substation | 772604 | 1 | 652456 | 4314.71 | 53.93 | 3862.37 | N/A | 4308.42 | 21.54 | 3727.38 | N/A | 4186.35 | 52.33 | 3726.79 | N/A | 4186.12 | 75.55 | 3726.76 | N/A | 4186.11 | 52.33 | 3726.76 | N/A | 4186.11 | 52.33 | N/A | N/A | N/A | N/A
GEN-2023-032 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Solar | Odessa and Lexington 161 kV Line | 772624 | 1 | 772620 | 2428.07 | 30.35 | 2019.18 | N/A | 2362.1 | 29.53 | 2019.64 | N/A | 2362.24 | 29.53 | 2031.31 | N/A | 2397.25 | 11.99 | 2019.59 | N/A | 2362.13 | 29.53 | 2019.19 | N/A | 2362.1 | 29.53 | N/A | N/A | N/A | N/A
GEN-2023-033 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Storage | Liberty South 161 kV Substation | 772644 | 1 | 541248 | 5947.05 | 59.47 | 4496.39 | N/A | 5489.48 | N/A | 4499.55 | N/A | 5490.81 | N/A | 4563.52 | N/A | 5872.24 | 58.72 | 4498.19 | N/A | 5489.58 | N/A | 4496.37 | N/A | 5489.47 | N/A | N/A | N/A | N/A | N/A
GEN-2023-033 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Storage | Liberty South 161 kV Substation | 772647 | 1 | 541248 | 5947.05 | 59.47 | 4496.39 | N/A | 5489.48 | N/A | 4499.55 | N/A | 5490.81 | N/A | 4563.52 | N/A | 5872.24 | 58.72 | 4498.19 | N/A | 5489.58 | N/A | 4496.37 | N/A | 5489.47 | N/A | N/A | N/A | N/A | N/A
GEN-2023-034 | DIS-23-1 | 03 CENTRAL | Evergy | 130 | ER/NR | Solar | Clear Water - Waco 138 kV line | 772664 | 1 | 772660 | 5056.68 | 97.24 | 4261.25 | N/A | 4744.4 | 91.24 | 4261.53 | N/A | 4744.51 | 91.24 | 4341.6 | N/A | 5018.77 | 38.61 | 4304.76 | N/A | 4774.69 | 91.82 | 4268.24 | N/A | 4747.97 | 91.31 | N/A | N/A | N/A | N/A
GEN-2023-035 | DIS-23-1 | 04 SOUTHEAST | WFEC | 200 | ER/NR | Solar | Cleveland - Amber Tap 138 kV Line | 772684 | 1 | 772680 | 2219.63 | 27.75 | 1908.32 | N/A | 2184.99 | 27.31 | 1908.32 | N/A | 2184.99 | 27.31 | 1909.01 | N/A | 2185.31 | 39.44 | 1926.2 | N/A | 2203.56 | 11.02 | 1911.16 | N/A | 2187.82 | 27.35 | N/A | N/A | N/A | N/A
GEN-2023-036 | DIS-23-1 | 03 CENTRAL | INDN | 200 | ER/NR | Storage | Eckles Road 161 kV Substation | 772704 | 1 | 548808 | 7823.58 | 39.12 | 5546.69 | N/A | 7053.73 | N/A | 5551.13 | N/A | 7055.86 | N/A | 5647.49 | N/A | 7688.25 | 38.44 | 5549.5 | N/A | 7053.94 | N/A | 5546.67 | N/A | 7053.72 | N/A | N/A | N/A | N/A | N/A
GEN-2023-037 | DIS-23-1 | 03 CENTRAL | KACY | 200 | ER/NR | Storage | Quindaro Bluffs 161 kV Substation | 772724 | 1 | 546652 | 4433.48 | 44.33 | 3370.29 | N/A | 4012.44 | N/A | 3371.87 | N/A | 4012.93 | N/A | 3406.74 | N/A | 4416.17 | 44.16 | 3371.68 | N/A | 4012.54 | N/A | 3370.36 | N/A | 4012.44 | N/A | N/A | N/A | N/A | N/A
GEN-2023-037 | DIS-23-1 | 03 CENTRAL | KACY | 200 | ER/NR | Storage | Quindaro Bluffs 161 kV Substation | 772727 | 1 | 546652 | 4433.48 | 44.33 | 3370.29 | N/A | 4012.44 | N/A | 3371.87 | N/A | 4012.93 | N/A | 3406.74 | N/A | 4416.17 | 44.16 | 3371.68 | N/A | 4012.54 | N/A | 3370.36 | N/A | 4012.44 | N/A | N/A | N/A | N/A | N/A
GEN-2023-038 | DIS-23-1 | 04 SOUTHEAST | OGE | 200 | ER/NR | Solar | Lula 138 kV Substation | 772744 | 1 | 515192 | 2725.09 | 34.06 | 2166.47 | N/A | 2606.07 | 32.58 | 2166.47 | N/A | 2606.07 | 32.58 | 2166.89 | N/A | 2606.6 | 47.05 | 2190.49 | N/A | 2707.99 | 13.54 | 2168.72 | N/A | 2608.33 | 32.6 | N/A | N/A | N/A | N/A
GEN-2023-039 | DIS-23-1 | 03 CENTRAL | SPS | 250 | ER/NR | Wind | Carpenter 345 kV Substation | 772764 | 1 | 523823 | 14203.78 | 561.86 | 11471.25 | 151.26 | 12558.34 | 496.77 | 11474.63 | 151.3 | 12562.29 | 496.93 | 11773.12 | 93.14 | 13561.53 | 107.29 | 11661.72 | 153.77 | 12758.76 | 504.7 | 11920.26 | 157.18 | 12978.98 | 513.41 | N/A | N/A | N/A | N/A
GEN-2023-039 | DIS-23-1 | 03 CENTRAL | SPS | 250 | ER/NR | Wind | Carpenter 345 kV Substation | 772767 | 1 | 523823 | 14203.78 | 574.59 | 11471.25 | 154.68 | 12558.34 | 508.02 | 11474.63 | 154.73 | 12562.29 | 508.18 | 11773.12 | 95.25 | 13561.53 | 109.72 | 11661.72 | 157.25 | 12758.76 | 516.13 | 11920.26 | 160.74 | 12978.98 | 525.04 | N/A | N/A | N/A | N/A
GEN-2023-040 | DIS-23-1 | 02 NEBRASKA | NPPD | 105 | ER/NR | Solar | Carleton Junction 115 kV Substation | 772784 | 1 | 640105 | 1321.73 | 31.47 | 1035.28 | N/A | 1245.8 | 29.66 | 1073.35 | N/A | 1315.75 | 12.53 | 1036.99 | N/A | 1246.84 | 42.86 | 1035.15 | N/A | 1245.77 | 29.66 | 1035.14 | N/A | 1245.77 | 29.66 | N/A | N/A | N/A | N/A
GEN-2023-042 | DIS-23-1 | 03 CENTRAL | EDE | 200 | ER/NR | Solar | Noel Southwest 161 kV Substation | 772824 | 1 | 547496 | 3389.02 | 42.36 | 2832.82 | N/A | 3213.17 | 40.16 | 2832.83 | N/A | 3213.17 | 40.16 | 2834.29 | N/A | 3345.67 | 16.73 | 2843.29 | N/A | 3251.13 | 40.64 | 2832.96 | N/A | 3213.19 | 40.16 | N/A | N/A | N/A | N/A
GEN-2023-043 | DIS-23-1 | 03 CENTRAL | SUNC | 200 | ER/NR | Solar | Setab 345 kV Substation | 772844 | 1 | 531465 | 7600.38 | 95 | 6669.31 | N/A | 7335.7 | 91.7 | 6678.18 | N/A | 7352.63 | 91.91 | 6767.43 | N/A | 7542.26 | 37.71 | 6690.34 | N/A | 7353.24 | 91.92 | 6708.78 | N/A | 7365.19 | 92.06 | N/A | N/A | N/A | N/A
GEN-2023-044 | DIS-23-1 | 03 CENTRAL | SUNC | 200 | ER/NR | Solar | Setab 345 kV Substation | 772864 | 1 | 531465 | 7600.38 | 95 | 6669.31 | N/A | 7335.7 | 91.7 | 6678.18 | N/A | 7352.63 | 91.91 | 6767.43 | N/A | 7542.26 | 37.71 | 6690.34 | N/A | 7353.24 | 91.92 | 6708.78 | N/A | 7365.19 | 92.06 | N/A | N/A | N/A | N/A
GEN-2023-045 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Setab 345 kV Substation | 772884 | 1 | 531465 | 7600.38 | 300.65 | 6669.31 | 87.94 | 7335.7 | 290.18 | 6678.18 | 88.06 | 7352.63 | 290.85 | 6767.43 | 53.54 | 7542.26 | 59.67 | 6690.34 | 88.22 | 7353.24 | 290.87 | 6708.78 | 88.46 | 7365.19 | 291.34 | N/A | N/A | N/A | N/A
GEN-2023-045 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Setab 345 kV Substation | 772887 | 1 | 531465 | 7600.38 | 307.46 | 6669.31 | 89.93 | 7335.7 | 296.75 | 6678.18 | 90.05 | 7352.63 | 297.44 | 6767.43 | 54.75 | 7542.26 | 61.02 | 6690.34 | 90.21 | 7353.24 | 297.46 | 6708.78 | 90.46 | 7365.19 | 297.94 | N/A | N/A | N/A | N/A
GEN-2023-046 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Setab 345 kV Substation | 772904 | 1 | 531465 | 7600.38 | 300.65 | 6669.31 | 87.94 | 7335.7 | 290.18 | 6678.18 | 88.06 | 7352.63 | 290.85 | 6767.43 | 53.54 | 7542.26 | 59.67 | 6690.34 | 88.22 | 7353.24 | 290.87 | 6708.78 | 88.46 | 7365.19 | 291.34 | N/A | N/A | N/A | N/A
GEN-2023-046 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Setab 345 kV Substation | 772907 | 1 | 531465 | 7600.38 | 307.46 | 6669.31 | 89.93 | 7335.7 | 296.75 | 6678.18 | 90.05 | 7352.63 | 297.44 | 6767.43 | 54.75 | 7542.26 | 61.02 | 6690.34 | 90.21 | 7353.24 | 297.46 | 6708.78 | 90.46 | 7365.19 | 297.94 | N/A | N/A | N/A | N/A
GEN-2023-047 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Setab 345 kV Substation | 772924 | 1 | 531465 | 7600.38 | 300.65 | 6669.31 | 87.94 | 7335.7 | 290.18 | 6678.18 | 88.06 | 7352.63 | 290.85 | 6767.43 | 53.54 | 7542.26 | 59.67 | 6690.34 | 88.22 | 7353.24 | 290.87 | 6708.78 | 88.46 | 7365.19 | 291.34 | N/A | N/A | N/A | N/A
GEN-2023-047 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Setab 345 kV Substation | 772927 | 1 | 531465 | 7600.38 | 307.46 | 6669.31 | 89.93 | 7335.7 | 296.75 | 6678.18 | 90.05 | 7352.63 | 297.44 | 6767.43 | 54.75 | 7542.26 | 61.02 | 6690.34 | 90.21 | 7353.24 | 297.46 | 6708.78 | 90.46 | 7365.19 | 297.94 | N/A | N/A | N/A | N/A
GEN-2023-048 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Setab 345 kV Substation | 772944 | 1 | 531465 | 7600.38 | 300.65 | 6669.31 | 87.94 | 7335.7 | 290.18 | 6678.18 | 88.06 | 7352.63 | 290.85 | 6767.43 | 53.54 | 7542.26 | 59.67 | 6690.34 | 88.22 | 7353.24 | 290.87 | 6708.78 | 88.46 | 7365.19 | 291.34 | N/A | N/A | N/A | N/A
GEN-2023-048 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Setab 345 kV Substation | 772947 | 1 | 531465 | 7600.38 | 307.46 | 6669.31 | 89.93 | 7335.7 | 296.75 | 6678.18 | 90.05 | 7352.63 | 297.44 | 6767.43 | 54.75 | 7542.26 | 61.02 | 6690.34 | 90.21 | 7353.24 | 297.46 | 6708.78 | 90.46 | 7365.19 | 297.94 | N/A | N/A | N/A | N/A
GEN-2023-049 | DIS-23-1 | 04 SOUTHEAST | GRDA | 150 | ER/NR | Solar | Dry Gulch - Pensacola 161 kV Line | 772964 | 1 | 772960 | 4025.69 | 63.1 | 3309.57 | N/A | 3765.94 | 59.03 | 3309.59 | N/A | 3765.94 | 59.03 | 3311.46 | N/A | 3777.1 | 85.49 | 3319.79 | N/A | 4010.4 | 39.31 | 3309.82 | N/A | 3765.97 | 59.03 | N/A | N/A | N/A | N/A
GEN-2023-049 | DIS-23-1 | 04 SOUTHEAST | GRDA | 150 | ER/NR | Storage | Dry Gulch - Pensacola 161 kV Line | 772964 | 2 | 772960 | 4025.69 | 53.68 | 3309.57 | N/A | 3765.94 | N/A | 3309.59 | N/A | 3765.94 | N/A | 3311.46 | N/A | 3777.1 | N/A | 3319.79 | N/A | 4010.4 | 83.59 | 3309.82 | N/A | 3765.97 | N/A | N/A | N/A | N/A | N/A
GEN-2023-050 | DIS-23-1 | 03 CENTRAL | Evergy | 400 | ER/NR | Solar | Neosho 345 kV Substation | 772984 | 1 | 532793 | 13115.79 | 155.58 | 9733.06 | N/A | 11544.67 | 136.94 | 9733.92 | N/A | 11544.78 | 136.94 | 9969.07 | N/A | 12774.16 | 94.18 | 10063.69 | N/A | 11852.61 | 140.59 | 9737.53 | N/A | 11545.82 | 136.95 | N/A | N/A | N/A | N/A
GEN-2023-050 | DIS-23-1 | 03 CENTRAL | Evergy | 400 | ER/NR | Storage | Neosho 345 kV Substation | 772984 | 2 | 532793 | 13115.79 | 131.16 | 9733.06 | N/A | 11544.67 | N/A | 9733.92 | N/A | 11544.78 | N/A | 9969.07 | N/A | 12774.16 | 198.49 | 10063.69 | N/A | 11852.61 | N/A | 9737.53 | N/A | 11545.82 | N/A | N/A | N/A | N/A | N/A
GEN-2023-050 | DIS-23-1 | 03 CENTRAL | Evergy | 400 | ER/NR | Solar | Neosho 345 kV Substation | 772987 | 1 | 532793 | 13115.79 | 155.58 | 9733.06 | N/A | 11544.67 | 136.94 | 9733.92 | N/A | 11544.78 | 136.94 | 9969.07 | N/A | 12774.16 | 94.18 | 10063.69 | N/A | 11852.61 | 140.59 | 9737.53 | N/A | 11545.82 | 136.95 | N/A | N/A | N/A | N/A
GEN-2023-050 | DIS-23-1 | 03 CENTRAL | Evergy | 400 | ER/NR | Storage | Neosho 345 kV Substation | 772987 | 2 | 532793 | 13115.79 | 131.16 | 9733.06 | N/A | 11544.67 | N/A | 9733.92 | N/A | 11544.78 | N/A | 9969.07 | N/A | 12774.16 | 198.49 | 10063.69 | N/A | 11852.61 | N/A | 9737.53 | N/A | 11545.82 | N/A | N/A | N/A | N/A | N/A
GEN-2023-051 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Solar | Red Rock Road - Weatherford Junction 138 kV Line | 773004 | 1 | 773000 | 2459.13 | 38.55 | 2016.44 | N/A | 2212.13 | 34.68 | 2016.45 | N/A | 2212.13 | 34.68 | 2017.64 | N/A | 2212.8 | 50.08 | 2063.41 | N/A | 2419.77 | 23.72 | 2019.17 | N/A | 2214.46 | 34.71 | N/A | N/A | N/A | N/A
GEN-2023-051 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Storage | Red Rock Road - Weatherford Junction 138 kV Line | 773004 | 2 | 773000 | 2459.13 | 32.79 | 2016.44 | N/A | 2212.13 | N/A | 2016.45 | N/A | 2212.13 | N/A | 2017.64 | N/A | 2212.8 | N/A | 2063.41 | N/A | 2419.77 | 50.44 | 2019.17 | N/A | 2214.46 | N/A | N/A | N/A | N/A | N/A
GEN-2023-052 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Solar | Rose Hill 345 kV Substation | 773024 | 1 | 532794 | 14329.04 | 224.61 | 11073.93 | N/A | 12586.56 | 197.29 | 11075.54 | N/A | 12587.15 | 197.3 | 11530.18 | N/A | 14077.27 | 137.15 | 11329.41 | N/A | 12796.61 | 200.59 | 11108.03 | N/A | 12605.52 | 197.59 | N/A | N/A | N/A | N/A
GEN-2023-052 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Storage | Rose Hill 345 kV Substation | 773024 | 2 | 532794 | 14329.04 | 191.05 | 11073.93 | N/A | 12586.56 | N/A | 11075.54 | N/A | 12587.15 | N/A | 11530.18 | N/A | 14077.27 | 291.64 | 11329.41 | N/A | 12796.61 | N/A | 11108.03 | N/A | 12605.52 | N/A | N/A | N/A | N/A | N/A
GEN-2023-052 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Solar | Rose Hill 345 kV Substation | 773027 | 1 | 532794 | 14329.04 | 228.68 | 11073.93 | N/A | 12586.56 | 200.87 | 11075.54 | N/A | 12587.15 | 200.88 | 11530.18 | N/A | 14077.27 | 139.63 | 11329.41 | N/A | 12796.61 | 204.22 | 11108.03 | N/A | 12605.52 | 201.17 | N/A | N/A | N/A | N/A
GEN-2023-052 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Storage | Rose Hill 345 kV Substation | 773027 | 2 | 532794 | 14329.04 | 191.05 | 11073.93 | N/A | 12586.56 | N/A | 11075.54 | N/A | 12587.15 | N/A | 11530.18 | N/A | 14077.27 | 291.64 | 11329.41 | N/A | 12796.61 | N/A | 11108.03 | N/A | 12605.52 | N/A | N/A | N/A | N/A | N/A
GEN-2023-053 | DIS-23-1 | 04 SOUTHEAST | AEP | 212 | ER/NR | Wind | Pittsburg - Valiant 345kV line | 773044 | 1 | 773040 | 7793.19 | 362.04 | 6604.87 | 102.28 | 7341.96 | 341.07 | 6604.9 | 102.28 | 7341.97 | 341.07 | 6608.4 | 102.33 | 7351.66 | 493.14 | 6876 | 63.89 | 7708.78 | 71.62 | 6625.64 | 102.6 | 7368.97 | 342.33 | N/A | N/A | N/A | N/A
GEN-2023-053 | DIS-23-1 | 04 SOUTHEAST | AEP | 212 | ER/NR | Wind | Pittsburg - Valiant 345kV line | 773047 | 1 | 773040 | 7793.19 | 373.34 | 6604.87 | 105.47 | 7341.96 | 351.73 | 6604.9 | 105.47 | 7341.97 | 351.73 | 6608.4 | 105.53 | 7351.66 | 508.52 | 6876 | 65.88 | 7708.78 | 73.86 | 6625.64 | 105.8 | 7368.97 | 353.02 | N/A | N/A | N/A | N/A
GEN-2023-054 | DIS-23-1 | 01 NORTH | BEPC | 400 | ER/NR | Solar | LeLand Olds-Fort Thompson 345kV line | 773064 | 1 | 773060 | 4171.11 | 52.14 | 3660.89 | N/A | 4162.72 | 20.81 | 3557.99 | N/A | 4058.58 | 50.73 | 3554.19 | N/A | 4055.71 | 73.2 | 3554.01 | N/A | 4055.64 | 50.7 | 3554.01 | N/A | 4055.64 | 50.7 | N/A | N/A | N/A | N/A
GEN-2023-054 | DIS-23-1 | 01 NORTH | BEPC | 400 | ER/NR | Solar | LeLand Olds-Fort Thompson 345kV line | 773067 | 1 | 773060 | 4171.11 | 52.14 | 3660.89 | N/A | 4162.72 | 20.81 | 3557.99 | N/A | 4058.58 | 50.73 | 3554.19 | N/A | 4055.71 | 73.2 | 3554.01 | N/A | 4055.64 | 50.7 | 3554.01 | N/A | 4055.64 | 50.7 | N/A | N/A | N/A | N/A
GEN-2023-055 | DIS-23-1 | 04 SOUTHEAST | GRDA | 100 | ER/NR | Storage | Kerr Grove 161 kV | 773084 | 1 | 512635 | 8765.55 | 87.66 | 7129.49 | N/A | 8365.06 | N/A | 7129.54 | N/A | 8365.06 | N/A | 7136.83 | N/A | 8393.29 | N/A | 7176.94 | N/A | 8708.61 | 87.09 | 7130.72 | N/A | 8365.26 | N/A | N/A | N/A | N/A | N/A
GEN-2023-056 | DIS-23-1 | 04 SOUTHEAST | SWPA | 150 | ER/NR | Storage | Van Buren 161 kV | 773104 | 1 | 505522 | 5533.6 | 36.89 | 4403.57 | N/A | 5189.74 | N/A | 4403.58 | N/A | 5189.74 | N/A | 4404.11 | N/A | 5190.29 | N/A | 4415.46 | N/A | 5531.72 | 36.88 | 4404.01 | N/A | 5189.85 | N/A | N/A | N/A | N/A | N/A
GEN-2023-057 | DIS-23-1 | 04 SOUTHEAST | GRDA | 150 | ER/NR | Storage | Pawnee Switch 138 kV | 773124 | 1 | 512749 | 2572.13 | 17.15 | 2273.11 | N/A | 2352.07 | N/A | 2273.12 | N/A | 2352.07 | N/A | 2275.05 | N/A | 2353.61 | N/A | 2295.41 | N/A | 2517.16 | 16.78 | 2273.82 | N/A | 2352.32 | N/A | N/A | N/A | N/A | N/A
GEN-2023-059 | DIS-23-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Solar | Tap Rockhill to South Shreveport 138 kV line | 773164 | 1 | 773160 | 2559.91 | 43.86 | 1829.6 | N/A | 2313.44 | 27.67 | 1829.6 | N/A | 2313.44 | 27.67 | 1829.62 | N/A | 2313.44 | 39.96 | 1830.29 | N/A | 2324.44 | 11.62 | 1829.69 | N/A | 2313.45 | 27.67 | N/A | N/A | N/A | N/A
GEN-2023-059 | DIS-23-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | CT | Tap Rockhill to South Shreveport 138 kV line | 773166 | 1 | 773160 | 2559.91 | 36.15 | 1829.6 | N/A | 2313.44 | N/A | 1829.6 | N/A | 2313.44 | N/A | 1829.62 | N/A | 2313.44 | N/A | 1830.29 | N/A | 2324.44 | N/A | 1829.69 | N/A | 2313.45 | N/A | N/A | N/A | N/A | N/A
GEN-2023-059 | DIS-23-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | CT | Tap Rockhill to South Shreveport 138 kV line | 773167 | 1 | 773160 | 2559.91 | 36.15 | 1829.6 | N/A | 2313.44 | N/A | 1829.6 | N/A | 2313.44 | N/A | 1829.62 | N/A | 2313.44 | N/A | 1830.29 | N/A | 2324.44 | N/A | 1829.69 | N/A | 2313.45 | N/A | N/A | N/A | N/A | N/A
GEN-2023-060 | DIS-23-1 | 05 SOUTHWEST | SPS | 256 | ER/NR | Solar | Plant X 230kV Substation | 773184 | 1 | 525481 | 11903.14 | 232.48 | 9318.32 | N/A | 11054.92 | 215.92 | 9318.46 | N/A | 11054.99 | 215.92 | 9330.69 | N/A | 11064.55 | 312.04 | 9357.79 | N/A | 11073.79 | 216.28 | 9708.33 | N/A | 11817.82 | 92.33 | N/A | N/A | N/A | N/A
GEN-2023-060 | DIS-23-1 | 05 SOUTHWEST | SPS | 256 | ER/NR | Solar | Plant X 230kV Substation | 773187 | 1 | 525481 | 11903.14 | 232.48 | 9318.32 | N/A | 11054.92 | 215.92 | 9318.46 | N/A | 11054.99 | 215.92 | 9330.69 | N/A | 11064.55 | 312.04 | 9357.79 | N/A | 11073.79 | 216.28 | 9708.33 | N/A | 11817.82 | 92.33 | N/A | N/A | N/A | N/A
GEN-2023-061 | DIS-23-1 | 03 CENTRAL | SWPA | 100 | ER/NR | Storage | Carthage 161 kV Substation | 773204 | 1 | 505488 | 5569.55 | 55.7 | 4050.34 | N/A | 4788.38 | N/A | 4050.39 | N/A | 4788.38 | N/A | 4055.9 | N/A | 5310.66 | 53.11 | 4073.4 | N/A | 4805.72 | N/A | 4050.57 | N/A | 4788.4 | N/A | N/A | N/A | N/A | N/A
GEN-2023-062 | DIS-23-1 | 01 NORTH | LYREC | 98 | ER | Thermal | REN 115 kV Substation | 773224 | 1 | 655796 | 1393.18 | 28.43 | 1124.6 | N/A | 1260 | N/A | 1099.51 | N/A | 1234.41 | N/A | 1099.48 | N/A | 1234.4 | N/A | 1099.48 | N/A | 1234.4 | N/A | 1099.48 | N/A | 1234.4 | N/A | N/A | N/A | N/A | N/A
GEN-2023-062 | DIS-23-1 | 01 NORTH | LYREC | 98 | ER | Thermal | REN 115 kV Substation | 773227 | 1 | 655796 | 1393.18 | 28.43 | 1124.6 | N/A | 1260 | N/A | 1099.51 | N/A | 1234.41 | N/A | 1099.48 | N/A | 1234.4 | N/A | 1099.48 | N/A | 1234.4 | N/A | 1099.48 | N/A | 1234.4 | N/A | N/A | N/A | N/A | N/A
GEN-2023-063 | DIS-23-1 | 03 CENTRAL | AEP | 135 | ER/NR | Solar | Catoosa - Owasso 88th 138 kV line | 773244 | 1 | 773240 | 5778.32 | 164.4 | 4729.68 | N/A | 5534.87 | 91.95 | 4729.71 | N/A | 5534.87 | 91.95 | 4734.75 | N/A | 5649.39 | 89.4 | 4791.9 | N/A | 5610.81 | 93.22 | 4731.14 | N/A | 5535.17 | 91.96 | N/A | N/A | N/A | N/A
GEN-2023-063 | DIS-23-1 | 03 CENTRAL | AEP | 135 | ER/NR | Storage | Catoosa - Owasso 88th 138 kV line | 773247 | 1 | 773240 | 5778.32 | 57.87 | 4729.68 | N/A | 5534.87 | N/A | 4729.71 | N/A | 5534.87 | N/A | 4734.75 | N/A | 5649.39 | 78.67 | 4791.9 | N/A | 5610.81 | N/A | 4731.14 | N/A | 5535.17 | N/A | N/A | N/A | N/A | N/A
GEN-2023-064 | DIS-23-1 | 04 SOUTHEAST | SWPA | 200 | ER/NR | Solar | RS Kerr-Stigler 161 kV line | 773264 | 1 | 773260 | 2682.98 | 51.4 | 2075.08 | N/A | 2500.78 | 28.12 | 2075.08 | N/A | 2500.78 | 28.12 | 2075.2 | N/A | 2500.86 | 40.61 | 2078.3 | N/A | 2682.56 | 28.6 | 2075.19 | N/A | 2500.81 | 28.12 | N/A | N/A | N/A | N/A
GEN-2023-064 | DIS-23-1 | 04 SOUTHEAST | SWPA | 200 | ER/NR | Storage | RS Kerr-Stigler 161 kV line | 773267 | 1 | 773260 | 2682.98 | 18.15 | 2075.08 | N/A | 2500.78 | N/A | 2075.08 | N/A | 2500.78 | N/A | 2075.2 | N/A | 2500.86 | N/A | 2078.3 | N/A | 2682.56 | 25.26 | 2075.19 | N/A | 2500.81 | N/A | N/A | N/A | N/A | N/A
GEN-2023-065 | DIS-23-1 | 03 CENTRAL | Evergy | 140 | ER/NR | Storage | Halstead 69 kV Substation | 773284 | 1 | 533736 | 788.83 | 5.63 | 647.29 | N/A | 655.69 | N/A | 647.31 | N/A | 655.7 | N/A | 649.26 | N/A | 788.28 | 5.63 | 647.86 | N/A | 655.98 | N/A | 647.45 | N/A | 655.76 | N/A | N/A | N/A | N/A | N/A
GEN-2023-066 | DIS-23-1 | 01 NORTH | WAPA | 130 | ER/NR | Solar | Tap Pierre - Midland 115 kV line | 773304 | 1 | 773300 | 1326.17 | 29.81 | 1091.2 | N/A | 1325.52 | 18.03 | 1073.94 | N/A | 1235.3 | 21.73 | 1072.76 | N/A | 1234.52 | 31.36 | 1072.69 | N/A | 1234.5 | 21.72 | 1072.69 | N/A | 1234.5 | 21.72 | N/A | N/A | N/A | N/A
GEN-2023-066 | DIS-23-1 | 01 NORTH | WAPA | 130 | ER/NR | Storage | Tap Pierre - Midland 115 kV line | 773307 | 1 | 773300 | 1326.17 | 15.51 | 1091.2 | N/A | 1325.52 | 23.46 | 1073.94 | N/A | 1235.3 | N/A | 1072.76 | N/A | 1234.52 | N/A | 1072.69 | N/A | 1234.5 | N/A | 1072.69 | N/A | 1234.5 | N/A | N/A | N/A | N/A | N/A
GEN-2023-067 | DIS-23-1 | 01 NORTH | WAPA | 41 | ER/NR | Wind | Sulphur 115 kV Substation | 773324 | 1 | 652491 | 658.9 | 80.35 | 625.44 | 15.25 | 658.71 | 16.07 | 508.67 | 20.68 | 529.14 | 64.53 | 508.48 | 20.67 | 528.93 | 93.14 | 508.46 | 20.67 | 528.92 | 64.5 | 508.46 | 20.67 | 528.92 | 64.5 | N/A | N/A | N/A | N/A
GEN-2023-068 | DIS-23-1 | 03 CENTRAL | SPS | 250 | ER/NR | Wind | Carpenter 345 kV Substation | 773344 | 1 | 523823 | 14203.78 | 561.86 | 11471.25 | 151.26 | 12558.34 | 496.77 | 11474.63 | 151.3 | 12562.29 | 496.93 | 11773.12 | 93.14 | 13561.53 | 107.29 | 11661.72 | 153.77 | 12758.76 | 504.7 | 11920.26 | 157.18 | 12978.98 | 513.41 | N/A | N/A | N/A | N/A
GEN-2023-068 | DIS-23-1 | 03 CENTRAL | SPS | 250 | ER/NR | Wind | Carpenter 345 kV Substation | 773347 | 1 | 523823 | 14203.78 | 574.59 | 11471.25 | 154.68 | 12558.34 | 508.02 | 11474.63 | 154.73 | 12562.29 | 508.18 | 11773.12 | 95.25 | 13561.53 | 109.72 | 11661.72 | 157.25 | 12758.76 | 516.13 | 11920.26 | 160.74 | 12978.98 | 525.04 | N/A | N/A | N/A | N/A
GEN-2023-069 | DIS-23-1 | 04 SOUTHEAST | WFEC | 100 | ER/NR | Solar | Tupelo - Atoka 138 kV Line | 773364 | 1 | 773360 | 1523.75 | 31.87 | 1216.33 | N/A | 1419.29 | 29.64 | 1216.33 | N/A | 1419.29 | 29.64 | 1216.45 | N/A | 1419.42 | 42.81 | 1222.67 | N/A | 1519.29 | 21.82 | 1216.99 | N/A | 1419.83 | 29.65 | N/A | N/A | N/A | N/A
GEN-2023-069 | DIS-23-1 | 04 SOUTHEAST | WFEC | 100 | ER/NR | Storage | Tupelo - Atoka 138 kV Line | 773367 | 1 | 773360 | 1523.75 | 29.2 | 1216.33 | N/A | 1419.29 | N/A | 1216.33 | N/A | 1419.29 | N/A | 1216.45 | N/A | 1419.42 | N/A | 1222.67 | N/A | 1519.29 | 50 | 1216.99 | N/A | 1419.83 | N/A | N/A | N/A | N/A | N/A
GEN-2023-070 | DIS-23-1 | 04 SOUTHEAST | AEP | 50 | ER/NR | Solar | Lane - McGee Creek Tap 69 kV | 773384 | 1 | 773380 | 366.14 | 15.74 | 294.61 | N/A | 347.07 | 14.92 | 294.61 | N/A | 347.07 | 14.92 | 294.62 | N/A | 347.07 | 21.55 | 294.9 | N/A | 365.9 | 10.31 | 294.64 | N/A | 347.09 | 14.92 | N/A | N/A | N/A | N/A
GEN-2023-070 | DIS-23-1 | 04 SOUTHEAST | AEP | 50 | ER/NR | Storage | Lane - McGee Creek Tap 69 kV | 773387 | 1 | 773380 | 366.14 | 15.42 | 294.61 | N/A | 347.07 | N/A | 294.61 | N/A | 347.07 | N/A | 294.62 | N/A | 347.07 | N/A | 294.9 | N/A | 365.9 | 25.23 | 294.64 | N/A | 347.09 | N/A | N/A | N/A | N/A | N/A
GEN-2023-071 | DIS-23-1 | 02 NEBRASKA | Tri-State | 200 | ER/NR | Solar | Elsie Tap - Paxton 115 kV Line | 773404 | 1 | 773400 | 1383.14 | 15.09 | 1048.07 | N/A | 1301.05 | 14.19 | 1051.19 | N/A | 1380.96 | 9.62 | 1050.42 | N/A | 1303.16 | 20.53 | 1047.87 | N/A | 1300.9 | 14.19 | 1047.88 | N/A | 1300.91 | 14.19 | N/A | N/A | N/A | N/A
GEN-2023-071 | DIS-23-1 | 02 NEBRASKA | Tri-State | 200 | ER/NR | Storage | Elsie Tap - Paxton 115 kV Line | 773407 | 1 | 773400 | 1383.14 | 15.33 | 1048.07 | N/A | 1301.05 | N/A | 1051.19 | N/A | 1380.96 | 24.44 | 1050.42 | N/A | 1303.16 | N/A | 1047.87 | N/A | 1300.9 | N/A | 1047.88 | N/A | 1300.91 | N/A | N/A | N/A | N/A | N/A
GEN-2023-072 | DIS-23-1 | 04 SOUTHEAST | WFEC | 250 | ER/NR | Wind | McAlister 138 kV Substation | 773424 | 1 | 520991 | 1537.73 | 60.45 | 1421.87 | 18.63 | 1449.36 | 56.98 | 1421.87 | 18.63 | 1449.36 | 56.98 | 1421.99 | 18.63 | 1449.43 | 82.27 | 1509.02 | 11.86 | 1535.86 | 12.08 | 1422.16 | 18.64 | 1449.53 | 56.98 | N/A | N/A | N/A | N/A
GEN-2023-072 | DIS-23-1 | 04 SOUTHEAST | WFEC | 250 | ER/NR | Wind | McAlister 138 kV Substation | 773427 | 1 | 520991 | 1537.73 | 62.61 | 1421.87 | 19.3 | 1449.36 | 59.01 | 1421.87 | 19.3 | 1449.36 | 59.01 | 1421.99 | 19.3 | 1449.43 | 85.21 | 1509.02 | 12.29 | 1535.86 | 12.51 | 1422.16 | 19.3 | 1449.53 | 59.02 | N/A | N/A | N/A | N/A
GEN-2023-073 | DIS-23-1 | 03 CENTRAL | Evergy | 400 | ER/NR | Storage | Rose Hill 345 kV Substation | 773444 | 1 | 532794 | 14329.04 | 71.65 | 11073.93 | N/A | 12586.56 | N/A | 11075.54 | N/A | 12587.15 | N/A | 11530.18 | N/A | 14077.27 | 70.39 | 11329.41 | N/A | 12796.61 | N/A | 11108.03 | N/A | 12605.52 | N/A | N/A | N/A | N/A | N/A
GEN-2023-073 | DIS-23-1 | 03 CENTRAL | Evergy | 400 | ER/NR | Storage | Rose Hill 345 kV Substation | 773447 | 1 | 532794 | 14329.04 | 71.65 | 11073.93 | N/A | 12586.56 | N/A | 11075.54 | N/A | 12587.15 | N/A | 11530.18 | N/A | 14077.27 | 70.39 | 11329.41 | N/A | 12796.61 | N/A | 11108.03 | N/A | 12605.52 | N/A | N/A | N/A | N/A | N/A
GEN-2023-074 | DIS-23-1 | 01 - Western Interconnect | WAPA | 85 | ER/NR | Solar | Custer to Rosebud Creek 230 kV Line Tap | 773464 | 1 | 773460 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 650.88 | N/A | 816.57 | 21.68
GEN-2023-074 | DIS-23-1 | 01 - Western Interconnect | WAPA | 85 | ER/NR | Battery/Storage | Custer to Rosebud Creek 230 kV Line Tap | 773467 | 1 | 773460 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 650.88 | N/A | 816.57 | 17.25
GEN-2023-075 | DIS-23-1 | 04 SOUTHEAST | Evergy | 200 | ER/NR | Wind | Delaware to Neosho 345 kV | 773484 | 1 | 773480 | 7956.67 | 397.83 | 6585.51 | 109.76 | 7258.5 | 362.93 | 6585.79 | 109.76 | 7258.53 | 362.93 | 6656.72 | 110.95 | 7542.96 | 544.58 | 6985.82 | 69.86 | 7650.35 | 76.5 | 6587.71 | 109.8 | 7258.99 | 362.95 | N/A | N/A | N/A | N/A
GEN-2023-075 | DIS-23-1 | 04 SOUTHEAST | Evergy | 200 | ER/NR | Wind | Delaware to Neosho 345 kV | 773487 | 1 | 773480 | 7956.67 | 397.83 | 6585.51 | 109.76 | 7258.5 | 362.93 | 6585.79 | 109.76 | 7258.53 | 362.93 | 6656.72 | 110.95 | 7542.96 | 544.58 | 6985.82 | 69.86 | 7650.35 | 76.5 | 6587.71 | 109.8 | 7258.99 | 362.95 | N/A | N/A | N/A | N/A
GEN-2023-076 | DIS-23-1 | 04 SOUTHEAST | Evergy | 100 | ER/NR | Wind | Delaware - Neosho 345 kV | 773504 | 1 | 773480 | 7956.67 | 397.83 | 6585.51 | 109.76 | 7258.5 | 362.93 | 6585.79 | 109.76 | 7258.53 | 362.93 | 6656.72 | 110.95 | 7542.96 | 544.58 | 6985.82 | 69.86 | 7650.35 | 76.5 | 6587.71 | 109.8 | 7258.99 | 362.95 | N/A | N/A | N/A | N/A
GEN-2023-077 | DIS-23-1 | 02 NEBRASKA | OPPD | 303 | ER/NR | Thermal | Substation 3740 345 kV | 773524 | 1 | 645740 | 14503.62 | 47.87 | 9195.95 | N/A | 12464.23 | N/A | 9307.02 | N/A | 13182.53 | N/A | 9290.03 | N/A | 12527.37 | N/A | 9183.44 | N/A | 12460.05 | N/A | 9182.97 | N/A | 12460.03 | N/A | N/A | N/A | N/A | N/A
GEN-2023-078 | DIS-23-1 | 02 NEBRASKA | OPPD | 303 | ER/NR | Thermal | Substation 3740 345 kV | 773544 | 1 | 645740 | 14503.62 | 47.87 | 9195.95 | N/A | 12464.23 | N/A | 9307.02 | N/A | 13182.53 | N/A | 9290.03 | N/A | 12527.37 | N/A | 9183.44 | N/A | 12460.05 | N/A | 9182.97 | N/A | 12460.03 | N/A | N/A | N/A | N/A | N/A
GEN-2023-079 | DIS-23-1 | 02 NEBRASKA | OPPD | 303 | ER/NR | Thermal | Substation 3740 345 kV | 773564 | 1 | 645740 | 14503.62 | 47.87 | 9195.95 | N/A | 12464.23 | N/A | 9307.02 | N/A | 13182.53 | N/A | 9290.03 | N/A | 12527.37 | N/A | 9183.44 | N/A | 12460.05 | N/A | 9182.97 | N/A | 12460.03 | N/A | N/A | N/A | N/A | N/A
GEN-2023-080 | DIS-23-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Solar | Lydia - Northwest Texarkana 345 kV | 773584 | 1 | 773580 | 8650.93 | 99.5 | 5530.76 | N/A | 7608.67 | 87.51 | 5530.76 | N/A | 7608.67 | 87.51 | 5531.35 | N/A | 7609.77 | 126.38 | 5565.08 | N/A | 8153.3 | 60.37 | 5535.04 | N/A | 7613.51 | 87.57 | N/A | N/A | N/A | N/A
GEN-2023-080 | DIS-23-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Storage | Lydia - Northwest Texarkana 345 kV | 773587 | 1 | 773580 | 8650.93 | 82.78 | 5530.76 | N/A | 7608.67 | N/A | 5530.76 | N/A | 7608.67 | N/A | 5531.35 | N/A | 7609.77 | N/A | 5565.08 | N/A | 8153.3 | 125.56 | 5535.04 | N/A | 7613.51 | N/A | N/A | N/A | N/A | N/A
GEN-2023-081 | DIS-23-1 | 05 SOUTHWEST | NEET | 625 | ER/NR | Solar | Crossroads - Hobbs 345 kV Line | 773604 | 1 | 773600 | 10828.62 | 123.96 | 6822.52 | N/A | 8824.33 | 101.02 | 6822.57 | N/A | 8824.35 | 101.02 | 6827.57 | N/A | 8827.36 | 145.91 | 6853.39 | N/A | 8839.86 | 101.19 | 7435.05 | N/A | 9833.83 | 60.94 | N/A | N/A | N/A | N/A
GEN-2023-081 | DIS-23-1 | 05 SOUTHWEST | NEET | 625 | ER/NR | Storage | Crossroads - Hobbs 345 kV Line | 773607 | 1 | 773600 | 10828.62 | 185.52 | 6822.52 | N/A | 8824.33 | N/A | 6822.57 | N/A | 8824.35 | N/A | 6827.57 | N/A | 8827.36 | N/A | 6853.39 | N/A | 8839.86 | N/A | 7435.05 | N/A | 9833.83 | 228.01 | N/A | N/A | N/A | N/A
GEN-2023-081 | DIS-23-1 | 05 SOUTHWEST | NEET | 625 | ER/NR | Solar | Crossroads - Hobbs 345 kV Line | 773610 | 1 | 773600 | 10828.62 | 123.96 | 6822.52 | N/A | 8824.33 | 101.02 | 6822.57 | N/A | 8824.35 | 101.02 | 6827.57 | N/A | 8827.36 | 145.91 | 6853.39 | N/A | 8839.86 | 101.19 | 7435.05 | N/A | 9833.83 | 60.94 | N/A | N/A | N/A | N/A
GEN-2023-081 | DIS-23-1 | 05 SOUTHWEST | NEET | 625 | ER/NR | Storage | Crossroads - Hobbs 345 kV Line | 773613 | 1 | 773600 | 10828.62 | 185.52 | 6822.52 | N/A | 8824.33 | N/A | 6822.57 | N/A | 8824.35 | N/A | 6827.57 | N/A | 8827.36 | N/A | 6853.39 | N/A | 8839.86 | N/A | 7435.05 | N/A | 9833.83 | 228.01 | N/A | N/A | N/A | N/A
GEN-2023-081 | DIS-23-1 | 05 SOUTHWEST | NEET | 625 | ER/NR | Solar | Crossroads - Hobbs 345 kV Line | 773616 | 1 | 773600 | 10828.62 | 115.7 | 6822.52 | N/A | 8824.33 | 94.28 | 6822.57 | N/A | 8824.35 | 94.28 | 6827.57 | N/A | 8827.36 | 136.18 | 6853.39 | N/A | 8839.86 | 94.45 | 7435.05 | N/A | 9833.83 | 56.88 | N/A | N/A | N/A | N/A
GEN-2023-081 | DIS-23-1 | 05 SOUTHWEST | NEET | 625 | ER/NR | Storage | Crossroads - Hobbs 345 kV Line | 773619 | 1 | 773600 | 10828.62 | 185.52 | 6822.52 | N/A | 8824.33 | N/A | 6822.57 | N/A | 8824.35 | N/A | 6827.57 | N/A | 8827.36 | N/A | 6853.39 | N/A | 8839.86 | N/A | 7435.05 | N/A | 9833.83 | 228.01 | N/A | N/A | N/A | N/A
GEN-2023-082 | DIS-23-1 | 01 NORTH | WAPA | 175 | ER/NR | Storage | White 115 kV Substation | 773624 | 1 | 652538 | 2029.36 | 11.6 | 1770.89 | N/A | 2029.01 | 11.59 | 1748.18 | N/A | 1846.58 | N/A | 1747.16 | N/A | 1846.21 | N/A | 1747.12 | N/A | 1846.21 | N/A | 1747.12 | N/A | 1846.21 | N/A | N/A | N/A | N/A | N/A
GEN-2023-083 | DIS-23-1 | 02 NEBRASKA | BEPC | 200 | ER/NR | Solar | Laramie River -Sidney 345 kV Line | 773644 | 1 | 773640 | 2846.9 | 31.06 | 2465.26 | N/A | 2728.1 | 29.76 | 2472.98 | N/A | 2838.29 | 20.08 | 2465.21 | N/A | 2725.73 | 42.94 | 2461.55 | N/A | 2722.26 | 29.7 | 2461.56 | N/A | 2722.27 | 29.7 | N/A | N/A | N/A | N/A
GEN-2023-083 | DIS-23-1 | 02 NEBRASKA | BEPC | 200 | ER/NR | Storage | Laramie River -Sidney 345 kV Line | 773647 | 1 | 773640 | 2846.9 | 29.97 | 2465.26 | N/A | 2728.1 | N/A | 2472.98 | N/A | 2838.29 | 48.42 | 2465.21 | N/A | 2725.73 | N/A | 2461.55 | N/A | 2722.26 | N/A | 2461.56 | N/A | 2722.27 | N/A | N/A | N/A | N/A | N/A
GEN-2023-084 | DIS-23-1 | 01 NORTH | WAPA | 100 | ER/NR | Solar | Groton South 115 kV Substation | 773664 | 1 | 652568 | 4376.66 | 181.32 | 3517.5 | N/A | 4375.79 | 98.77 | 3333.03 | N/A | 4074.79 | 94.56 | 3331.7 | N/A | 4074.3 | 136.52 | 3331.64 | N/A | 4074.29 | 94.55 | 3331.64 | N/A | 4074.29 | 94.55 | N/A | N/A | N/A | N/A
GEN-2023-084 | DIS-23-1 | 01 NORTH | WAPA | 100 | ER/NR | Storage | Groton South 115 kV Substation | 773667 | 1 | 652568 | 4376.66 | 57.69 | 3517.5 | N/A | 4375.79 | 78.57 | 3333.03 | N/A | 4074.79 | N/A | 3331.7 | N/A | 4074.3 | N/A | 3331.64 | N/A | 4074.29 | N/A | 3331.64 | N/A | 4074.29 | N/A | N/A | N/A | N/A | N/A
GEN-2023-085 | DIS-23-1 | 03 CENTRAL | SWPA | 150 | ER/NR | Wind | Mansfield - Logan 161 kV Line | 773684 | 1 | 773680 | 2495.31 | 83.18 | 2337.3 | 25.97 | 2478.62 | 82.62 | 2337.31 | 25.97 | 2478.62 | 82.62 | 2339.42 | 15.6 | 2486.87 | 16.58 | 2345.73 | 26.06 | 2483.21 | 82.77 | 2337.32 | 25.97 | 2478.62 | 82.62 | N/A | N/A | N/A | N/A
GEN-2023-086 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Potter - Newhart 230 kV line | 773704 | 1 | 773700 | 4174.98 | 62.05 | 3388.09 | N/A | 3847.96 | 31.96 | 3388.17 | N/A | 3848 | 31.96 | 3394.4 | N/A | 3854.38 | 46.23 | 3398.83 | N/A | 3854.66 | 32.02 | 3428.48 | N/A | 4158.97 | 33.04 | N/A | N/A | N/A | N/A
GEN-2023-086 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Storage | Potter - Newhart 230 kV line | 773707 | 1 | 773700 | 4174.98 | 17.94 | 3388.09 | N/A | 3847.96 | N/A | 3388.17 | N/A | 3848 | N/A | 3394.4 | N/A | 3854.38 | N/A | 3398.83 | N/A | 3854.66 | N/A | 3428.48 | N/A | 4158.97 | 23.88 | N/A | N/A | N/A | N/A
GEN-2023-087 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Solar | Archie 161 kV Substation | 773724 | 1 | 541207 | 5987.33 | 74.84 | 4404.28 | N/A | 5640.94 | 70.51 | 4405.77 | N/A | 5641.24 | 70.52 | 4447.07 | N/A | 5934.33 | 29.67 | 4408.01 | N/A | 5641.61 | 70.52 | 4404.46 | N/A | 5640.95 | 70.51 | N/A | N/A | N/A | N/A
GEN-2023-088 | DIS-23-1 | 04 SOUTHEAST | WFEC | 117 | ER/NR | Wind | Pharaoh 138 kV Substation | 773744 | 1 | 521026 | 4172.52 | 178.31 | 3721.06 | 53.01 | 4011.15 | 171.42 | 3721.06 | 53.01 | 4011.15 | 171.42 | 3722.38 | 53.03 | 4011.9 | 247.56 | 3855.87 | 32.96 | 4141.2 | 35.39 | 3723.34 | 53.04 | 4012.41 | 171.47 | N/A | N/A | N/A | N/A
GEN-2023-089 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Buckner 345 kV Substation | 773764 | 1 | 531501 | 8567.22 | 342.69 | 7386.8 | 98.49 | 7777.43 | 311.1 | 7391.53 | 98.55 | 7784.39 | 311.38 | 7993.34 | 63.95 | 8470.81 | 67.77 | 7425.98 | 99.01 | 7811.09 | 312.44 | 7441 | 99.21 | 7817.07 | 312.68 | N/A | N/A | N/A | N/A
GEN-2023-089 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Buckner 345 kV Substation | 773767 | 1 | 531501 | 8567.22 | 342.69 | 7386.8 | 98.49 | 7777.43 | 311.1 | 7391.53 | 98.55 | 7784.39 | 311.38 | 7993.34 | 63.95 | 8470.81 | 67.77 | 7425.98 | 99.01 | 7811.09 | 312.44 | 7441 | 99.21 | 7817.07 | 312.68 | N/A | N/A | N/A | N/A
GEN-2023-090 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Buckner 345 kV Substation | 773784 | 1 | 531501 | 8567.22 | 342.69 | 7386.8 | 98.49 | 7777.43 | 311.1 | 7391.53 | 98.55 | 7784.39 | 311.38 | 7993.34 | 63.95 | 8470.81 | 67.77 | 7425.98 | 99.01 | 7811.09 | 312.44 | 7441 | 99.21 | 7817.07 | 312.68 | N/A | N/A | N/A | N/A
GEN-2023-090 | DIS-23-1 | 03 CENTRAL | SUNC | 250 | ER/NR | Wind | Buckner 345 kV Substation | 773787 | 1 | 531501 | 8567.22 | 342.69 | 7386.8 | 98.49 | 7777.43 | 311.1 | 7391.53 | 98.55 | 7784.39 | 311.38 | 7993.34 | 63.95 | 8470.81 | 67.77 | 7425.98 | 99.01 | 7811.09 | 312.44 | 7441 | 99.21 | 7817.07 | 312.68 | N/A | N/A | N/A | N/A
GEN-2023-091 | DIS-23-1 | 03 CENTRAL | SUNC | 504 | ER/NR | Wind | Buckner 345 kV Substation | 773804 | 1 | 531501 | 8567.22 | 171.62 | 7386.8 | 49.32 | 7777.43 | 155.8 | 7391.53 | 49.36 | 7784.39 | 155.94 | 7993.34 | 32.02 | 8470.81 | 33.94 | 7425.98 | 49.59 | 7811.09 | 156.47 | 7441 | 49.69 | 7817.07 | 156.59 | N/A | N/A | N/A | N/A
GEN-2023-091 | DIS-23-1 | 03 CENTRAL | SUNC | 504 | ER/NR | Wind | Buckner 345 kV Substation | 773807 | 1 | 531501 | 8567.22 | 168.38 | 7386.8 | 48.39 | 7777.43 | 152.86 | 7391.53 | 48.42 | 7784.39 | 153 | 7993.34 | 31.42 | 8470.81 | 33.3 | 7425.98 | 48.65 | 7811.09 | 153.52 | 7441 | 48.75 | 7817.07 | 153.64 | N/A | N/A | N/A | N/A
GEN-2023-092 | DIS-23-1 | 04 SOUTHEAST | WFEC | 125 | ER/NR | Solar | Unger - Frogville 138 kV line | 773824 | 1 | 773820 | 2033.11 | 34.56 | 1565.27 | N/A | 1917.2 | 32.59 | 1565.27 | N/A | 1917.2 | 32.59 | 1565.43 | N/A | 1917.52 | 47.07 | 1573.8 | N/A | 2024.64 | 23 | 1566.44 | N/A | 1918.4 | 32.61 | N/A | N/A | N/A | N/A
GEN-2023-092 | DIS-23-1 | 04 SOUTHEAST | WFEC | 125 | ER/NR | Storage | Unger - Frogville 138 kV line | 773827 | 1 | 773820 | 2033.11 | 32.92 | 1565.27 | N/A | 1917.2 | N/A | 1565.27 | N/A | 1917.2 | N/A | 1565.43 | N/A | 1917.52 | N/A | 1573.8 | N/A | 2024.64 | 54.77 | 1566.44 | N/A | 1918.4 | N/A | N/A | N/A | N/A | N/A
GEN-2023-093 | DIS-23-1 | 03 CENTRAL | SPS | 250 | ER/NR | Wind | Carpenter 345 kV Substation | 773844 | 1 | 523823 | 14203.78 | 561.86 | 11471.25 | 151.26 | 12558.34 | 496.77 | 11474.63 | 151.3 | 12562.29 | 496.93 | 11773.12 | 93.14 | 13561.53 | 107.29 | 11661.72 | 153.77 | 12758.76 | 504.7 | 11920.26 | 157.18 | 12978.98 | 513.41 | N/A | N/A | N/A | N/A
GEN-2023-093 | DIS-23-1 | 03 CENTRAL | SPS | 250 | ER/NR | Wind | Carpenter 345 kV Substation | 773847 | 1 | 523823 | 14203.78 | 574.59 | 11471.25 | 154.68 | 12558.34 | 508.02 | 11474.63 | 154.73 | 12562.29 | 508.18 | 11773.12 | 95.25 | 13561.53 | 109.72 | 11661.72 | 157.25 | 12758.76 | 516.13 | 11920.26 | 160.74 | 12978.98 | 525.04 | N/A | N/A | N/A | N/A
GEN-2023-094 | DIS-23-1 | 03 CENTRAL | SPS | 250 | ER/NR | Wind | Carpenter 345 kV Substation | 773864 | 1 | 523823 | 14203.78 | 561.86 | 11471.25 | 151.26 | 12558.34 | 496.77 | 11474.63 | 151.3 | 12562.29 | 496.93 | 11773.12 | 93.14 | 13561.53 | 107.29 | 11661.72 | 153.77 | 12758.76 | 504.7 | 11920.26 | 157.18 | 12978.98 | 513.41 | N/A | N/A | N/A | N/A
GEN-2023-094 | DIS-23-1 | 03 CENTRAL | SPS | 250 | ER/NR | Wind | Carpenter 345 kV Substation | 773867 | 1 | 523823 | 14203.78 | 574.59 | 11471.25 | 154.68 | 12558.34 | 508.02 | 11474.63 | 154.73 | 12562.29 | 508.18 | 11773.12 | 95.25 | 13561.53 | 109.72 | 11661.72 | 157.25 | 12758.76 | 516.13 | 11920.26 | 160.74 | 12978.98 | 525.04 | N/A | N/A | N/A | N/A
GEN-2023-097 | DIS-23-1 | 01 NORTH | BEPC | 250 | ER/NR | Storage | Judson 345 kV Substation | 773924 | 1 | 659333 | 5824.24 | 46.59 | 3971.72 | N/A | 5110.18 | 40.88 | 3783.89 | N/A | 4611.25 | N/A | 3783.55 | N/A | 4611.13 | N/A | 3783.53 | N/A | 4611.12 | N/A | 3783.53 | N/A | 4611.12 | N/A | N/A | N/A | N/A | N/A
GEN-2023-097 | DIS-23-1 | 01 NORTH | BEPC | 250 | ER/NR | Storage | Judson 345 kV Substation | 773927 | 1 | 659333 | 5824.24 | 46.59 | 3971.72 | N/A | 5110.18 | 40.88 | 3783.89 | N/A | 4611.25 | N/A | 3783.55 | N/A | 4611.13 | N/A | 3783.53 | N/A | 4611.12 | N/A | 3783.53 | N/A | 4611.12 | N/A | N/A | N/A | N/A | N/A
GEN-2023-098 | DIS-23-1 | 01 NORTH | WAPA | 200 | ER/NR | Solar | Bison - Maurine 230 kV Line | 773944 | 1 | 773940 | 1418.29 | 15.47 | 1088.92 | N/A | 1417.29 | 10.02 | 1031.65 | N/A | 1259.19 | 13.74 | 1031.16 | N/A | 1258.58 | 19.83 | 1031.11 | N/A | 1258.55 | 13.73 | 1031.11 | N/A | 1258.55 | 13.73 | N/A | N/A | N/A | N/A
GEN-2023-098 | DIS-23-1 | 01 NORTH | WAPA | 200 | ER/NR | Storage | Bison - Maurine 230 kV Line | 773947 | 1 | 773940 | 1418.29 | 14.93 | 1088.92 | N/A | 1417.29 | 24.18 | 1031.65 | N/A | 1259.19 | N/A | 1031.16 | N/A | 1258.58 | N/A | 1031.11 | N/A | 1258.55 | N/A | 1031.11 | N/A | 1258.55 | N/A | N/A | N/A | N/A | N/A
GEN-2023-099 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Solar | Jeffery Energy Center 345 kV Substation | 773964 | 1 | 532766 | 13361.44 | 222.69 | 8140.72 | N/A | 12991.77 | 216.53 | 8146.23 | N/A | 12994.16 | 216.57 | 8442.14 | N/A | 13312.79 | 88.75 | 8151.82 | N/A | 12994.96 | 216.58 | 8143.88 | N/A | 12992.72 | 216.55 | N/A | N/A | N/A | N/A
GEN-2023-099 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Solar | Jeffery Energy Center 345 kV Substation | 773967 | 1 | 532766 | 13361.44 | 222.69 | 8140.72 | N/A | 12991.77 | 216.53 | 8146.23 | N/A | 12994.16 | 216.57 | 8442.14 | N/A | 13312.79 | 88.75 | 8151.82 | N/A | 12994.96 | 216.58 | 8143.88 | N/A | 12992.72 | 216.55 | N/A | N/A | N/A | N/A
GEN-2023-100 | DIS-23-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Solar | Degrasse 345 kV Substation | 773984 | 1 | 515852 | 18112.12 | 259.6 | 13920.26 | N/A | 16146.28 | 231.43 | 13923.84 | N/A | 16149.53 | 231.47 | 14343.96 | N/A | 16794.29 | 347.57 | 14522.45 | N/A | 17078.51 | 160.37 | 14218.76 | N/A | 16416.33 | 235.3 | N/A | N/A | N/A | N/A
GEN-2023-100 | DIS-23-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Storage | Degrasse 345 kV Substation | 773987 | 1 | 515852 | 18112.12 | 254.21 | 13920.26 | N/A | 16146.28 | N/A | 13923.84 | N/A | 16149.53 | N/A | 14343.96 | N/A | 16794.29 | N/A | 14522.45 | N/A | 17078.51 | 392.58 | 14218.76 | N/A | 16416.33 | N/A | N/A | N/A | N/A | N/A
GEN-2023-100 | DIS-23-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Solar | Degrasse 345 kV Substation | 773990 | 1 | 515852 | 18112.12 | 259.6 | 13920.26 | N/A | 16146.28 | 231.43 | 13923.84 | N/A | 16149.53 | 231.47 | 14343.96 | N/A | 16794.29 | 347.57 | 14522.45 | N/A | 17078.51 | 160.37 | 14218.76 | N/A | 16416.33 | 235.3 | N/A | N/A | N/A | N/A
GEN-2023-100 | DIS-23-1 | 04 SOUTHEAST | OGE | 300 | ER/NR | Storage | Degrasse 345 kV Substation | 773993 | 1 | 515852 | 18112.12 | 254.21 | 13920.26 | N/A | 16146.28 | N/A | 13923.84 | N/A | 16149.53 | N/A | 14343.96 | N/A | 16794.29 | N/A | 14522.45 | N/A | 17078.51 | 392.58 | 14218.76 | N/A | 16416.33 | N/A | N/A | N/A | N/A | N/A
GEN-2023-101 | DIS-23-1 | 04 SOUTHEAST | SPS | 150 | ER/NR | Solar | Tap Stateline Demarc - Wheeler 230 kV Line | 774004 | 1 | 774000 | 3748.67 | 57.29 | 3365.29 | N/A | 3610.11 | 55.17 | 3365.36 | N/A | 3610.15 | 55.17 | 3371.65 | N/A | 3616.43 | 79.8 | 3386.9 | N/A | 3724.88 | 36.79 | 3381.2 | N/A | 3626.21 | 55.42 | N/A | N/A | N/A | N/A
GEN-2023-101 | DIS-23-1 | 04 SOUTHEAST | SPS | 150 | ER/NR | Storage | Tap Stateline Demarc - Wheeler 230 kV Line | 774007 | 1 | 774000 | 3748.67 | 47.59 | 3365.29 | N/A | 3610.11 | N/A | 3365.36 | N/A | 3610.15 | N/A | 3371.65 | N/A | 3616.43 | N/A | 3386.9 | N/A | 3724.88 | 76.4 | 3381.2 | N/A | 3626.21 | N/A | N/A | N/A | N/A | N/A
GEN-2023-102 | DIS-23-1 | 04 SOUTHEAST | OGE | 475 | ER/NR | Solar | Degrasse 345 kV Substation | 776827 | 1 | 515852 | 18112.12 | 331 | 13920.26 | N/A | 16146.28 | 295.07 | 13923.84 | N/A | 16149.53 | 295.13 | 14343.96 | N/A | 16794.29 | 443.16 | 14522.45 | N/A | 17078.51 | 192.51 | 14218.76 | N/A | 16416.33 | 300.01 | N/A | N/A | N/A | N/A
GEN-2023-102 | DIS-23-1 | 04 SOUTHEAST | OGE | 475 | ER/NR | Storage | Degrasse 345 kV Substation | 776829 | 1 | 515852 | 18112.12 | 381.31 | 13920.26 | N/A | 16146.28 | N/A | 13923.84 | N/A | 16149.53 | N/A | 14343.96 | N/A | 16794.29 | N/A | 14522.45 | N/A | 17078.51 | 554.43 | 14218.76 | N/A | 16416.33 | N/A | N/A | N/A | N/A | N/A
GEN-2023-102 | DIS-23-1 | 04 SOUTHEAST | OGE | 475 | ER/NR | Solar | Degrasse 345 kV Substation | 776831 | 1 | 515852 | 18112.12 | 331 | 13920.26 | N/A | 16146.28 | 295.07 | 13923.84 | N/A | 16149.53 | 295.13 | 14343.96 | N/A | 16794.29 | 443.16 | 14522.45 | N/A | 17078.51 | 192.51 | 14218.76 | N/A | 16416.33 | 300.01 | N/A | N/A | N/A | N/A
GEN-2023-102 | DIS-23-1 | 04 SOUTHEAST | OGE | 475 | ER/NR | Storage | Degrasse 345 kV Substation | 776833 | 1 | 515852 | 18112.12 | 381.31 | 13920.26 | N/A | 16146.28 | N/A | 13923.84 | N/A | 16149.53 | N/A | 14343.96 | N/A | 16794.29 | N/A | 14522.45 | N/A | 17078.51 | 554.43 | 14218.76 | N/A | 16416.33 | N/A | N/A | N/A | N/A | N/A
GEN-2023-102 | DIS-23-1 | 04 SOUTHEAST | OGE | 475 | ER/NR | Solar | Degrasse 345 kV Substation | 776835 | 1 | 515852 | 18112.12 | 331 | 13920.26 | N/A | 16146.28 | 295.07 | 13923.84 | N/A | 16149.53 | 295.13 | 14343.96 | N/A | 16794.29 | 443.16 | 14522.45 | N/A | 17078.51 | 192.51 | 14218.76 | N/A | 16416.33 | 300.01 | N/A | N/A | N/A | N/A
GEN-2023-102 | DIS-23-1 | 04 SOUTHEAST | OGE | 475 | ER/NR | Storage | Degrasse 345 kV Substation | 776837 | 1 | 515852 | 18112.12 | 381.31 | 13920.26 | N/A | 16146.28 | N/A | 13923.84 | N/A | 16149.53 | N/A | 14343.96 | N/A | 16794.29 | N/A | 14522.45 | N/A | 17078.51 | 554.43 | 14218.76 | N/A | 16416.33 | N/A | N/A | N/A | N/A | N/A
GEN-2023-102 | DIS-23-1 | 04 SOUTHEAST | OGE | 475 | ER/NR | Solar | Degrasse 345 kV Substation | 776839 | 1 | 515852 | 18112.12 | 331 | 13920.26 | N/A | 16146.28 | 295.07 | 13923.84 | N/A | 16149.53 | 295.13 | 14343.96 | N/A | 16794.29 | 443.16 | 14522.45 | N/A | 17078.51 | 192.51 | 14218.76 | N/A | 16416.33 | 300.01 | N/A | N/A | N/A | N/A
GEN-2023-102 | DIS-23-1 | 04 SOUTHEAST | OGE | 475 | ER/NR | Storage | Degrasse 345 kV Substation | 776841 | 1 | 515852 | 18112.12 | 423.68 | 13920.26 | N/A | 16146.28 | N/A | 13923.84 | N/A | 16149.53 | N/A | 14343.96 | N/A | 16794.29 | N/A | 14522.45 | N/A | 17078.51 | 616.02 | 14218.76 | N/A | 16416.33 | N/A | N/A | N/A | N/A | N/A
GEN-2023-103 | DIS-23-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Storage | Northeastern 138 kV Substation | 774044 | 1 | 510396 | 8764.27 | 43.82 | 4377.39 | N/A | 8367.05 | N/A | 4377.42 | N/A | 8367.05 | N/A | 4382.87 | N/A | 8393.36 | N/A | 4427.4 | N/A | 8702.41 | 43.51 | 4378.59 | N/A | 8367.34 | N/A | N/A | N/A | N/A | N/A
GEN-2023-104 | DIS-23-1 | 04 SOUTHEAST | WFEC | 100 | ER/NR | Solar | Mooreland - Noel 138 kV Line | 774064 | 1 | 774060 | 3745.66 | 78.33 | 3350.4 | N/A | 3567.04 | 74.5 | 3350.56 | N/A | 3567.15 | 74.5 | 3370.21 | N/A | 3589.6 | 108.25 | 3439.22 | N/A | 3713.4 | 53.34 | 3363.81 | N/A | 3576.28 | 74.69 | N/A | N/A | N/A | N/A
GEN-2023-104 | DIS-23-1 | 04 SOUTHEAST | WFEC | 100 | ER/NR | Storage | Mooreland - Noel 138 kV Line | 774067 | 1 | 774060 | 3745.66 | 71.78 | 3350.4 | N/A | 3567.04 | N/A | 3350.56 | N/A | 3567.15 | N/A | 3370.21 | N/A | 3589.6 | N/A | 3439.22 | N/A | 3713.4 | 122.2 | 3363.81 | N/A | 3576.28 | N/A | N/A | N/A | N/A | N/A
GEN-2023-105 | DIS-23-1 | 01 NORTH | BEPC | 249 | ER/NR | Wind | Chappelle Creek 345 kV | 774084 | 1 | 659130 | 7776.01 | 312.29 | 7135.94 | 57.32 | 7682.37 | 61.71 | 6495.83 | 86.96 | 7078.45 | 284.28 | 6403.29 | 85.72 | 6988.25 | 405.23 | 6399.25 | 85.67 | 6986.39 | 280.58 | 6399.24 | 85.67 | 6986.39 | 280.58 | N/A | N/A | N/A | N/A
GEN-2023-105 | DIS-23-1 | 01 NORTH | BEPC | 249 | ER/NR | Wind | Chappelle Creek 345 kV | 774087 | 1 | 659130 | 7776.01 | 312.29 | 7135.94 | 57.32 | 7682.37 | 61.71 | 6495.83 | 86.96 | 7078.45 | 284.28 | 6403.29 | 85.72 | 6988.25 | 405.23 | 6399.25 | 85.67 | 6986.39 | 280.58 | 6399.24 | 85.67 | 6986.39 | 280.58 | N/A | N/A | N/A | N/A
GEN-2023-106 | DIS-23-1 | 01 NORTH | BEPC | 504 | ER/NR | Wind | Chappelle Creek 345 kV Substation | 774104 | 1 | 659130 | 7776.01 | 155.77 | 7135.94 | 28.59 | 7682.37 | 30.78 | 6495.83 | 43.37 | 7078.45 | 141.8 | 6403.29 | 42.76 | 6988.25 | 202.13 | 6399.25 | 42.73 | 6986.39 | 139.95 | 6399.24 | 42.73 | 6986.39 | 139.95 | N/A | N/A | N/A | N/A
GEN-2023-106 | DIS-23-1 | 01 NORTH | BEPC | 504 | ER/NR | Wind | Chappelle Creek 345 kV Substation | 774107 | 1 | 659130 | 7776.01 | 152.83 | 7135.94 | 28.05 | 7682.37 | 30.2 | 6495.83 | 42.56 | 7078.45 | 139.12 | 6403.29 | 41.95 | 6988.25 | 198.32 | 6399.25 | 41.92 | 6986.39 | 137.31 | 6399.24 | 41.92 | 6986.39 | 137.31 | N/A | N/A | N/A | N/A
GEN-2023-107 | DIS-23-1 | 03 CENTRAL | SUNC | 300 | ER | Wind | Setab 345 kV | 774124 | 1 | 531465 | 7600.38 | 253.35 | 6669.31 | 74.1 | 7335.7 | 244.52 | 6678.18 | 74.2 | 7352.63 | 245.09 | 6767.43 | 45.12 | 7542.26 | 50.28 | 6690.34 | 74.34 | 7353.24 | 245.11 | 6708.78 | 74.54 | 7365.19 | 245.51 | N/A | N/A | N/A | N/A
GEN-2023-107 | DIS-23-1 | 03 CENTRAL | SUNC | 300 | ER | Wind | Setab 345 kV | 774127 | 1 | 531465 | 7600.38 | 253.35 | 6669.31 | 74.1 | 7335.7 | 244.52 | 6678.18 | 74.2 | 7352.63 | 245.09 | 6767.43 | 45.12 | 7542.26 | 50.28 | 6690.34 | 74.34 | 7353.24 | 245.11 | 6708.78 | 74.54 | 7365.19 | 245.51 | N/A | N/A | N/A | N/A
GEN-2023-109 | DIS-23-1 | 05 SOUTHWEST | SPS | 65 | ER/NR | Solar | Dumas and 19th Street 115 kV Substation | 774164 | 1 | 523318 | 1318.76 | 50.72 | 1174.49 | N/A | 1256.81 | 48.34 | 1174.5 | N/A | 1256.82 | 48.34 | 1175.44 | N/A | 1257.86 | 69.85 | 1175.77 | N/A | 1257.69 | 48.37 | 1233.98 | N/A | 1316.74 | 20.26 | N/A | N/A | N/A | N/A
GEN-2023-110 | DIS-23-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Tap Border to Tuco 345 kV Line | 774184 | 1 | 774180 | 3694.6 | 72.8 | 3268.89 | N/A | 3618.85 | 71.31 | 3268.95 | N/A | 3618.88 | 71.31 | 3273.9 | N/A | 3623.52 | 103.1 | 3287.57 | N/A | 3633.51 | 71.6 | 3296.68 | N/A | 3661.83 | 28.86 | N/A | N/A | N/A | N/A
GEN-2023-110 | DIS-23-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Tap Border to Tuco 345 kV Line | 774187 | 1 | 774180 | 3694.6 | 75.01 | 3268.89 | N/A | 3618.85 | 73.48 | 3268.95 | N/A | 3618.88 | 73.48 | 3273.9 | N/A | 3623.52 | 106.23 | 3287.57 | N/A | 3633.51 | 73.77 | 3296.68 | N/A | 3661.83 | 29.74 | N/A | N/A | N/A | N/A
GEN-2023-111 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Solar | Buffalo Flats 345 kV Substation | 774204 | 1 | 532782 | 21342.82 | 266.79 | 15966.89 | N/A | 18766.89 | 234.59 | 15972.32 | N/A | 18770.52 | 234.63 | 17094.68 | N/A | 20660.46 | 103.3 | 16389.93 | N/A | 19185.38 | 239.82 | 16141.06 | N/A | 18904.73 | 236.31 | N/A | N/A | N/A | N/A
GEN-2023-114 | DIS-23-1 | 01 NORTH | WAPA | 425 | ER/NR | Wind | Jamestown 230 kV Substation | 774264 | 1 | 652444 | 4220.05 | 98.64 | 3930.08 | 18.37 | 4219.5 | 19.73 | 3698.63 | 28.82 | 3947.47 | 92.27 | 3698.33 | 28.82 | 3947.4 | 133.23 | 3698.32 | 28.82 | 3947.4 | 92.27 | 3698.32 | 28.82 | 3947.4 | 92.27 | N/A | N/A | N/A | N/A
GEN-2023-114 | DIS-23-1 | 01 NORTH | WAPA | 425 | ER/NR | Wind | Jamestown 230 kV Substation | 774267 | 1 | 652444 | 4220.05 | 99.96 | 3930.08 | 18.62 | 4219.5 | 19.99 | 3698.63 | 29.2 | 3947.47 | 93.5 | 3698.33 | 29.2 | 3947.4 | 135 | 3698.32 | 29.2 | 3947.4 | 93.5 | 3698.32 | 29.2 | 3947.4 | 93.5 | N/A | N/A | N/A | N/A
GEN-2023-115 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Solar | Tap Georgetown Overton to Sedalia East 161 kV Line | 774284 | 1 | 774280 | 2463.45 | 41.06 | 1956.51 | N/A | 2302.24 | 38.37 | 1956.66 | N/A | 2302.28 | 38.37 | 1977.31 | N/A | 2447.62 | 16.32 | 1956.73 | N/A | 2302.28 | 38.37 | 1956.51 | N/A | 2302.24 | 38.37 | N/A | N/A | N/A | N/A
GEN-2023-115 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Solar | Tap Georgetown Overton to Sedalia East 161 kV Line | 774287 | 1 | 774280 | 2463.45 | 41.06 | 1956.51 | N/A | 2302.24 | 38.37 | 1956.66 | N/A | 2302.28 | 38.37 | 1977.31 | N/A | 2447.62 | 16.32 | 1956.73 | N/A | 2302.28 | 38.37 | 1956.51 | N/A | 2302.24 | 38.37 | N/A | N/A | N/A | N/A
GEN-2023-116 | DIS-23-1 | 02 NEBRASKA | NPPD | 500 | ER/NR | Wind | Keystone 345 kV Substation | 774304 | 1 | 640252 | 6428.29 | 190.71 | 5333.37 | 52.74 | 6070.62 | 180.09 | 5450.01 | 32.34 | 6349.28 | 37.67 | 5386.18 | 53.26 | 6139.3 | 262.98 | 5328.51 | 52.69 | 6065.43 | 179.94 | 5328.73 | 52.7 | 6065.5 | 179.94 | N/A | N/A | N/A | N/A
GEN-2023-116 | DIS-23-1 | 02 NEBRASKA | NPPD | 500 | ER/NR | Wind | Keystone 345 kV Substation | 774307 | 1 | 640252 | 6428.29 | 193.94 | 5333.37 | 53.64 | 6070.62 | 183.15 | 5450.01 | 32.88 | 6349.28 | 38.31 | 5386.18 | 54.17 | 6139.3 | 267.44 | 5328.51 | 53.59 | 6065.43 | 182.99 | 5328.73 | 53.59 | 6065.5 | 182.99 | N/A | N/A | N/A | N/A
GEN-2023-116 | DIS-23-1 | 02 NEBRASKA | NPPD | 500 | ER/NR | Wind | Keystone 345 kV Substation | 774310 | 1 | 640252 | 6428.29 | 193.94 | 5333.37 | 53.64 | 6070.62 | 183.15 | 5450.01 | 32.88 | 6349.28 | 38.31 | 5386.18 | 54.17 | 6139.3 | 267.44 | 5328.51 | 53.59 | 6065.43 | 182.99 | 5328.73 | 53.59 | 6065.5 | 182.99 | N/A | N/A | N/A | N/A
GEN-2023-117 | DIS-23-1 | 02 NEBRASKA | NPPD | 300 | ER/NR | Wind | Keystone 345 kV Substation | 774324 | 1 | 640252 | 6428.29 | 212.29 | 5333.37 | 58.71 | 6070.62 | 200.48 | 5450.01 | 36 | 6349.28 | 41.94 | 5386.18 | 59.29 | 6139.3 | 292.75 | 5328.51 | 58.66 | 6065.43 | 200.31 | 5328.73 | 58.66 | 6065.5 | 200.31 | N/A | N/A | N/A | N/A
GEN-2023-117 | DIS-23-1 | 02 NEBRASKA | NPPD | 300 | ER/NR | Wind | Keystone 345 kV Substation | 774327 | 1 | 640252 | 6428.29 | 216.3 | 5333.37 | 59.82 | 6070.62 | 204.26 | 5450.01 | 36.68 | 6349.28 | 42.73 | 5386.18 | 60.41 | 6139.3 | 298.27 | 5328.51 | 59.76 | 6065.43 | 204.09 | 5328.73 | 59.77 | 6065.5 | 204.09 | N/A | N/A | N/A | N/A
GEN-2023-118 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Wind | Buffalo Flats 345 kV Substation | 774344 | 1 | 532782 | 21342.82 | 533.57 | 15966.89 | 133.06 | 18766.89 | 469.17 | 15972.32 | 133.1 | 18770.52 | 469.26 | 17094.68 | 85.47 | 20660.46 | 103.3 | 16389.93 | 136.58 | 19185.38 | 479.63 | 16141.06 | 134.51 | 18904.73 | 472.62 | N/A | N/A | N/A | N/A
GEN-2023-120 | DIS-23-1 | 05 SOUTHWEST | SPS | 130 | ER/NR | Solar | Kress 115 kV Substation | 774384 | 1 | 525192 | 2564.55 | 49.32 | 2312.12 | N/A | 2528.16 | 48.62 | 2312.14 | N/A | 2528.16 | 48.62 | 2313.47 | N/A | 2529.01 | 70.22 | 2316.17 | N/A | 2529.84 | 48.65 | 2338.7 | N/A | 2557.54 | 19.67 | N/A | N/A | N/A | N/A
GEN-2023-121 | DIS-23-1 | 03 CENTRAL | GridLiance | 50 | ER/NR | Solar | Tie 69 kV Substation | 774404 | 1 | 533561 | 1077.88 | 53.89 | 781.46 | N/A | 882.78 | 44.14 | 781.47 | N/A | 882.78 | 44.14 | 787.5 | N/A | 983.54 | 19.67 | 803.32 | N/A | 901.48 | 45.07 | 781.59 | N/A | 882.83 | 44.14 | N/A | N/A | N/A | N/A
GEN-2023-122 | DIS-23-1 | 03 CENTRAL | Evergy | 250 | ER/NR | Solar | Wolf Creek - LaCygne 345 kV Line | 774424 | 1 | 774420 | 11932.87 | 235.14 | 9663.24 | N/A | 10762.2 | 212.07 | 9664.47 | N/A | 10762.4 | 212.08 | 9757.65 | N/A | 11894.54 | 93.75 | 9715.1 | N/A | 10789.14 | 212.6 | 9669.41 | N/A | 10764.61 | 212.12 | N/A | N/A | N/A | N/A
GEN-2023-122 | DIS-23-1 | 03 CENTRAL | Evergy | 250 | ER/NR | Solar | Wolf Creek - LaCygne 345 kV Line | 774427 | 1 | 774420 | 11932.87 | 242.28 | 9663.24 | N/A | 10762.2 | 218.51 | 9664.47 | N/A | 10762.4 | 218.52 | 9757.65 | N/A | 11894.54 | 96.6 | 9715.1 | N/A | 10789.14 | 219.06 | 9669.41 | N/A | 10764.61 | 218.56 | N/A | N/A | N/A | N/A
GEN-2023-123 | DIS-23-1 | 05 SOUTHWEST | SPS | 285 | ER/NR | Wind | Pringle Interchange 230 kV Substation | 774444 | 1 | 523267 | 1991.96 | 69.89 | 1915.06 | 22.4 | 1981.02 | 69.51 | 1915.08 | 22.4 | 1981.03 | 69.51 | 1916.57 | 22.42 | 1982.37 | 100.43 | 1917.17 | 22.42 | 1982.24 | 69.55 | 1922.45 | 13.49 | 1988.73 | 13.96 | N/A | N/A | N/A | N/A
GEN-2023-123 | DIS-23-1 | 05 SOUTHWEST | SPS | 285 | ER/NR | Wind | Pringle Interchange 230 kV Substation | 774447 | 1 | 523267 | 1991.96 | 69.89 | 1915.06 | 22.4 | 1981.02 | 69.51 | 1915.08 | 22.4 | 1981.03 | 69.51 | 1916.57 | 22.42 | 1982.37 | 100.43 | 1917.17 | 22.42 | 1982.24 | 69.55 | 1922.45 | 13.49 | 1988.73 | 13.96 | N/A | N/A | N/A | N/A
GEN-2023-124 | DIS-23-1 | 05 SOUTHWEST | SPS | 200 | ER/NR | Wind | Spearman Interchange 115 kV Substation | 774464 | 1 | 523186 | 1949.44 | 48.74 | 1893.24 | 15.78 | 1924.25 | 48.11 | 1893.27 | 15.78 | 1924.27 | 48.11 | 1895.65 | 15.8 | 1927.18 | 69.57 | 1895.72 | 15.8 | 1926.08 | 48.15 | 1911.79 | 9.56 | 1945.09 | 9.73 | N/A | N/A | N/A | N/A
GEN-2023-130 | DIS-23-1 | 01 NORTH | WAPA | 96 | ER/NR | Solar | Whitlock 230 kV Substation | 774584 | 1 | 655765 | 1882.65 | 45.37 | 1672.25 | N/A | 1881.77 | 29.53 | 1623.44 | N/A | 1797.56 | 43.32 | 1621.69 | N/A | 1796.56 | 62.52 | 1621.59 | N/A | 1796.53 | 43.29 | 1621.59 | N/A | 1796.53 | 43.29 | N/A | N/A | N/A | N/A
GEN-2023-130 | DIS-23-1 | 01 NORTH | WAPA | 96 | ER/NR | Storage | Whitlock 230 kV Substation | 774587 | 1 | 655765 | 1882.65 | 35.85 | 1672.25 | N/A | 1881.77 | 58.32 | 1623.44 | N/A | 1797.56 | N/A | 1621.69 | N/A | 1796.56 | N/A | 1621.59 | N/A | 1796.53 | N/A | 1621.59 | N/A | 1796.53 | N/A | N/A | N/A | N/A | N/A
GEN-2023-132 | DIS-23-1 | 04 SOUTHEAST | SWPA | 150 | ER/NR | Solar | Jonesboro - Independence 161 kV | 774624 | 1 | 774620 | 2364.53 | 39.41 | 2096 | N/A | 2354.58 | 39.24 | 2096 | N/A | 2354.58 | 39.24 | 2096.09 | N/A | 2355.52 | 56.69 | 2097.59 | N/A | 2363.27 | 15.76 | 2096 | N/A | 2354.58 | 39.24 | N/A | N/A | N/A | N/A
GEN-2023-133 | DIS-23-1 | 02 NEBRASKA | NPPD | 250 | ER | Wind | Sweetwater 345 kV Substation | 774644 | 1 | 640374 | 8511.93 | 340.48 | 6786.81 | 90.49 | 7401.09 | 296.04 | 7091.79 | 56.73 | 7975.64 | 63.81 | 7173.92 | 95.65 | 7795.2 | 450.23 | 6781.51 | 90.42 | 7398.56 | 295.94 | 6781.68 | 90.42 | 7398.59 | 295.94 | N/A | N/A | N/A | N/A
GEN-2023-133 | DIS-23-1 | 02 NEBRASKA | NPPD | 250 | ER | Wind | Sweetwater 345 kV Substation | 774647 | 1 | 640374 | 8511.93 | 340.48 | 6786.81 | 90.49 | 7401.09 | 296.04 | 7091.79 | 56.73 | 7975.64 | 63.81 | 7173.92 | 95.65 | 7795.2 | 450.23 | 6781.51 | 90.42 | 7398.56 | 295.94 | 6781.68 | 90.42 | 7398.59 | 295.94 | N/A | N/A | N/A | N/A
GEN-2023-134 | DIS-23-1 | 04 SOUTHEAST | AEP | 252 | ER/NR | Wind | Fixico Tap to Weleetka 138 kV Line | 774664 | 1 | 774660 | 2027.76 | 40.23 | 1955.02 | 12.93 | 2005.65 | 39.79 | 1955.02 | 12.93 | 2005.65 | 39.79 | 1955.34 | 12.93 | 2005.81 | 57.46 | 1970.91 | 7.82 | 2021.2 | 8.02 | 1955.82 | 12.94 | 2006.16 | 39.8 | N/A | N/A | N/A | N/A
GEN-2023-135 | DIS-23-1 | 04 SOUTHEAST | AEP | 52 | ER/NR | Solar | Lydia 345kV substation | 774684 | 1 | 508298 | 9508.17 | 457.12 | 5861.63 | N/A | 8254.03 | 396.83 | 5861.64 | N/A | 8254.03 | 396.83 | 5862.32 | N/A | 8255.38 | 573.09 | 5901.31 | N/A | 8873.37 | 170.64 | 5866.58 | N/A | 8259.98 | 397.11 | N/A | N/A | N/A | N/A
GEN-2023-136 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Solar | Vinita Junction - Hockerville 138 kV | 774704 | 1 | 774700 | 1647.83 | 25.94 | 1314.5 | N/A | 1540.48 | 24.25 | 1314.5 | N/A | 1540.48 | 24.25 | 1315.08 | N/A | 1550.73 | 35.24 | 1317.13 | N/A | 1636.87 | 16.46 | 1314.55 | N/A | 1540.48 | 24.25 | N/A | N/A | N/A | N/A
GEN-2023-136 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Storage | Vinita Junction - Hockerville 138 kV | 774707 | 1 | 774700 | 1647.83 | 20.41 | 1314.5 | N/A | 1540.48 | N/A | 1314.5 | N/A | 1540.48 | N/A | 1315.08 | N/A | 1550.73 | N/A | 1317.13 | N/A | 1636.87 | 32.38 | 1314.55 | N/A | 1540.48 | N/A | N/A | N/A | N/A | N/A
GEN-2023-137 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Storage | North Boston - Bann 138 kV Line Tap | 774724 | 1 | 762431 | 3074.97 | 20.5 | 2428.76 | N/A | 2686.14 | N/A | 2428.76 | N/A | 2686.14 | N/A | 2428.83 | N/A | 2686.22 | N/A | 2432.86 | N/A | 3009.97 | 20.07 | 2429.27 | N/A | 2686.46 | N/A | N/A | N/A | N/A | N/A
GEN-2023-138 | DIS-23-1 | 04 SOUTHEAST | GRDA | 250 | ER/NR | Wind | GRDA1 - Tonece7 345 kV Line | 774744 | 1 | 774740 | 9786.43 | 391.46 | 8555.03 | 114.07 | 9552.11 | 382.08 | 8555.11 | 114.07 | 9552.11 | 382.08 | 8566.72 | 114.22 | 9607.19 | 554.88 | 8620.44 | 68.96 | 9717.72 | 77.74 | 8556.56 | 114.09 | 9552.38 | 382.1 | N/A | N/A | N/A | N/A
GEN-2023-138 | DIS-23-1 | 04 SOUTHEAST | GRDA | 250 | ER/NR | Wind | GRDA1 - Tonece7 345 kV Line | 774747 | 1 | 774740 | 9786.43 | 391.46 | 8555.03 | 114.07 | 9552.11 | 382.08 | 8555.11 | 114.07 | 9552.11 | 382.08 | 8566.72 | 114.22 | 9607.19 | 554.88 | 8620.44 | 68.96 | 9717.72 | 77.74 | 8556.56 | 114.09 | 9552.38 | 382.1 | N/A | N/A | N/A | N/A
GEN-2023-142 | DIS-23-1 | 05 SOUTHWEST | SPS | 275 | ER/NR | Solar | Plant X 230 kV Substation | 774824 | 1 | 525481 | 11903.14 | 210.57 | 9318.32 | N/A | 11054.92 | 195.57 | 9318.46 | N/A | 11054.99 | 195.57 | 9330.69 | N/A | 11064.55 | 282.63 | 9357.79 | N/A | 11073.79 | 195.9 | 9708.33 | N/A | 11817.82 | 83.62 | N/A | N/A | N/A | N/A
GEN-2023-142 | DIS-23-1 | 05 SOUTHWEST | SPS | 275 | ER/NR | Solar | Plant X 230 kV Substation | 774827 | 1 | 525481 | 11903.14 | 222.61 | 9318.32 | N/A | 11054.92 | 206.74 | 9318.46 | N/A | 11054.99 | 206.74 | 9330.69 | N/A | 11064.55 | 298.78 | 9357.79 | N/A | 11073.79 | 207.1 | 9708.33 | N/A | 11817.82 | 88.4 | N/A | N/A | N/A | N/A
GEN-2023-143 | DIS-23-1 | 05 SOUTHWEST | SPS | 200 | ER/NR | Storage | Plant X 230 kV Substation | 774844 | 1 | 525481 | 11903.14 | 59.52 | 9318.32 | N/A | 11054.92 | N/A | 9318.46 | N/A | 11054.99 | N/A | 9330.69 | N/A | 11064.55 | N/A | 9357.79 | N/A | 11073.79 | N/A | 9708.33 | N/A | 11817.82 | 59.09 | N/A | N/A | N/A | N/A
GEN-2023-144 | DIS-23-1 | 01 NORTH | WAPA | 265 | ER/NR | Solar | Bismarck - Jamestown 230 kV | 774864 | 1 | 774860 | 2300.56 | 42.13 | 2017.16 | N/A | 2300.33 | 16.85 | 1973.51 | N/A | 2253.3 | 41.26 | 1973.42 | N/A | 2253.27 | 59.58 | 1973.41 | N/A | 2253.27 | 41.26 | 1973.41 | N/A | 2253.27 | 41.26 | N/A | N/A | N/A | N/A
GEN-2023-144 | DIS-23-1 | 01 NORTH | WAPA | 265 | ER/NR | Solar | Bismarck - Jamestown 230 kV | 774867 | 1 | 774860 | 2300.56 | 44.76 | 2017.16 | N/A | 2300.33 | 17.9 | 1973.51 | N/A | 2253.3 | 43.85 | 1973.42 | N/A | 2253.27 | 63.31 | 1973.41 | N/A | 2253.27 | 43.84 | 1973.41 | N/A | 2253.27 | 43.84 | N/A | N/A | N/A | N/A
GEN-2023-145 | DIS-23-1 | 04 SOUTHEAST | SWPA | 180 | ER/NR | Solar | Eufaula - Gore 161 kV Line | 774884 | 1 | 774880 | 2494.9 | 34.65 | 2100.78 | N/A | 2471.57 | 34.33 | 2100.78 | N/A | 2471.57 | 34.33 | 2101.05 | N/A | 2471.79 | 49.57 | 2108.51 | N/A | 2493.58 | 13.85 | 2101.04 | N/A | 2471.65 | 34.33 | N/A | N/A | N/A | N/A
GEN-2023-146 | DIS-23-1 | 02 NEBRASKA | NPPD | 125 | ER/NR | Solar | Seward 115 kV Substation | 774904 | 1 | 640340 | 1603.82 | 32.08 | 1441.64 | N/A | 1580.69 | 31.61 | 1450.43 | N/A | 1597.1 | 12.78 | 1443.58 | N/A | 1581.61 | 45.67 | 1441.12 | N/A | 1580.51 | 31.61 | 1441.11 | N/A | 1580.51 | 31.61 | N/A | N/A | N/A | N/A
GEN-2023-147 | DIS-23-1 | 02 NEBRASKA | NPPD | 85 | ER/NR | Wind | Victory Hill - Crawford 115 kV Line | 774924 | 1 | 774920 | 615.97 | 36.23 | 603.79 | 11.84 | 614.51 | 36.15 | 601.8 | 7.08 | 611.75 | 7.2 | 601.41 | 11.79 | 610.37 | 51.84 | 601.3 | 11.79 | 610.29 | 35.9 | 601.3 | 11.79 | 610.29 | 35.9 | N/A | N/A | N/A | N/A
GEN-2023-148 | DIS-23-1 | 04 SOUTHEAST | AEP | 110 | ER/NR | Solar | Russell - Lake Pauline 138 kV Line | 774944 | 1 | 774940 | 800.69 | 16.16 | 609.97 | N/A | 725.37 | 14.33 | 609.97 | N/A | 725.37 | 14.33 | 610.06 | N/A | 725.43 | 20.69 | 614.97 | N/A | 794.89 | 10.75 | 610.41 | N/A | 725.9 | 14.34 | N/A | N/A | N/A | N/A
GEN-2023-148 | DIS-23-1 | 04 SOUTHEAST | AEP | 110 | ER/NR | Storage | Russell - Lake Pauline 138 kV Line | 774947 | 1 | 774940 | 800.69 | 13.25 | 609.97 | N/A | 725.37 | N/A | 609.97 | N/A | 725.37 | N/A | 610.06 | N/A | 725.43 | N/A | 614.97 | N/A | 794.89 | 22.03 | 610.41 | N/A | 725.9 | N/A | N/A | N/A | N/A | N/A
GEN-2023-149 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Storage | LaCygne - Stilwell 345 kV Line | 774964 | 1 | 774960 | 15383.03 | 102.55 | 8446.24 | N/A | 13624.56 | N/A | 8450.33 | N/A | 13625.69 | N/A | 8591.62 | N/A | 15302.53 | 102.02 | 8481.74 | N/A | 13641.78 | N/A | 8448.58 | N/A | 13625.12 | N/A | N/A | N/A | N/A | N/A
GEN-2023-149 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Storage | LaCygne - Stilwell 345 kV Line | 774967 | 1 | 774960 | 15383.03 | 102.55 | 8446.24 | N/A | 13624.56 | N/A | 8450.33 | N/A | 13625.69 | N/A | 8591.62 | N/A | 15302.53 | 102.02 | 8481.74 | N/A | 13641.78 | N/A | 8448.58 | N/A | 13625.12 | N/A | N/A | N/A | N/A | N/A
GEN-2023-150 | DIS-23-1 | 04 SOUTHEAST | OGE | 150 | ER/NR | Solar | Gracemont 138 kV Substation | 774984 | 1 | 515802 | 10539.37 | 175.66 | 7299.7 | N/A | 9743.24 | 162.39 | 7299.79 | N/A | 9743.27 | 162.39 | 7310.66 | N/A | 9751.92 | 234.68 | 7628.18 | N/A | 10223.27 | 68.16 | 7365.44 | N/A | 9885.6 | 164.76 | N/A | N/A | N/A | N/A
GEN-2023-151 | DIS-23-1 | 04 SOUTHEAST | AEP | 100 | ER/NR | Solar | South Nashville - South Murfreesboro 138kV | 775004 | 1 | 775000 | 981.1 | 40.34 | 815.27 | N/A | 938.29 | 38.58 | 815.27 | N/A | 938.29 | 38.58 | 815.27 | N/A | 938.3 | 55.71 | 815.57 | N/A | 978.02 | 25.75 | 815.3 | N/A | 938.31 | 38.58 | N/A | N/A | N/A | N/A
GEN-2023-151 | DIS-23-1 | 04 SOUTHEAST | AEP | 100 | ER/NR | Solar | South Nashville - South Murfreesboro 138kV | 775007 | 1 | 775000 | 981.1 | 40.34 | 815.27 | N/A | 938.29 | 38.58 | 815.27 | N/A | 938.29 | 38.58 | 815.27 | N/A | 938.3 | 55.71 | 815.57 | N/A | 978.02 | 25.75 | 815.3 | N/A | 938.31 | 38.58 | N/A | N/A | N/A | N/A
GEN-2023-151 | DIS-23-1 | 04 SOUTHEAST | AEP | 100 | ER/NR | Storage | South Nashville - South Murfreesboro 138kV | 775009 | 1 | 775000 | 981.1 | 25.5 | 815.27 | N/A | 938.29 | N/A | 815.27 | N/A | 938.29 | N/A | 815.27 | N/A | 938.3 | N/A | 815.57 | N/A | 978.02 | 40.69 | 815.3 | N/A | 938.31 | N/A | N/A | N/A | N/A | N/A
GEN-2023-152 | DIS-23-1 | 04 SOUTHEAST | AEP | 140 | ER/NR | Solar | Allen NG4 138 kV Substation | 775024 | 1 | 510863 | 1623.92 | 29 | 1320.31 | N/A | 1571.52 | 28.06 | 1320.31 | N/A | 1571.52 | 28.06 | 1320.46 | N/A | 1571.69 | 40.53 | 1328.39 | N/A | 1616.82 | 11.55 | 1321.11 | N/A | 1572.2 | 28.07 | N/A | N/A | N/A | N/A
GEN-2023-153 | DIS-23-1 | 02 NEBRASKA | Tri-State | 120 | ER/NR | Solar | Grant 115 kV Substation | 775044 | 1 | 659800 | 1680.41 | 58.01 | 1261.22 | N/A | 1447.53 | 28.34 | 1265.7 | N/A | 1676.6 | 31.54 | 1264.47 | N/A | 1451.43 | 41.04 | 1260.92 | N/A | 1447.27 | 28.34 | 1260.94 | N/A | 1447.28 | 28.34 | N/A | N/A | N/A | N/A
GEN-2023-153 | DIS-23-1 | 02 NEBRASKA | Tri-State | 120 | ER/NR | Storage | Grant 115 kV Substation | 775047 | 1 | 659800 | 1680.41 | 18.46 | 1261.22 | N/A | 1447.53 | N/A | 1265.7 | N/A | 1676.6 | 25.09 | 1264.47 | N/A | 1451.43 | N/A | 1260.92 | N/A | 1447.27 | N/A | 1260.94 | N/A | 1447.28 | N/A | N/A | N/A | N/A | N/A
GEN-2023-154 | DIS-23-1 | 01 NORTH | WAPA | 200 | ER/NR | Solar | Fort Thompson - Huron 230 kV Tap | 775064 | 1 | 589324 | 3253.54 | 40.67 | 2981.28 | N/A | 3248.67 | 16.24 | 2767 | N/A | 3046.66 | 38.08 | 2759.51 | N/A | 3041.47 | 54.9 | 2759.15 | N/A | 3041.35 | 38.02 | 2759.15 | N/A | 3041.35 | 38.02 | N/A | N/A | N/A | N/A
GEN-2023-155 | DIS-23-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Solar | Longwood - Lieberman 138 kV | 775084 | 1 | 775080 | 4485.38 | 109.98 | 2857.97 | N/A | 4344.88 | 106.53 | 2857.97 | N/A | 4344.88 | 106.53 | 2858 | N/A | 4344.89 | 153.83 | 2859.57 | N/A | 4468.59 | 43.83 | 2858.17 | N/A | 4344.91 | 106.53 | N/A | N/A | N/A | N/A
GEN-2023-155 | DIS-23-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Solar | Longwood - Lieberman 138 kV | 775087 | 1 | 775080 | 4485.38 | 114.38 | 2857.97 | N/A | 4344.88 | 110.79 | 2857.97 | N/A | 4344.88 | 110.79 | 2858 | N/A | 4344.89 | 159.98 | 2859.57 | N/A | 4468.59 | 45.58 | 2858.17 | N/A | 4344.91 | 110.79 | N/A | N/A | N/A | N/A
GEN-2023-156 | DIS-23-1 | 04 SOUTHEAST | WFEC | 200 | ER/NR | Solar | Between South Wilson - Ringling 138 kV Line | 775104 | 1 | 775100 | 1270.29 | 28.65 | 878.78 | N/A | 1068.39 | 13.6 | 878.78 | N/A | 1068.39 | 13.6 | 878.89 | N/A | 1068.58 | 19.63 | 883.21 | N/A | 1263.26 | 15.19 | 879.55 | N/A | 1069.39 | 13.61 | N/A | N/A | N/A | N/A
GEN-2023-156 | DIS-23-1 | 04 SOUTHEAST | WFEC | 200 | ER/NR | Storage | Between South Wilson - Ringling 138 kV Line | 775107 | 1 | 775100 | 1270.29 | 8.16 | 878.78 | N/A | 1068.39 | N/A | 878.78 | N/A | 1068.39 | N/A | 878.89 | N/A | 1068.58 | N/A | 883.21 | N/A | 1263.26 | 10.81 | 879.55 | N/A | 1069.39 | N/A | N/A | N/A | N/A | N/A
GEN-2023-157 | DIS-23-1 | 03 CENTRAL | Evergy | 150 | ER/NR | Storage | Bucyrus 161 kV Substation | 775124 | 1 | 543057 | 5976.83 | 39.85 | 4691.74 | N/A | 5705.81 | N/A | 4693.77 | N/A | 5706.31 | N/A | 4747.89 | N/A | 5948.33 | 39.66 | 4696.5 | N/A | 5706.56 | N/A | 4692.05 | N/A | 5705.84 | N/A | N/A | N/A | N/A | N/A
GEN-2023-158 | DIS-23-1 | 05 SOUTHWEST | SPS | 335 | ER/NR | Solar | Needmore - Yoakum 230 kV Line | 775144 | 1 | 775140 | 4504.11 | 66.42 | 3620.51 | N/A | 4114.65 | 60.68 | 3620.52 | N/A | 4114.66 | 60.68 | 3622.08 | N/A | 4115.61 | 87.64 | 3626.32 | N/A | 4116.87 | 60.71 | 3748.28 | N/A | 4488.15 | 26.48 | N/A | N/A | N/A | N/A
GEN-2023-158 | DIS-23-1 | 05 SOUTHWEST | SPS | 335 | ER/NR | Solar | Needmore - Yoakum 230 kV Line | 775147 | 1 | 775140 | 4504.11 | 68.05 | 3620.51 | N/A | 4114.65 | 62.16 | 3620.52 | N/A | 4114.66 | 62.16 | 3622.08 | N/A | 4115.61 | 89.78 | 3626.32 | N/A | 4116.87 | 62.2 | 3748.28 | N/A | 4488.15 | 27.12 | N/A | N/A | N/A | N/A
GEN-2023-159 | DIS-23-1 | 05 SOUTHWEST | SPS | 200 | ER/NR | Storage | Needmore - Yoakum 230 kV Line | 775164 | 1 | 775140 | 4504.11 | 22.52 | 3620.51 | N/A | 4114.65 | N/A | 3620.52 | N/A | 4114.66 | N/A | 3622.08 | N/A | 4115.61 | N/A | 3626.32 | N/A | 4116.87 | N/A | 3748.28 | N/A | 4488.15 | 22.44 | N/A | N/A | N/A | N/A
GEN-2023-160 | DIS-23-1 | 01 NORTH | BEPC | 300 | ER/NR | Solar | Belfield - Rhame 230 kV Line | 775184 | 1 | 775180 | 2509.79 | 35.97 | 1906.58 | N/A | 2497.83 | 23.45 | 1819.05 | N/A | 2236.62 | 32.06 | 1818.9 | N/A | 2236.54 | 46.29 | 1818.89 | N/A | 2236.54 | 32.06 | 1818.89 | N/A | 2236.54 | 32.06 | N/A | N/A | N/A | N/A
GEN-2023-160 | DIS-23-1 | 01 NORTH | BEPC | 300 | ER/NR | Storage | Belfield - Rhame 230 kV Line | 775187 | 1 | 775180 | 2509.79 | 35.23 | 1906.58 | N/A | 2497.83 | 57.42 | 1819.05 | N/A | 2236.62 | N/A | 1818.9 | N/A | 2236.54 | N/A | 1818.89 | N/A | 2236.54 | N/A | 1818.89 | N/A | 2236.54 | N/A | N/A | N/A | N/A | N/A
GEN-2023-160 | DIS-23-1 | 01 NORTH | BEPC | 300 | ER/NR | Solar | Belfield - Rhame 230 kV Line | 775190 | 1 | 775180 | 2509.79 | 35.97 | 1906.58 | N/A | 2497.83 | 23.45 | 1819.05 | N/A | 2236.62 | 32.06 | 1818.9 | N/A | 2236.54 | 46.29 | 1818.89 | N/A | 2236.54 | 32.06 | 1818.89 | N/A | 2236.54 | 32.06 | N/A | N/A | N/A | N/A
GEN-2023-160 | DIS-23-1 | 01 NORTH | BEPC | 300 | ER/NR | Storage | Belfield - Rhame 230 kV Line | 775193 | 1 | 775180 | 2509.79 | 35.23 | 1906.58 | N/A | 2497.83 | 57.42 | 1819.05 | N/A | 2236.62 | N/A | 1818.9 | N/A | 2236.54 | N/A | 1818.89 | N/A | 2236.54 | N/A | 1818.89 | N/A | 2236.54 | N/A | N/A | N/A | N/A | N/A
GEN-2023-161 | DIS-23-1 | 04 SOUTHEAST | OGE | 74.9 | ER/NR | Storage | Roman Nose 138 kV Substation | 775204 | 1 | 514823 | 1582.73 | 21.13 | 1418 | N/A | 1458.76 | N/A | 1418 | N/A | 1458.77 | N/A | 1418.71 | N/A | 1459.19 | N/A | 1437.8 | N/A | 1566.62 | 20.92 | 1419.27 | N/A | 1459.69 | N/A | N/A | N/A | N/A | N/A
GEN-2023-162 | DIS-23-1 | 04 SOUTHEAST | AEP | 100 | ER/NR | Solar | Grove - Jay 138 kV Line | 775224 | 1 | 775220 | 1316.84 | 32.07 | 1082.77 | N/A | 1231.95 | 28.14 | 1082.78 | N/A | 1231.95 | 28.14 | 1082.98 | N/A | 1237.86 | 40.83 | 1084.21 | N/A | 1310.73 | 20.63 | 1082.8 | N/A | 1231.96 | 28.14 | N/A | N/A | N/A | N/A
GEN-2023-162 | DIS-23-1 | 04 SOUTHEAST | AEP | 100 | ER/NR | Storage | Grove - Jay 138 kV Line | 775227 | 1 | 775220 | 1316.84 | 22.34 | 1082.77 | N/A | 1231.95 | N/A | 1082.78 | N/A | 1231.95 | N/A | 1082.98 | N/A | 1237.86 | N/A | 1084.21 | N/A | 1310.73 | 35.93 | 1082.8 | N/A | 1231.96 | N/A | N/A | N/A | N/A | N/A
GEN-2023-163 | DIS-23-1 | 03 CENTRAL | Evergy | 150 | ER/NR | Solar | Midway - Avenue City 161 kV | 775244 | 1 | 775240 | 2006.26 | 33.44 | 1787.02 | N/A | 1978.75 | 32.98 | 1788.96 | N/A | 1983.17 | 33.05 | 1810.96 | N/A | 1999.93 | 13.33 | 1786.73 | N/A | 1978.63 | 32.98 | 1786.66 | N/A | 1978.63 | 32.98 | N/A | N/A | N/A | N/A
GEN-2023-164 | DIS-23-1 | 04 SOUTHEAST | OGE | 210 | ER/NR | Storage | Gracemont 345 kV Substation | 775264 | 1 | 515800 | 16704.02 | 79.54 | 11596.52 | N/A | 14085.73 | N/A | 11596.81 | N/A | 14085.86 | N/A | 11631.71 | N/A | 14121.05 | N/A | 12677.48 | N/A | 15794.67 | 75.21 | 11827.43 | N/A | 14745.02 | N/A | N/A | N/A | N/A | N/A
GEN-2023-165 | DIS-23-1 | 04 SOUTHEAST | OGE | 210 | ER/NR | Storage | Gracemont 345 kV Substation | 775284 | 1 | 515800 | 16704.02 | 79.54 | 11596.52 | N/A | 14085.73 | N/A | 11596.81 | N/A | 14085.86 | N/A | 11631.71 | N/A | 14121.05 | N/A | 12677.48 | N/A | 15794.67 | 75.21 | 11827.43 | N/A | 14745.02 | N/A | N/A | N/A | N/A | N/A
GEN-2023-166 | DIS-23-1 | 04 SOUTHEAST | OGE | 150 | ER | Storage | 84th Street - Tennessee Tap 138 kV Line | 775304 | 1 | 775300 | 6622.63 | 44.15 | 5568.38 | N/A | 6247.1 | N/A | 5568.43 | N/A | 6247.11 | N/A | 5575.63 | N/A | 6250.7 | N/A | 5725.3 | N/A | 6559.41 | 43.73 | 5584.66 | N/A | 6261.61 | N/A | N/A | N/A | N/A | N/A
GEN-2023-167 | DIS-23-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Storage | Washington Park 138 kV Substation | 775324 | 1 | 515156 | 5574.23 | 22.3 | 4674.6 | N/A | 5178.19 | N/A | 4674.63 | N/A | 5178.2 | N/A | 4679.19 | N/A | 5180.29 | N/A | 4774.81 | N/A | 5519.35 | 22.08 | 4686.04 | N/A | 5187.98 | N/A | N/A | N/A | N/A | N/A
GEN-2023-168 | DIS-23-1 | 04 SOUTHEAST | OGE | 175 | ER/NR | Storage | Classen 138 kV Substation | 775344 | 1 | 514922 | 8069.74 | 46.11 | 6527.61 | N/A | 7551.39 | N/A | 6527.67 | N/A | 7551.41 | N/A | 6536.76 | N/A | 7556.09 | N/A | 6722.17 | N/A | 7958.68 | 45.48 | 6550.45 | N/A | 7573.55 | N/A | N/A | N/A | N/A | N/A
GEN-2023-169 | DIS-23-1 | 03 CENTRAL | Evergy | 125 | ER/NR | Storage | Missouri City - Liberty South 161 kV Line | 775364 | 1 | 775360 | 5670.39 | 45.36 | 4398.67 | N/A | 5198.3 | N/A | 4401.59 | N/A | 5199.63 | N/A | 4460.19 | N/A | 5570.63 | 44.57 | 4400.24 | N/A | 5198.39 | N/A | 4398.62 | N/A | 5198.29 | N/A | N/A | N/A | N/A | N/A
GEN-2023-170 | DIS-23-1 | 03 CENTRAL | Evergy | 150 | ER | Storage | Salisbury 161 kV Substation | 775384 | 1 | 543062 | 3505.9 | 23.37 | 2950.6 | N/A | 3191.23 | N/A | 2950.91 | N/A | 3191.31 | N/A | 2993.03 | N/A | 3485.62 | 23.24 | 2950.81 | N/A | 3191.26 | N/A | 2950.58 | N/A | 3191.23 | N/A | N/A | N/A | N/A | N/A
GEN-2023-171 | DIS-23-1 | 03 CENTRAL | INDN | 150 | ER/NR | Storage | Sub M 161 kV Substation | 775404 | 1 | 548814 | 6107.28 | 40.72 | 4431.99 | N/A | 5578.43 | N/A | 4434.92 | N/A | 5579.57 | N/A | 4496.44 | N/A | 5973.58 | 39.82 | 4433.85 | N/A | 5578.55 | N/A | 4431.99 | N/A | 5578.43 | N/A | N/A | N/A | N/A | N/A
GEN-2023-172 | DIS-23-1 | 03 CENTRAL | SUNC | 200 | ER/NR | Wind | Holcomb 345 kV | 775424 | 1 | 531449 | 14605.02 | 730.25 | 12040.43 | 200.67 | 13507.26 | 675.36 | 12048.31 | 200.81 | 13519.14 | 675.96 | 12425.17 | 124.25 | 14196.96 | 141.97 | 12184.85 | 203.08 | 13653.28 | 682.66 | 12329.64 | 205.49 | 13765.97 | 688.3 | N/A | N/A | N/A | N/A
GEN-2023-172 | DIS-23-1 | 03 CENTRAL | SUNC | 200 | ER/NR | Wind | Holcomb 345 kV | 775427 | 1 | 531449 | 14605.02 | 730.25 | 12040.43 | 200.67 | 13507.26 | 675.36 | 12048.31 | 200.81 | 13519.14 | 675.96 | 12425.17 | 124.25 | 14196.96 | 141.97 | 12184.85 | 203.08 | 13653.28 | 682.66 | 12329.64 | 205.49 | 13765.97 | 688.3 | N/A | N/A | N/A | N/A
GEN-2023-173 | DIS-23-1 | 03 CENTRAL | SUNC | 100 | ER/NR | Wind | Holcomb 345 kV | 775444 | 1 | 531449 | 14605.02 | 730.25 | 12040.43 | 200.67 | 13507.26 | 675.36 | 12048.31 | 200.81 | 13519.14 | 675.96 | 12425.17 | 124.25 | 14196.96 | 141.97 | 12184.85 | 203.08 | 13653.28 | 682.66 | 12329.64 | 205.49 | 13765.97 | 688.3 | N/A | N/A | N/A | N/A
GEN-2023-174 | DIS-23-1 | 04 SOUTHEAST | WFEC | 150 | ER | Storage | Paoli West 138 kV Substation | 775464 | 1 | 521023 | 2395.04 | 15.97 | 2086.57 | N/A | 2198.87 | N/A | 2086.58 | N/A | 2198.87 | N/A | 2087.24 | N/A | 2199.25 | N/A | 2105.38 | N/A | 2376.48 | 15.84 | 2089.8 | N/A | 2202.11 | N/A | N/A | N/A | N/A | N/A
GEN-2023-175 | DIS-23-1 | 03 CENTRAL | SUNC | 200 | ER/NR | Storage | Hickock 115 kV Substation | 775484 | 1 | 531378 | 1163.15 | 5.82 | 876.11 | N/A | 893.11 | N/A | 876.14 | N/A | 893.15 | N/A | 880.55 | N/A | 1160.1 | 5.8 | 876.75 | N/A | 893.57 | N/A | 877.52 | N/A | 894.13 | N/A | N/A | N/A | N/A | N/A
GEN-2023-176 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Wind | Plant X 230 kV Substation | 775504 | 1 | 525481 | 11903.14 | 393.1 | 9318.32 | 102.58 | 11054.92 | 365.09 | 9318.46 | 102.58 | 11054.99 | 365.09 | 9330.69 | 102.72 | 11064.55 | 527.61 | 9357.79 | 103.01 | 11073.79 | 365.71 | 9708.33 | 64.12 | 11817.82 | 78.06 | N/A | N/A | N/A | N/A
GEN-2023-176 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Wind | Plant X 230 kV Substation | 775507 | 1 | 525481 | 11903.14 | 400.51 | 9318.32 | 104.51 | 11054.92 | 371.97 | 9318.46 | 104.51 | 11054.99 | 371.97 | 9330.69 | 104.65 | 11064.55 | 537.56 | 9357.79 | 104.96 | 11073.79 | 372.6 | 9708.33 | 65.33 | 11817.82 | 79.53 | N/A | N/A | N/A | N/A
GEN-2023-177 | DIS-23-1 | 04 SOUTHEAST | OGE | 200 | ER/NR | Solar | Paoli - Seminole 138 kV line tap | 775524 | 1 | 775520 | 2188.16 | 53.65 | 1930.66 | N/A | 2153.17 | 52.79 | 1930.66 | N/A | 2153.17 | 52.79 | 1931.09 | N/A | 2153.65 | 76.25 | 1952.55 | N/A | 2177.62 | 21.36 | 1933.04 | N/A | 2156.04 | 52.86 | N/A | N/A | N/A | N/A
GEN-2023-177 | DIS-23-1 | 04 SOUTHEAST | OGE | 200 | ER/NR | Solar | Paoli - Seminole 138 kV line tap | 775527 | 1 | 775520 | 2188.16 | 55.8 | 1930.66 | N/A | 2153.17 | 54.91 | 1930.66 | N/A | 2153.17 | 54.91 | 1931.09 | N/A | 2153.65 | 79.3 | 1952.55 | N/A | 2177.62 | 22.21 | 1933.04 | N/A | 2156.04 | 54.98 | N/A | N/A | N/A | N/A
GEN-2023-178 | DIS-23-1 | 05 SOUTHWEST | SPS | 200 | ER/NR | Solar | Roosevelt 230kV Substation | 775544 | 1 | 524909 | 5942.03 | 148.55 | 4655.13 | N/A | 5217.59 | 130.44 | 4655.15 | N/A | 5217.6 | 130.44 | 4657.76 | N/A | 5219.27 | 188.41 | 4664.4 | N/A | 5221.29 | 130.53 | 4928.06 | N/A | 5906.77 | 59.07 | N/A | N/A | N/A | N/A
GEN-2023-178 | DIS-23-1 | 05 SOUTHWEST | SPS | 200 | ER/NR | Solar | Roosevelt 230kV Substation | 775547 | 1 | 524909 | 5942.03 | 148.55 | 4655.13 | N/A | 5217.59 | 130.44 | 4655.15 | N/A | 5217.6 | 130.44 | 4657.76 | N/A | 5219.27 | 188.41 | 4664.4 | N/A | 5221.29 | 130.53 | 4928.06 | N/A | 5906.77 | 59.07 | N/A | N/A | N/A | N/A
GEN-2023-180 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Solar | Hackett - N Huntington 161 kV Line Tap | 775584 | 1 | 775580 | 2532.88 | 42.21 | 2239.01 | N/A | 2481.66 | 41.36 | 2239.02 | N/A | 2481.66 | 41.36 | 2239.11 | N/A | 2481.73 | 59.72 | 2241.3 | N/A | 2532.61 | 16.88 | 2239.1 | N/A | 2481.68 | 41.36 | N/A | N/A | N/A | N/A
GEN-2023-181 | DIS-23-1 | 01 NORTH | BEPC | 100 | ER/NR | Storage | Groton - Leland Olds 345 kV Line | 775604 | 1 | 762544 | 4021.64 | 40.22 | 3654.57 | N/A | 4019.7 | 40.2 | 3415.48 | N/A | 3658.52 | N/A | 3414.45 | N/A | 3658.17 | N/A | 3414.41 | N/A | 3658.16 | N/A | 3414.41 | N/A | 3658.16 | N/A | N/A | N/A | N/A | N/A
GEN-2023-182 | DIS-23-1 | 01 NORTH | BEPC | 300 | ER/NR | Wind | Groton - Leland Olds 345 kV Line | 775624 | 1 | 762544 | 4021.64 | 134.05 | 3654.57 | 24.36 | 4019.7 | 26.8 | 3415.48 | 37.95 | 3658.52 | 121.95 | 3414.45 | 37.94 | 3658.17 | 176.07 | 3414.41 | 37.94 | 3658.16 | 121.94 | 3414.41 | 37.94 | 3658.16 | 121.94 | N/A | N/A | N/A | N/A
GEN-2023-182 | DIS-23-1 | 01 NORTH | BEPC | 300 | ER/NR | Wind | Groton - Leland Olds 345 kV Line | 775627 | 1 | 762544 | 4021.64 | 134.05 | 3654.57 | 24.36 | 4019.7 | 26.8 | 3415.48 | 37.95 | 3658.52 | 121.95 | 3414.45 | 37.94 | 3658.17 | 176.07 | 3414.41 | 37.94 | 3658.16 | 121.94 | 3414.41 | 37.94 | 3658.16 | 121.94 | N/A | N/A | N/A | N/A
GEN-2023-183 | DIS-23-1 | 05 SOUTHWEST | SPS | 217 | ER/NR | Thermal | Tuco 345kV | 775644 | 1 | 525832 | 19538.06 | 90.04 | 13210.06 | N/A | 17478.57 | N/A | 13210.36 | N/A | 17478.7 | N/A | 13239.25 | N/A | 17502.58 | N/A | 13448.47 | N/A | 17675.78 | N/A | 13868.31 | N/A | 18605.06 | N/A | N/A | N/A | N/A | N/A
GEN-2023-184 | DIS-23-1 | 05 SOUTHWEST | SPS | 200 | ER/NR | Solar | Phantom 115 kV Substation | 775664 | 1 | 528013 | 3189.58 | 39.87 | 2542.11 | N/A | 2981.49 | 37.27 | 2542.12 | N/A | 2981.49 | 37.27 | 2542.7 | N/A | 2981.72 | 53.82 | 2545.58 | N/A | 2982.62 | 37.28 | 2593.32 | N/A | 3058.18 | 15.29 | N/A | N/A | N/A | N/A
GEN-2023-185 | DIS-23-1 | 05 SOUTHWEST | SPS | 150 | ER/NR | Solar | Nichols - Amarillo 230 kV line tap | 775684 | 1 | 775680 | 5750.42 | 95.84 | 4647.91 | N/A | 5591.47 | 93.19 | 4648.04 | N/A | 5591.54 | 93.19 | 4658.86 | N/A | 5601.63 | 134.8 | 4666.35 | N/A | 5603.45 | 93.39 | 4704.1 | N/A | 5695.96 | 37.97 | N/A | N/A | N/A | N/A
GEN-2023-186 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Solar | Murray Gill 138 kV Substation | 775704 | 1 | 533044 | 6461.27 | 112.43 | 5211.45 | N/A | 5918.22 | 61.8 | 5211.87 | N/A | 5918.39 | 61.8 | 5331.01 | N/A | 6400.55 | 63.75 | 5277.23 | N/A | 5964.87 | 62.29 | 5221.91 | N/A | 5923.74 | 61.86 | N/A | N/A | N/A | N/A
GEN-2023-186 | DIS-23-1 | 03 CENTRAL | Evergy | 200 | ER/NR | Storage | Murray Gill 138 kV Substation | 775707 | 1 | 533044 | 6461.27 | 45.33 | 5211.45 | N/A | 5918.22 | N/A | 5211.87 | N/A | 5918.39 | N/A | 5331.01 | N/A | 6400.55 | 64.26 | 5277.23 | N/A | 5964.87 | N/A | 5221.91 | N/A | 5923.74 | N/A | N/A | N/A | N/A | N/A
GEN-2023-188 | DIS-23-1 | 05 SOUTHWEST | AEP | 160 | ER/NR | Solar | Oklaunion - Lawton 345 kV Line | 775744 | 1 | 775740 | 11729.81 | 334.07 | 8009.39 | N/A | 9174.64 | 261.3 | 8009.51 | N/A | 9174.68 | 261.3 | 8023.04 | N/A | 9191.05 | 377.97 | 8463.81 | N/A | 9843.21 | 280.34 | 8349.81 | N/A | 10709.11 | 133.86 | N/A | N/A | N/A | N/A
GEN-2023-188 | DIS-23-1 | 05 SOUTHWEST | AEP | 160 | ER/NR | Storage | Oklaunion - Lawton 345 kV Line | 775747 | 1 | 775740 | 11729.81 | 133.63 | 8009.39 | N/A | 9174.64 | N/A | 8009.51 | N/A | 9174.68 | N/A | 8023.04 | N/A | 9191.05 | N/A | 8463.81 | N/A | 9843.21 | N/A | 8349.81 | N/A | 10709.11 | 133.86 | N/A | N/A | N/A | N/A
GEN-2023-189 | DIS-23-1 | 02 NEBRASKA | LES | 200 | ER/NR | Storage | NW 68th - Holdrege 345 kV Substation | 775764 | 1 | 650114 | 11157.12 | 55.79 | 8566.33 | N/A | 10052.38 | N/A | 8881.55 | N/A | 10738.03 | 53.69 | 8649.28 | N/A | 10102.62 | N/A | 8551.18 | N/A | 10046.21 | N/A | 8550.81 | N/A | 10046.19 | N/A | N/A | N/A | N/A | N/A
GEN-2023-191 | DIS-23-1 | 03 CENTRAL | EDE | 74 | ER/NR | Storage | Hockersville 138 kV Substation | 775804 | 1 | 547486 | 3498.59 | 47.28 | 2676.28 | N/A | 3305.6 | N/A | 2676.3 | N/A | 3305.6 | N/A | 2679.39 | N/A | 3449.24 | 46.61 | 2686.45 | N/A | 3344.55 | N/A | 2676.44 | N/A | 3305.62 | N/A | N/A | N/A | N/A | N/A
GEN-2023-193 | DIS-23-1 | 04 SOUTHEAST | AEP | 175 | ER/NR | Solar | Pirkey - Whitney 138 kV Line | 775844 | 1 | 775840 | 5270.9 | 105.42 | 3261.46 | N/A | 4989.44 | 59.68 | 3261.46 | N/A | 4989.44 | 59.68 | 3261.51 | N/A | 4989.46 | 86.18 | 3264.62 | N/A | 5172.03 | 59.11 | 3261.85 | N/A | 4989.53 | 59.68 | N/A | N/A | N/A | N/A
GEN-2023-193 | DIS-23-1 | 04 SOUTHEAST | AEP | 175 | ER/NR | Storage | Pirkey - Whitney 138 kV Line | 775847 | 1 | 775840 | 5270.9 | 42.17 | 3261.46 | N/A | 4989.44 | N/A | 3261.46 | N/A | 4989.44 | N/A | 3261.51 | N/A | 4989.46 | N/A | 3264.62 | N/A | 5172.03 | 59.11 | 3261.85 | N/A | 4989.53 | N/A | N/A | N/A | N/A | N/A
GEN-2023-194 | DIS-23-1 | 03 CENTRAL | EDE | 225 | ER/NR | Solar | Riverton - Neosho 161 kV Line Tap | 775864 | 1 | 764310 | 5789.47 | 64.33 | 3778.51 | N/A | 5277.3 | 58.64 | 3778.57 | N/A | 5277.31 | 58.64 | 3788.12 | N/A | 5733.86 | 25.48 | 3801.47 | N/A | 5303.81 | 58.93 | 3778.86 | N/A | 5277.35 | 58.64 | N/A | N/A | N/A | N/A
GEN-2023-195 | DIS-23-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Roosevelt - Tolk 230 kV line tap | 775884 | 1 | 775880 | 4751.01 | 89.43 | 3880.06 | N/A | 4349.79 | 81.88 | 3880.08 | N/A | 4349.8 | 81.88 | 3881.98 | N/A | 4351.03 | 118.26 | 3886.72 | N/A | 4352.46 | 81.93 | 3995.4 | N/A | 4734.64 | 35.65 | N/A | N/A | N/A | N/A
GEN-2023-195 | DIS-23-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Solar | Roosevelt - Tolk 230 kV line tap | 775887 | 1 | 775880 | 4751.01 | 101.35 | 3880.06 | N/A | 4349.79 | 92.79 | 3880.08 | N/A | 4349.8 | 92.79 | 3881.98 | N/A | 4351.03 | 134.03 | 3886.72 | N/A | 4352.46 | 92.85 | 3995.4 | N/A | 4734.64 | 40.4 | N/A | N/A | N/A | N/A
GEN-2023-196 | DIS-23-1 | 05 SOUTHWEST | SPS | 150 | ER/NR | Storage | Roosevelt - Tolk 230 kV line tap | 775904 | 1 | 775880 | 4751.01 | 31.67 | 3880.06 | N/A | 4349.79 | N/A | 3880.08 | N/A | 4349.8 | N/A | 3881.98 | N/A | 4351.03 | N/A | 3886.72 | N/A | 4352.46 | N/A | 3995.4 | N/A | 4734.64 | 31.56 | N/A | N/A | N/A | N/A
GEN-2023-197 | DIS-23-1 | 02 NEBRASKA | OPPD | 150 | ER/NR | Solar | Sub 1366 - Sub 1258 161 kV | 775924 | 1 | 775920 | 2152.34 | 35.87 | 1878.77 | N/A | 2126.39 | 35.44 | 1882.81 | N/A | 2141.55 | 14.28 | 1882.58 | N/A | 2127.8 | 51.21 | 1878.29 | N/A | 2126.3 | 35.44 | 1878.26 | N/A | 2126.3 | 35.44 | N/A | N/A | N/A | N/A
GEN-2023-198 | DIS-23-1 | 01 NORTH | WAPA | 250 | ER/NR | Solar | Hebron 230 kV Substation | 775944 | 1 | 652468 | 2530.91 | 44.99 | 2218 | N/A | 2525.82 | 17.96 | 2192.05 | N/A | 2480.37 | 44.09 | 2191.95 | N/A | 2480.34 | 63.67 | 2191.94 | N/A | 2480.34 | 44.09 | 2191.94 | N/A | 2480.34 | 44.09 | N/A | N/A | N/A | N/A
GEN-2023-198 | DIS-23-1 | 01 NORTH | WAPA | 250 | ER/NR | Solar | Hebron 230 kV Substation | 775947 | 1 | 652468 | 2530.91 | 57.85 | 2218 | N/A | 2525.82 | 23.09 | 2192.05 | N/A | 2480.37 | 56.69 | 2191.95 | N/A | 2480.34 | 81.86 | 2191.94 | N/A | 2480.34 | 56.69 | 2191.94 | N/A | 2480.34 | 56.69 | N/A | N/A | N/A | N/A
GEN-2023-199 | DIS-23-1 | 02 NEBRASKA | NPPD | 250 | ER/NR | Solar | Twin Church 230 kV Substation | 775964 | 1 | 640386 | 3839.95 | 54.26 | 3233.06 | N/A | 3598.86 | 30.95 | 3257.21 | N/A | 3822.36 | 30.78 | 3212.35 | N/A | 3584.53 | 44.51 | 3210.08 | N/A | 3583.8 | 30.82 | 3210.07 | N/A | 3583.8 | 30.82 | N/A | N/A | N/A | N/A
GEN-2023-199 | DIS-23-1 | 02 NEBRASKA | NPPD | 250 | ER/NR | Storage | Twin Church 230 kV Substation | 775967 | 1 | 640386 | 3839.95 | 21.42 | 3233.06 | N/A | 3598.86 | N/A | 3257.21 | N/A | 3822.36 | 30.38 | 3212.35 | N/A | 3584.53 | N/A | 3210.08 | N/A | 3583.8 | N/A | 3210.07 | N/A | 3583.8 | N/A | N/A | N/A | N/A | N/A
GEN-2023-200 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Solar | Caney River 345 kV Substation | 775984 | 1 | 532780 | 6462.76 | 107.71 | 5638.4 | N/A | 6192.73 | 103.21 | 5638.72 | N/A | 6192.81 | 103.21 | 5748.12 | N/A | 6426.94 | 42.85 | 5694.16 | N/A | 6229.47 | 103.82 | 5643.31 | N/A | 6194.84 | 103.25 | N/A | N/A | N/A | N/A
GEN-2023-200 | DIS-23-1 | 03 CENTRAL | Evergy | 300 | ER/NR | Solar | Caney River 345 kV Substation | 775987 | 1 | 532780 | 6462.76 | 107.71 | 5638.4 | N/A | 6192.73 | 103.21 | 5638.72 | N/A | 6192.81 | 103.21 | 5748.12 | N/A | 6426.94 | 42.85 | 5694.16 | N/A | 6229.47 | 103.82 | 5643.31 | N/A | 6194.84 | 103.25 | N/A | N/A | N/A | N/A
GEN-2023-201 | DIS-23-1 | 05 SOUTHWEST | NEET | 300 | ER/NR | Solar | Crossroads - Hobbs 345 kV Line | 776004 | 1 | 776000 | 11199.41 | 193.77 | 6777.15 | N/A | 8873.98 | 138.02 | 6777.2 | N/A | 8874 | 138.02 | 6781.87 | N/A | 8876.74 | 199.35 | 6805.88 | N/A | 8888.06 | 138.24 | 7367.03 | N/A | 9903.98 | 108.58 | N/A | N/A | N/A | N/A
GEN-2023-201 | DIS-23-1 | 05 SOUTHWEST | NEET | 300 | ER/NR | Storage | Crossroads - Hobbs 345 kV Line | 776007 | 1 | 776000 | 11199.41 | 122.28 | 6777.15 | N/A | 8873.98 | N/A | 6777.2 | N/A | 8874 | N/A | 6781.87 | N/A | 8876.74 | N/A | 6805.88 | N/A | 8888.06 | N/A | 7367.03 | N/A | 9903.98 | 171.3 | N/A | N/A | N/A | N/A
GEN-2023-201 | DIS-23-1 | 05 SOUTHWEST | NEET | 300 | ER/NR | Solar | Crossroads - Hobbs 345 kV Line | 776010 | 1 | 776000 | 11199.41 | 189.74 | 6777.15 | N/A | 8873.98 | 135.14 | 6777.2 | N/A | 8874 | 135.14 | 6781.87 | N/A | 8876.74 | 195.2 | 6805.88 | N/A | 8888.06 | 135.36 | 7367.03 | N/A | 9903.98 | 106.32 | N/A | N/A | N/A | N/A
GEN-2023-201 | DIS-23-1 | 05 SOUTHWEST | NEET | 300 | ER/NR | Storage | Crossroads - Hobbs 345 kV Line | 776013 | 1 | 776000 | 11199.41 | 122.28 | 6777.15 | N/A | 8873.98 | N/A | 6777.2 | N/A | 8874 | N/A | 6781.87 | N/A | 8876.74 | N/A | 6805.88 | N/A | 8888.06 | N/A | 7367.03 | N/A | 9903.98 | 171.3 | N/A | N/A | N/A | N/A
GEN-2023-202 | DIS-23-1 | 02 NEBRASKA | OPPD | 150 | ER/NR | Solar | Tekamah - Raun 161 kV Line | 776024 | 1 | 762069 | 2459.98 | 41 | 2135.17 | N/A | 2355.16 | 39.25 | 2227.79 | N/A | 2453.09 | 16.35 | 2134.38 | N/A | 2354.41 | 56.66 | 2132.34 | N/A | 2353.86 | 39.23 | 2132.33 | N/A | 2353.86 | 39.23 | N/A | N/A | N/A | N/A
GEN-2023-203 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Hobbs - Ink Basin 230 kV Transmission Line | 776044 | 1 | 776040 | 4592.37 | 79.46 | 3524.58 | N/A | 4269.87 | 66.41 | 3524.59 | N/A | 4269.88 | 66.41 | 3525.35 | N/A | 4270.14 | 95.9 | 3528.98 | N/A | 4271.11 | 66.43 | 3577.87 | N/A | 4504.89 | 49.39 | N/A | N/A | N/A | N/A
GEN-2023-203 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Storage | Hobbs - Ink Basin 230 kV Transmission Line | 776047 | 1 | 776040 | 4592.37 | 50.14 | 3524.58 | N/A | 4269.87 | N/A | 3524.59 | N/A | 4269.88 | N/A | 3525.35 | N/A | 4270.14 | N/A | 3528.98 | N/A | 4271.11 | N/A | 3577.87 | N/A | 4504.89 | 77.92 | N/A | N/A | N/A | N/A
GEN-2023-203 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Hobbs - Ink Basin 230 kV Transmission Line | 776050 | 1 | 776040 | 4592.37 | 77.8 | 3524.58 | N/A | 4269.87 | 65.03 | 3524.59 | N/A | 4269.88 | 65.03 | 3525.35 | N/A | 4270.14 | 93.9 | 3528.98 | N/A | 4271.11 | 65.04 | 3577.87 | N/A | 4504.89 | 48.36 | N/A | N/A | N/A | N/A
GEN-2023-203 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Storage | Hobbs - Ink Basin 230 kV Transmission Line | 776053 | 1 | 776040 | 4592.37 | 50.14 | 3524.58 | N/A | 4269.87 | N/A | 3524.59 | N/A | 4269.88 | N/A | 3525.35 | N/A | 4270.14 | N/A | 3528.98 | N/A | 4271.11 | N/A | 3577.87 | N/A | 4504.89 | 77.92 | N/A | N/A | N/A | N/A
GEN-2023-204 | DIS-23-1 | 04 SOUTHEAST | AEP | 953 | ER/NR | Thermal | Welsh-Lydia 345kV Line | 776064 | 1 | 776060 | 10038.86 | 21.07 | 5720 | N/A | 8546.07 | N/A | 5720.01 | N/A | 8546.07 | N/A | 5720.49 | N/A | 8546.93 | N/A | 5748.29 | N/A | 8979.96 | N/A | 5723.53 | N/A | 8549.83 | N/A | N/A | N/A | N/A | N/A
GEN-2023-204 | DIS-23-1 | 04 SOUTHEAST | AEP | 953 | ER/NR | Thermal | Welsh-Lydia 345kV Line | 776067 | 1 | 776060 | 10038.86 | 21.07 | 5720 | N/A | 8546.07 | N/A | 5720.01 | N/A | 8546.07 | N/A | 5720.49 | N/A | 8546.93 | N/A | 5748.29 | N/A | 8979.96 | N/A | 5723.53 | N/A | 8549.83 | N/A | N/A | N/A | N/A | N/A
GEN-2023-205 | DIS-23-1 | 04 SOUTHEAST | AEP | 180 | ER/NR | Solar | McAlester City - Weleetka 138 kV line | 776084 | 1 | 776080 | 2407.31 | 33.43 | 2128.66 | N/A | 2370.52 | 32.92 | 2128.66 | N/A | 2370.52 | 32.92 | 2129.08 | N/A | 2370.76 | 47.54 | 2160.5 | N/A | 2401.06 | 13.34 | 2129.48 | N/A | 2370.99 | 32.93 | N/A | N/A | N/A | N/A
GEN-2023-206 | DIS-23-1 | 04 SOUTHEAST | OGE | 50 | ER/NR | Storage | Battlefield BESS 161 kV Substation | 769584 | X | 515349 | 5108.75 | 102.17 | 4378.92 | N/A | 4788.64 | N/A | 4378.92 | N/A | 4788.64 | N/A | 4379.35 | N/A | 4788.97 | N/A | 4388.83 | N/A | 5107.27 | 102.15 | 4379.31 | N/A | 4788.74 | N/A | N/A | N/A | N/A | N/A
GEN-2023-207 | DIS-23-1 | 04 SOUTHEAST | WFEC | 50 | ER | Storage | Colbert 138 kV Substation | 769704 | X | 520860 | 1638.08 | 32.76 | 1209.16 | N/A | 1285.35 | N/A | 1209.17 | N/A | 1285.35 | N/A | 1209.32 | N/A | 1286.03 | N/A | 1219.11 | N/A | 1621.09 | 32.42 | 1210.4 | N/A | 1287.02 | N/A | N/A | N/A | N/A | N/A
GEN-2023-208 | DIS-23-1 | 05 SOUTHWEST | SPS | 200 | ER | Storage | Rolling Hills 115 kV | 776144 | 1 | 524007 | 4261.76 | 21.31 | 3594.15 | N/A | 4001.26 | N/A | 3594.23 | N/A | 4001.3 | N/A | 3601.2 | N/A | 4007.74 | N/A | 3605.57 | N/A | 4008.64 | N/A | 3628.57 | N/A | 4228.67 | 21.14 | N/A | N/A | N/A | N/A
GEN-2023-209 | DIS-23-1 | 05 SOUTHWEST | SPS | 125 | ER/NR | Storage | Amarillo South 115 kV | 776164 | 1 | 524414 | 3690.88 | 29.53 | 3165.29 | N/A | 3483.76 | N/A | 3165.35 | N/A | 3483.79 | N/A | 3170.34 | N/A | 3488.03 | N/A | 3173.79 | N/A | 3488.73 | N/A | 3194.2 | N/A | 3649.17 | 29.19 | N/A | N/A | N/A | N/A
GEN-2023-210 | DIS-23-1 | 04 SOUTHEAST | WFEC | 191 | ER/NR | Solar | Prague - Chernicky 138 kV Line | 776184 | 1 | 776180 | 1484.48 | 19.43 | 1267.97 | N/A | 1475.46 | 19.31 | 1267.97 | N/A | 1475.46 | 19.31 | 1268.22 | N/A | 1475.57 | 27.89 | 1275.07 | N/A | 1481.75 | 7.76 | 1268.52 | N/A | 1475.83 | 19.32 | N/A | N/A | N/A | N/A
GEN-2023-211 | DIS-23-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Wind | Ranch Road 345 kV Substation | 776204 | 1 | 515576 | 8987.83 | 311.03 | 7097.91 | 69.1 | 7970.06 | 232.78 | 7098.14 | 69.11 | 7970.12 | 232.79 | 7218.51 | 70.28 | 8172.19 | 344.64 | 7657.5 | 44.73 | 8765.41 | 102.07 | 7107.4 | 69.2 | 7974.43 | 232.91 | N/A | N/A | N/A | N/A
GEN-2023-211 | DIS-23-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Solar | Ranch Road 345 kV Substation | 776207 | 1 | 515576 | 8987.83 | 244.97 | 7097.91 | N/A | 7970.06 | 183.34 | 7098.14 | N/A | 7970.12 | 183.34 | 7218.51 | N/A | 8172.19 | 271.44 | 7657.5 | N/A | 8765.41 | 160.78 | 7107.4 | N/A | 7974.43 | 183.44 | N/A | N/A | N/A | N/A
GEN-2023-211 | DIS-23-1 | 04 SOUTHEAST | OGE | 250 | ER/NR | Storage | Ranch Road 345 kV Substation | 776210 | 1 | 515576 | 8987.83 | 48.74 | 7097.91 | N/A | 7970.06 | N/A | 7098.14 | N/A | 7970.12 | N/A | 7218.51 | N/A | 8172.19 | N/A | 7657.5 | N/A | 8765.41 | 79.97 | 7107.4 | N/A | 7974.43 | N/A | N/A | N/A | N/A | N/A
GEN-2023-212 | DIS-23-1 | 04 SOUTHEAST | AEP | 400 | ER/NR | Solar | Northwest Texarkana - Valliant 345 kV Line | 776224 | 1 | 776220 | 7284.49 | 41.49 | 5036.47 | N/A | 6555.44 | 37.34 | 5036.48 | N/A | 6555.44 | 37.34 | 5036.98 | N/A | 6556.34 | 53.92 | 5066.07 | N/A | 7026.58 | 22.25 | 5040.16 | N/A | 6559.39 | 37.36 | N/A | N/A | N/A | N/A
GEN-2023-212 | DIS-23-1 | 04 SOUTHEAST | AEP | 400 | ER/NR | Storage | Northwest Texarkana - Valliant 345 kV Line | 776227 | 1 | 776220 | 7284.49 | 62.24 | 5036.47 | N/A | 6555.44 | N/A | 5036.48 | N/A | 6555.44 | N/A | 5036.98 | N/A | 6556.34 | N/A | 5066.07 | N/A | 7026.58 | 83.44 | 5040.16 | N/A | 6559.39 | N/A | N/A | N/A | N/A | N/A
GEN-2023-213 | DIS-23-1 | 04 SOUTHEAST | AEP | 100 | ER/NR | Storage | Chamber Springs 161 kV Substation | 776244 | 1 | 506944 | 6719.35 | 67.19 | 5802.31 | N/A | 6333.2 | N/A | 5802.34 | N/A | 6333.2 | N/A | 5806.15 | N/A | 6366.47 | N/A | 5843.71 | N/A | 6681.61 | 66.82 | 5803.2 | N/A | 6333.37 | N/A | N/A | N/A | N/A | N/A
GEN-2023-214 | DIS-23-1 | 04 SOUTHEAST | OGE | 100 | ER/NR | Storage | Brown 138 kV Substation | 776264 | 1 | 515157 | 2898.71 | 28.99 | 2018.37 | N/A | 2239.86 | N/A | 2018.38 | N/A | 2239.87 | N/A | 2018.81 | N/A | 2241.93 | N/A | 2046.24 | N/A | 2838.6 | 28.39 | 2021.82 | N/A | 2244.96 | N/A | N/A | N/A | N/A | N/A
GEN-2023-216 | DIS-23-1 | 02 NEBRASKA | NPPD | 200 | ER/NR | Wind | Turtle Creek 345 kV Substation | 776304 | 1 | 640588 | 10000.65 | 250.02 | 8182.69 | 68.19 | 8759.21 | 218.98 | 9151.8 | 45.76 | 9939.35 | 49.7 | 8145.42 | 67.88 | 8734.58 | 315.31 | 8121.44 | 67.68 | 8722.87 | 218.07 | 8121.38 | 67.68 | 8722.87 | 218.07 | N/A | N/A | N/A | N/A
GEN-2023-217 | DIS-23-1 | 02 NEBRASKA | NPPD | 200 | ER/NR | Wind | Turtle Creek 345 kV Substation | 776324 | 1 | 640588 | 10000.65 | 250.02 | 8182.69 | 68.19 | 8759.21 | 218.98 | 9151.8 | 45.76 | 9939.35 | 49.7 | 8145.42 | 67.88 | 8734.58 | 315.31 | 8121.44 | 67.68 | 8722.87 | 218.07 | 8121.38 | 67.68 | 8722.87 | 218.07 | N/A | N/A | N/A | N/A
GEN-2023-218 | DIS-23-1 | 02 NEBRASKA | NPPD | 200 | ER/NR | Wind | Turtle Creek 345 kV Substation | 776344 | 1 | 640588 | 10000.65 | 250.02 | 8182.69 | 68.19 | 8759.21 | 218.98 | 9151.8 | 45.76 | 9939.35 | 49.7 | 8145.42 | 67.88 | 8734.58 | 315.31 | 8121.44 | 67.68 | 8722.87 | 218.07 | 8121.38 | 67.68 | 8722.87 | 218.07 | N/A | N/A | N/A | N/A
GEN-2023-219 | DIS-23-1 | 03 CENTRAL | Evergy | 125 | ER/NR | Solar | Reading - Osage Jct 115 kV Line | 776364 | 1 | 776360 | 1341.33 | 26.83 | 1162.13 | N/A | 1325.36 | 26.51 | 1162.24 | N/A | 1325.39 | 26.51 | 1169.19 | N/A | 1340.86 | 10.73 | 1162.57 | N/A | 1325.46 | 26.51 | 1162.25 | N/A | 1325.38 | 26.51 | N/A | N/A | N/A | N/A
GEN-2023-220 | DIS-23-1 | 03 CENTRAL | Evergy | 250 | ER/NR | Solar | Emporia Energy Center - Swissvale 345 kV Line | 776384 | 1 | 776380 | 9048.05 | 90.48 | 6374.18 | N/A | 8792.17 | 87.92 | 6377 | N/A | 8792.95 | 87.93 | 6620.71 | N/A | 9023.6 | 36.09 | 6387.49 | N/A | 8796.7 | 87.97 | 6377.71 | N/A | 8793.34 | 87.93 | N/A | N/A | N/A | N/A
GEN-2023-221 | DIS-23-1 | 03 CENTRAL | Evergy | 250 | ER/NR | Solar | Emporia Energy Center - Swissvale 345 kV Line | 776404 | 1 | 776400 | 9121.21 | 91.21 | 6396.9 | N/A | 8861.1 | 88.61 | 6399.71 | N/A | 8861.88 | 88.62 | 6646.26 | N/A | 9096.84 | 36.39 | 6410.42 | N/A | 8865.8 | 88.66 | 6400.51 | N/A | 8862.32 | 88.62 | N/A | N/A | N/A | N/A
GEN-2023-222 | DIS-23-1 | 02 NEBRASKA | NPPD | 478 | ER/NR | Thermal | New Beatrice Power Station 345 kV | 776424 | 1 | 771999 | 2319.07 | 9.7 | 1279.5 | N/A | 1622.97 | N/A | 1299.72 | N/A | 1638.91 | N/A | 1281.58 | N/A | 1624.25 | N/A | 1279.35 | N/A | 1622.94 | N/A | 1279.33 | N/A | 1622.94 | N/A | N/A | N/A | N/A | N/A
GEN-2023-222 | DIS-23-1 | 02 NEBRASKA | NPPD | 478 | ER/NR | Thermal | New Beatrice Power Station 345 kV | 776427 | 1 | 771999 | 2319.07 | 9.7 | 1279.5 | N/A | 1622.97 | N/A | 1299.72 | N/A | 1638.91 | N/A | 1281.58 | N/A | 1624.25 | N/A | 1279.35 | N/A | 1622.94 | N/A | 1279.33 | N/A | 1622.94 | N/A | N/A | N/A | N/A | N/A
GEN-2023-223 | DIS-23-1 | 02 NEBRASKA | NPPD | 239 | ER/NR | Thermal | New Beatrice Power Station 345 kV | 776444 | 1 | 771999 | 2319.07 | 9.7 | 1279.5 | N/A | 1622.97 | N/A | 1299.72 | N/A | 1638.91 | N/A | 1281.58 | N/A | 1624.25 | N/A | 1279.35 | N/A | 1622.94 | N/A | 1279.33 | N/A | 1622.94 | N/A | N/A | N/A | N/A | N/A
GEN-2023-224 | DIS-23-1 | 02 NEBRASKA | NPPD | 478 | ER | Thermal | Olive Creek 345 kV Substation | 776464 | 1 | 640590 | 15077.32 | 63.09 | 10499.64 | N/A | 12913.62 | N/A | 11082.88 | N/A | 13966.33 | N/A | 10664.07 | N/A | 13031.14 | N/A | 10482.89 | N/A | 12906.9 | N/A | 10482.21 | N/A | 12906.86 | N/A | N/A | N/A | N/A | N/A
GEN-2023-224 | DIS-23-1 | 02 NEBRASKA | NPPD | 478 | ER | Thermal | Olive Creek 345 kV Substation | 776467 | 1 | 640590 | 15077.32 | 63.09 | 10499.64 | N/A | 12913.62 | N/A | 11082.88 | N/A | 13966.33 | N/A | 10664.07 | N/A | 13031.14 | N/A | 10482.89 | N/A | 12906.9 | N/A | 10482.21 | N/A | 12906.86 | N/A | N/A | N/A | N/A | N/A
GEN-2023-225 | DIS-23-1 | 02 NEBRASKA | NPPD | 217 | ER | Thermal | Olive Creek 345 kV Substation | 776484 | 1 | 640590 | 15077.32 | 138.96 | 10499.64 | N/A | 12913.62 | N/A | 11082.88 | N/A | 13966.33 | N/A | 10664.07 | N/A | 13031.14 | N/A | 10482.89 | N/A | 12906.9 | N/A | 10482.21 | N/A | 12906.86 | N/A | N/A | N/A | N/A | N/A
GEN-2023-225 | DIS-23-1 | 02 NEBRASKA | NPPD | 217 | ER | Thermal | Olive Creek 345 kV Substation | 776487 | 1 | 640590 | 15077.32 | 138.96 | 10499.64 | N/A | 12913.62 | N/A | 11082.88 | N/A | 13966.33 | N/A | 10664.07 | N/A | 13031.14 | N/A | 10482.89 | N/A | 12906.9 | N/A | 10482.21 | N/A | 12906.86 | N/A | N/A | N/A | N/A | N/A
GEN-2023-226 | DIS-23-1 | 03 CENTRAL | EDE | 200 | ER/NR | Storage | La Russell 161 kV Substation | 776504 | 1 | 547479 | 5590.77 | 55.91 | 3937.64 | N/A | 4358.15 | N/A | 3937.68 | N/A | 4358.15 | N/A | 3942.17 | N/A | 4917.12 | 49.17 | 3959.1 | N/A | 4371.57 | N/A | 3937.81 | N/A | 4358.16 | N/A | N/A | N/A | N/A | N/A
GEN-2023-226 | DIS-23-1 | 03 CENTRAL | EDE | 200 | ER/NR | Storage | La Russell 161 kV Substation | 776507 | 1 | 547479 | 5590.77 | 55.91 | 3937.64 | N/A | 4358.15 | N/A | 3937.68 | N/A | 4358.15 | N/A | 3942.17 | N/A | 4917.12 | 49.17 | 3959.1 | N/A | 4371.57 | N/A | 3937.81 | N/A | 4358.16 | N/A | N/A | N/A | N/A | N/A
GEN-2023-227 | DIS-23-1 | 04 SOUTHEAST | AEP | 200 | ER/NR | Storage | Petty to Chapel 138 kV Line | 776524 | 1 | 776520 | 2245.63 | 11.23 | 1670.48 | N/A | 1878.66 | N/A | 1670.48 | N/A | 1878.66 | N/A | 1670.49 | N/A | 1878.67 | N/A | 1671.35 | N/A | 2160.79 | 10.8 | 1670.59 | N/A | 1878.69 | N/A | N/A | N/A | N/A | N/A
GEN-2023-228 | DIS-23-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Storage | Tuco-Okalunion 345 kV line | 776544 | 1 | 762467 | 7828.59 | 62.63 | 6321.39 | N/A | 6902.6 | N/A | 6321.47 | N/A | 6902.63 | N/A | 6329.59 | N/A | 6909.13 | N/A | 6462.7 | N/A | 7052.28 | N/A | 6488.46 | N/A | 7625.57 | 61 | N/A | N/A | N/A | N/A
GEN-2023-228 | DIS-23-1 | 05 SOUTHWEST | SPS | 250 | ER/NR | Storage | Tuco-Okalunion 345 kV line | 776547 | 1 | 762467 | 7828.59 | 62.63 | 6321.39 | N/A | 6902.6 | N/A | 6321.47 | N/A | 6902.63 | N/A | 6329.59 | N/A | 6909.13 | N/A | 6462.7 | N/A | 7052.28 | N/A | 6488.46 | N/A | 7625.57 | 61 | N/A | N/A | N/A | N/A
GEN-2023-229 | DIS-23-1 | 04 SOUTHEAST | AEP | 230 | ER/NR | Wind | Southwestern Power Station 138 kV Substation (SWS4) | 776564 | 1 | 511477 | 9361.44 | 366.31 | 5789.54 | 75.51 | 8810.21 | 344.74 | 5789.59 | 75.52 | 8810.23 | 344.74 | 5795.74 | 75.6 | 8814.81 | 498.04 | 6008.65 | 47.02 | 9160.75 | 71.69 | 5827.5 | 76.01 | 8886.85 | 347.74 | N/A | N/A | N/A | N/A
GEN-2023-229 | DIS-23-1 | 04 SOUTHEAST | AEP | 230 | ER/NR | Wind | Southwestern Power Station 138 kV Substation (SWS4) | 776567 | 1 | 511477 | 9361.44 | 457.91 | 5789.54 | 94.4 | 8810.21 | 430.94 | 5789.59 | 94.4 | 8810.23 | 430.94 | 5795.74 | 94.5 | 8814.81 | 622.56 | 6008.65 | 58.78 | 9160.75 | 89.62 | 5827.5 | 95.02 | 8886.85 | 434.69 | N/A | N/A | N/A | N/A
GEN-2023-230 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Solar | Red Pointe 138 kV Substation | 776584 | 1 | 507751 | 3042.89 | 72.8 | 2111.44 | N/A | 2818.47 | 67.43 | 2111.44 | N/A | 2818.47 | 67.43 | 2111.45 | N/A | 2818.47 | 97.36 | 2112.18 | N/A | 3036.79 | 30.45 | 2111.53 | N/A | 2818.48 | 67.43 | N/A | N/A | N/A | N/A
GEN-2023-230 | DIS-23-1 | 04 SOUTHEAST | AEP | 150 | ER/NR | Storage | Red Pointe 138 kV Substation | 776587 | 1 | 507751 | 3042.89 | 57.77 | 2111.44 | N/A | 2818.47 | N/A | 2111.44 | N/A | 2818.47 | N/A | 2111.45 | N/A | 2818.47 | N/A | 2112.18 | N/A | 3036.79 | 60.41 | 2111.53 | N/A | 2818.48 | N/A | N/A | N/A | N/A | N/A
GEN-2023-231 | DIS-23-1 | 03 CENTRAL | Evergy | 310 | ER | Solar | Neosho - LaCynge 345 kV Line | 776604 | 1 | 776600 | 8913.2 | 177.78 | 6872.5 | N/A | 8021.47 | 122.19 | 6873.19 | N/A | 8021.56 | 122.19 | 6974.8 | N/A | 8805.89 | 104.34 | 6999.89 | N/A | 8124.61 | 123.76 | 6874.62 | N/A | 8021.93 | 122.2 | N/A | N/A | N/A | N/A
GEN-2023-231 | DIS-23-1 | 03 CENTRAL | Evergy | 310 | ER | Solar | Neosho - LaCynge 345 kV Line | 776607 | 1 | 776600 | 8913.2 | 177.78 | 6872.5 | N/A | 8021.47 | 122.19 | 6873.19 | N/A | 8021.56 | 122.19 | 6974.8 | N/A | 8805.89 | 104.34 | 6999.89 | N/A | 8124.61 | 123.76 | 6874.62 | N/A | 8021.93 | 122.2 | N/A | N/A | N/A | N/A
GEN-2023-231 | DIS-23-1 | 03 CENTRAL | Evergy | 310 | ER | Storage | Neosho - LaCynge 345 kV Line | 776609 | 1 | 776600 | 8913.2 | 83.85 | 6872.5 | N/A | 8021.47 | N/A | 6873.19 | N/A | 8021.56 | N/A | 6974.8 | N/A | 8805.89 | 123.03 | 6999.89 | N/A | 8124.61 | N/A | 6874.62 | N/A | 8021.93 | N/A | N/A | N/A | N/A | N/A
GEN-2023-231 | DIS-23-1 | 03 CENTRAL | Evergy | 310 | ER | Storage | Neosho - LaCynge 345 kV Line | 776611 | 1 | 776600 | 8913.2 | 86.18 | 6872.5 | N/A | 8021.47 | N/A | 6873.19 | N/A | 8021.56 | N/A | 6974.8 | N/A | 8805.89 | 126.45 | 6999.89 | N/A | 8124.61 | N/A | 6874.62 | N/A | 8021.93 | N/A | N/A | N/A | N/A | N/A
GEN-2023-235 | DIS-23-1 | 04 SOUTHEAST | AEP | 250 | ER/NR | Storage | Chamber Springs 345 kV Substation | 776684 | 1 | 506945 | 6294.55 | 25.18 | 5404.64 | N/A | 5904.76 | N/A | 5404.67 | N/A | 5904.76 | N/A | 5408.04 | N/A | 5925.89 | N/A | 5448.58 | N/A | 6269.33 | 25.08 | 5405.72 | N/A | 5905 | N/A | N/A | N/A | N/A | N/A
GEN-2023-236 | DIS-23-1 | 05 SOUTHWEST | SPS | 400 | ER/NR | Solar | Hobbs - Yoakum 345 kV | 776703 | 1 | 776700 | 10822.94 | 239 | 6482.38 | N/A | 8496.16 | 187.62 | 6482.43 | N/A | 8496.17 | 187.62 | 6486.32 | N/A | 8498.28 | 270.97 | 6506.27 | N/A | 8507.06 | 187.86 | 6882.58 | N/A | 9263.54 | 81.83 | N/A | N/A | N/A | N/A
GEN-2023-236 | DIS-23-1 | 05 SOUTHWEST | SPS | 400 | ER/NR | Solar | Hobbs - Yoakum 345 kV | 776705 | 1 | 776700 | 10822.94 | 298.75 | 6482.38 | N/A | 8496.16 | 234.52 | 6482.43 | N/A | 8496.17 | 234.52 | 6486.32 | N/A | 8498.28 | 338.71 | 6506.27 | N/A | 8507.06 | 234.82 | 6882.58 | N/A | 9263.54 | 102.28 | N/A | N/A | N/A | N/A
GEN-2023-236 | DIS-23-1 | 05 SOUTHWEST | SPS | 400 | ER/NR | Solar | Hobbs - Yoakum 345 kV | 776707 | 1 | 776700 | 10822.94 | 239 | 6482.38 | N/A | 8496.16 | 187.62 | 6482.43 | N/A | 8496.17 | 187.62 | 6486.32 | N/A | 8498.28 | 270.97 | 6506.27 | N/A | 8507.06 | 187.86 | 6882.58 | N/A | 9263.54 | 81.83 | N/A | N/A | N/A | N/A
GEN-2023-236 | DIS-23-1 | 05 SOUTHWEST | SPS | 400 | ER/NR | Solar | Hobbs - Yoakum 345 kV | 776709 | 1 | 776700 | 10822.94 | 325.91 | 6482.38 | N/A | 8496.16 | 255.85 | 6482.43 | N/A | 8496.17 | 255.85 | 6486.32 | N/A | 8498.28 | 369.51 | 6506.27 | N/A | 8507.06 | 256.18 | 6882.58 | N/A | 9263.54 | 111.58 | N/A | N/A | N/A | N/A
GEN-2023-237 | DIS-23-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Wind | Crawfish Draw 345 kV Substation | 776724 | 1 | 560022 | 19825.06 | 793 | 13466.73 | 179.56 | 17729.12 | 709.16 | 13467.04 | 179.56 | 17729.25 | 709.17 | 13497.2 | 179.96 | 17754.31 | 1025.43 | 13718.14 | 182.91 | 17938.74 | 717.55 | 14148.32 | 113.19 | 18889.52 | 151.12 | N/A | N/A | N/A | N/A
GEN-2023-237 | DIS-23-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Wind | Crawfish Draw 345 kV Substation | 776727 | 1 | 560022 | 19825.06 | 793 | 13466.73 | 179.56 | 17729.12 | 709.16 | 13467.04 | 179.56 | 17729.25 | 709.17 | 13497.2 | 179.96 | 17754.31 | 1025.43 | 13718.14 | 182.91 | 17938.74 | 717.55 | 14148.32 | 113.19 | 18889.52 | 151.12 | N/A | N/A | N/A | N/A
GEN-2023-237 | DIS-23-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Wind | Crawfish Draw 345 kV Substation | 776730 | 1 | 560022 | 19825.06 | 793 | 13466.73 | 179.56 | 17729.12 | 709.16 | 13467.04 | 179.56 | 17729.25 | 709.17 | 13497.2 | 179.96 | 17754.31 | 1025.43 | 13718.14 | 182.91 | 17938.74 | 717.55 | 14148.32 | 113.19 | 18889.52 | 151.12 | N/A | N/A | N/A | N/A
GEN-2023-237 | DIS-23-1 | 05 SOUTHWEST | SPS | 500 | ER/NR | Wind | Crawfish Draw 345 kV Substation | 776733 | 1 | 560022 | 19825.06 | 793 | 13466.73 | 179.56 | 17729.12 | 709.16 | 13467.04 | 179.56 | 17729.25 | 709.17 | 13497.2 | 179.96 | 17754.31 | 1025.43 | 13718.14 | 182.91 | 17938.74 | 717.55 | 14148.32 | 113.19 | 18889.52 | 151.12 | N/A | N/A | N/A | N/A
GEN-2023-238 | DIS-23-1 | 05 SOUTHWEST | SPS | 280 | ER/NR | Solar | Potter County 345 kV Substation | 776743 | 1 | 523961 | 18975.41 | 330.37 | 14562.82 | N/A | 17475.43 | 304.26 | 14565.29 | N/A | 17477.92 | 304.3 | 14770.96 | N/A | 17838.12 | 448.44 | 14861.83 | N/A | 17798.05 | 309.88 | 15211.8 | N/A | 18246.63 | 127.07 | N/A | N/A | N/A | N/A
GEN-2023-238 | DIS-23-1 | 05 SOUTHWEST | SPS | 280 | ER/NR | Solar | Potter County 345 kV Substation | 776745 | 1 | 523961 | 18975.41 | 347.76 | 14562.82 | N/A | 17475.43 | 320.27 | 14565.29 | N/A | 17477.92 | 320.32 | 14770.96 | N/A | 17838.12 | 472.05 | 14861.83 | N/A | 17798.05 | 326.19 | 15211.8 | N/A | 18246.63 | 133.76 | N/A | N/A | N/A | N/A
GEN-2023-239 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Rolling Hills 230 kV Substation | 776763 | 1 | 524010 | 11390.6 | 187.58 | 8359.3 | N/A | 10874.96 | 179.09 | 8359.82 | N/A | 10875.38 | 179.1 | 8403.66 | N/A | 10935.89 | 260.04 | 8428.17 | N/A | 10936.89 | 180.11 | 8546.01 | N/A | 11223.16 | 73.93 | N/A | N/A | N/A | N/A
GEN-2023-239 | DIS-23-1 | 05 SOUTHWEST | SPS | 300 | ER/NR | Solar | Rolling Hills 230 kV Substation | 776765 | 1 | 524010 | 11390.6 | 192.16 | 8359.3 | N/A | 10874.96 | 183.46 | 8359.82 | N/A | 10875.38 | 183.47 | 8403.66 | N/A | 10935.89 | 266.39 | 8428.17 | N/A | 10936.89 | 184.51 | 8546.01 | N/A | 11223.16 | 75.73 | N/A | N/A | N/A | N/A
GEN-2023-240 | DIS-23-1 | 05 SOUTHWEST | SPS | 550 | ER/NR | Solar | Tolk 345 kV Substation | 776783 | 1 | 525549 | 14534.83 | 249.4 | 11376.03 | N/A | 13546.54 | 232.44 | 11376.32 | N/A | 13546.71 | 232.44 | 11402.07 | N/A | 13571.83 | 336.25 | 11459.65 | N/A | 13595.28 | 233.28 | 11907.82 | N/A | 14307.79 | 98.2 | N/A | N/A | N/A | N/A
GEN-2023-240 | DIS-23-1 | 05 SOUTHWEST | SPS | 550 | ER/NR | Solar | Tolk 345 kV Substation | 776785 | 1 | 525549 | 14534.83 | 255.8 | 11376.03 | N/A | 13546.54 | 238.41 | 11376.32 | N/A | 13546.71 | 238.41 | 11402.07 | N/A | 13571.83 | 344.89 | 11459.65 | N/A | 13595.28 | 239.27 | 11907.82 | N/A | 14307.79 | 100.72 | N/A | N/A | N/A | N/A
GEN-2023-240 | DIS-23-1 | 05 SOUTHWEST | SPS | 550 | ER/NR | Solar | Tolk 345 kV Substation | 776787 | 1 | 525549 | 14534.83 | 311.75 | 11376.03 | N/A | 13546.54 | 290.55 | 11376.32 | N/A | 13546.71 | 290.55 | 11402.07 | N/A | 13571.83 | 420.31 | 11459.65 | N/A | 13595.28 | 291.59 | 11907.82 | N/A | 14307.79 | 122.75 | N/A | N/A | N/A | N/A
GEN-2023-240 | DIS-23-1 | 05 SOUTHWEST | SPS | 550 | ER/NR | Solar | Tolk 345 kV Substation | 776789 | 1 | 525549 | 14534.83 | 249.4 | 11376.03 | N/A | 13546.54 | 232.44 | 11376.32 | N/A | 13546.71 | 232.44 | 11402.07 | N/A | 13571.83 | 336.25 | 11459.65 | N/A | 13595.28 | 233.28 | 11907.82 | N/A | 14307.79 | 98.2 | N/A | N/A | N/A | N/A
GEN-2023-241 | DIS-23-1 | 04 SOUTHEAST | AEP | 93 | ER | Solar | Winnsboro 138 kV Substation | 776803 | 1 | 508317 | 1487.31 | 39.98 | 1206.7 | N/A | 1405.4 | 37.78 | 1206.7 | N/A | 1405.4 | 37.78 | 1206.71 | N/A | 1405.4 | 54.55 | 1207.17 | N/A | 1460.25 | 15.7 | 1206.76 | N/A | 1405.41 | 37.78 | N/A | N/A | N/A | N/A