Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09322 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0939 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09592 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10326 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10326 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10326 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10879 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10879 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10879 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11209 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11209 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09847 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1058 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1058 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1058 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11134 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11134 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11134 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11463 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11463 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09938 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10663 | 102.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10663 | 102.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10663 | 102.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10697 | 103.68 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10697 | 103.68 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10741 | 104.16 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13183 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13479 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14443 | 107.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14443 | 108.41 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14443 | 108.41 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14477 | 109.17 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14477 | 109.17 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14522 | 109.67 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0509 | 117.56 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0509 | 120.95 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05398 | 115.77 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05398 | 116.09 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05404 | 116.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05404 | 116.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05413 | 116.49 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05864 | 127.17 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0509 | 115.67 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0509 | 119.13 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05398 | 114.41 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05398 | 114.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05404 | 115.06 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05404 | 115.06 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05413 | 115.22 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05864 | 125.32 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.12825 | 138.46 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16739 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16844 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16844 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16845 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16848 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16849 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1685 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1685 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1685 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16851 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16851 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16851 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16854 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16857 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16858 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16861 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16861 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16861 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16861 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16865 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16871 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16871 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16898 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16899 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16899 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16903 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16903 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16906 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16906 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16912 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16914 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16925 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16935 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16935 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1696 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16982 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16982 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16982 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17042 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17046 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17054 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17054 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17103 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17164 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17225 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17225 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17506 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17563 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17626 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17626 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1831 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18559 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19091 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19813 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21984 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21999 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21999 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22027 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21929 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21929 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09198 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16721 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16721 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16723 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16723 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1673 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1673 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1673 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16731 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16731 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16742 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16746 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16752 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16752 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16755 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16761 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16773 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16773 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16824 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16825 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16825 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16834 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16834 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16839 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16839 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16847 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16851 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16894 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1693 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1697 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1698 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1698 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17095 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17103 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17118 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17118 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17219 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1741 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1741 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18051 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18051 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19038 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19881 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27695 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14918 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14918 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15006 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15172 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15172 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15731 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15731 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16591 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17326 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26721 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11569 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22309 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22572 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22582 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22608 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22834 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22844 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2286 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22865 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22866 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22871 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23002 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23098 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23104 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23104 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23303 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24294 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25177 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27211 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37207 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4202 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42171 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42542 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22289 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24966 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37174 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41979 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42128 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42498 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09198 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16721 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16721 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16723 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16723 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16724 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16731 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16731 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16733 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16734 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16742 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16746 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16752 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16752 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16755 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16761 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16773 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16773 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16824 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16825 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16825 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16834 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16834 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16839 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16839 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16847 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16851 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16894 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16894 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1693 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16961 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1697 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1698 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1698 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17095 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17103 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17118 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17118 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17219 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1741 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1741 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18051 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18051 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18194 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19038 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19881 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19974 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20463 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27695 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14918 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14918 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15006 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15172 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15172 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15731 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15731 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16591 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17326 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17407 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17833 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26721 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09635 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09767 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09806 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10952 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0854 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08544 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08545 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08568 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08581 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08603 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08621 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08628 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0863 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0864 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08642 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08643 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08645 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08655 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08656 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08658 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08662 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08664 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08666 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08668 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08669 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0869 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08692 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.087 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08706 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08734 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08738 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08749 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08753 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08758 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08768 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0882 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08822 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08902 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0891 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08973 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09008 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09048 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09148 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09376 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09455 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10434 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10946 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11275 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09919 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10689 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11201 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1153 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13888 | 102.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13915 | 103.68 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1395 | 104.16 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17344 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17719 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 107.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18762 | 108.41 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18788 | 109.17 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18824 | 109.67 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.11 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.12 | ASGI-2011-004_POI_525915_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.17 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.33 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.59 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.64 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773700 G23-086-TAP 230 773701 GEN-2023-086 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | 773701 GEN-2023-086 230 773702 G23-086XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.04 | GEN-2023-086_POI_773700_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.21 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.36 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 106.65 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07656 | 100.11 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0766 | 100.13 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07661 | 100.84 | Potential P4 Event - POI 776000_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.19 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.25 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.29 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07662 | 100.31 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07663 | 100.19 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07665 | 100.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.67 | POI 515800_22 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07678 | 100.69 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 102.94 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 101.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 102.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.85 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 104.28 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.13 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 105.26 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07843 | 102.17 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 103.83 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 105.78 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.93 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 115.77 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 116.09 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 116.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 116.49 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 117.56 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 120.95 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 127.17 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 100.66 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 101.52 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 103.4 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07654 | 105.44 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07682 | 101.12 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07725 | 100.64 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.3 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 102.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.7 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0784 | 103.84 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07935 | 102.14 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08031 | 104.12 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08139 | 118.92 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.41 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09004 | 114.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 115.06 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09015 | 115.22 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 115.67 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09265 | 119.13 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10347 | 125.32 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.11102 | 138.46 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15121 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15122 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15123 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15125 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15126 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15128 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15132 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15135 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15136 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15138 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15142 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15149 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15175 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15176 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15181 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15184 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1519 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15191 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15216 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15225 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15237 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15258 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15321 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15324 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15333 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15386 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15504 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15736 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15747 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15801 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15893 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16243 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16484 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16762 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17038 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1998 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19991 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20014 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.2073 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17735 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1132 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2206 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22083 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2236 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22589 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.226 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22616 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22621 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22622 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22626 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22861 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23058 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24019 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24771 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26243 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37835 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41566 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41702 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42068 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22037 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24078 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37802 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41526 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4166 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42025 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10203 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17709 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17726 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17729 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1773 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17736 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17737 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17738 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17739 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1774 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17748 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17752 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17757 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17767 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17778 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1783 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17831 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17841 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17845 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17853 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17858 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17976 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17997 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17999 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18023 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18104 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18111 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18127 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18237 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18285 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18418 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19039 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19703 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20217 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20312 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21264 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2936 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15797 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15893 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1605 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16592 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17171 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17618 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17701 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1853 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28327 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10263 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10278 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10303 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11545 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11588 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11588 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08587 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08591 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08592 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08621 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08627 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0866 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0866 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08668 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08675 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08676 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08684 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08685 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08685 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08687 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08687 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08688 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08688 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08688 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08689 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08689 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08689 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08689 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08689 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0869 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0869 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08691 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08693 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08695 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08695 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08697 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.087 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08701 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08703 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08703 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08703 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08703 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08704 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08707 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08708 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0871 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08711 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08713 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08714 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08716 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08716 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08736 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08739 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08746 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08752 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08752 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0878 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08797 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08797 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08799 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08803 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08815 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08863 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08863 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08865 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08865 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08867 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08868 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08868 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08885 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08885 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08885 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08941 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08941 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08948 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08956 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09007 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09007 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09047 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09056 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09206 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09457 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09505 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09715 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09715 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09715 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09715 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09715 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10499 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10499 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10499 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11005 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11005 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11005 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11333 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11333 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0997 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0997 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0997 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0997 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0997 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10754 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10754 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10754 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1126 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1126 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1126 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11588 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11588 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.07743 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08257 | 102.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08257 | 102.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08257 | 102.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08286 | 103.68 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08286 | 103.68 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08337 | 104.16 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.12378 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.12597 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13371 | 107.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13371 | 108.41 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13371 | 108.41 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.134 | 109.17 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.134 | 109.17 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13453 | 109.67 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.12336 | 138.46 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16265 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16354 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16355 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16355 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16356 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16359 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16359 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16359 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1636 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1636 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1636 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1636 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1636 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16361 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16361 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16361 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16361 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16361 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16365 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16368 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16369 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16371 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16371 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16371 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16371 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16376 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16382 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16382 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16409 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1641 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1641 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16415 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16415 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16417 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16417 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16419 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16424 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16442 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16451 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16451 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16471 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16493 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16497 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16498 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16555 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16559 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16567 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16567 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16623 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16746 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16746 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16969 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17021 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17162 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17162 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1752 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17688 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17865 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17865 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17865 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17865 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17865 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17865 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18599 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2112 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2112 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2112 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21133 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21133 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21166 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20333 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20333 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09145 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1665 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1665 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16668 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16668 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1667 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1667 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16676 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16676 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16676 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16677 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16678 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16679 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16679 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16679 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1668 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16681 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16681 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16689 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16693 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16699 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16699 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16708 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1672 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1672 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16772 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16772 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16772 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16783 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16783 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16787 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16787 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16797 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16801 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16868 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16878 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16917 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16918 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16944 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16944 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17047 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17054 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1707 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1707 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17183 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17374 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17374 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18041 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18041 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18981 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19442 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27607 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14876 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14876 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14975 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15141 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15141 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15722 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15722 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16542 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16943 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17549 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17549 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17549 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26635 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10803 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21283 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21543 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21836 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21844 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22075 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22085 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22106 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22108 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22112 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22262 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22342 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22348 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22348 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22564 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23592 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24202 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2644 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36385 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40634 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4073 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41082 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41082 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41082 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41082 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21646 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24258 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36353 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40594 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40688 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4104 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4104 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4104 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4104 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09145 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1665 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1665 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16668 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16668 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1667 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1667 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16671 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16677 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16678 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16679 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16679 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16679 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1668 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1668 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16681 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16681 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16689 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16693 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16699 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16699 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16703 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16708 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1672 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1672 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16772 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16772 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16772 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16783 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16783 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16787 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16787 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16797 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16801 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16868 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16868 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16878 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16917 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16918 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16944 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16944 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17047 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17054 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1707 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1707 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17183 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17247 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17374 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17374 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18041 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18041 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18981 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19442 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19533 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20137 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27607 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14876 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14876 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14975 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15141 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15141 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15722 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15722 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16542 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16943 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17023 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17549 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17549 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17549 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26635 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08821 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08859 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08859 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08859 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08859 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08859 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08859 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08859 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08859 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08931 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10158 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05124 | 138.19 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05124 | 130.1 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05124 | 137.17 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12284 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12284 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09172 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09176 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09177 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09199 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.092 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09206 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09212 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09229 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09234 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09245 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09245 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09246 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09246 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09253 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0926 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09261 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0927 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0927 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09272 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09272 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09273 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09273 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09273 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09274 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09274 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09274 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09274 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09274 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09275 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09275 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09276 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09278 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0928 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0928 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0928 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09281 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09282 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09282 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09284 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09286 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09287 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09287 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09288 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09288 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09289 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09291 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09292 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09292 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09294 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09296 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09299 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09299 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09299 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09319 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09322 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09327 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09333 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09333 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09333 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09362 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09376 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09379 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09394 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09394 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09405 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09407 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09439 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09439 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0944 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0944 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0944 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0944 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09444 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09444 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09445 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09445 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09528 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09536 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09566 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09566 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09664 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09707 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09707 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09707 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09707 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09738 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09738 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.099 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10128 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10323 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10365 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10365 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10365 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10365 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10365 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11368 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11368 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11368 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11708 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11708 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11708 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1203 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1203 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1062 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1062 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1062 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1062 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1062 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11623 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11623 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11623 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11963 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11963 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11963 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12284 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12284 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06075 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07969 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05912 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05931 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05936 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06214 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06214 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06215 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06218 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06219 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06219 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06219 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06219 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06219 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06219 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0622 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0622 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0622 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06221 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06221 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06221 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06225 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06228 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06229 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06231 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06231 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06231 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06231 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06231 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06236 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06244 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06244 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06272 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06272 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06272 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06274 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0628 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0628 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0628 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0628 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06281 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06281 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06291 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06294 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.063 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06335 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06359 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06403 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06404 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06428 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06432 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06441 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06441 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06524 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06687 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06687 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07269 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07314 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07314 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08404 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08404 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08404 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08404 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08404 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08404 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10766 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07255 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07255 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07255 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08669 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08813 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08813 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08831 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08831 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08833 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0884 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0884 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0884 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08841 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08842 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08843 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08844 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08844 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08844 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08845 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08845 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08854 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08859 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08863 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08863 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08864 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08887 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08887 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08941 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08941 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08947 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08957 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08957 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08979 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08987 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08996 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09022 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09022 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0905 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09094 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0916 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0916 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09237 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09243 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0926 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0926 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10703 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10703 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12926 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13522 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1463 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06323 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06323 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06323 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08069 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08069 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08215 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0844 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0844 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09327 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09327 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11264 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11784 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14115 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.0553 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14182 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15059 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1627 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16462 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16583 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16839 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16849 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16864 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16869 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16871 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16876 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.171 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17121 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17127 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17127 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17504 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19064 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2419 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26204 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30809 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31026 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31026 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31026 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31026 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31112 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.17491 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24042 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24169 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30778 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30994 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30994 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30994 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30994 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31082 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07255 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07255 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07255 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08669 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08669 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08693 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08813 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08813 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08831 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08831 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08833 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08834 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08841 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08842 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08843 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08844 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08844 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08844 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08844 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08845 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08845 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08854 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08859 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08863 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08863 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08864 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08887 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08887 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08941 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08941 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08947 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08956 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08957 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08957 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08979 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08987 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08996 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09022 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09022 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0905 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09094 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0916 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0916 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09237 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09243 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0926 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0926 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10703 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10703 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12926 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12986 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13522 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1463 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06323 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06323 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06323 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08069 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08069 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08215 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0844 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0844 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09327 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09327 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11264 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11317 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11784 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14115 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.06753 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08178 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08203 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08203 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08203 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08203 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08203 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08203 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08203 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08203 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.094 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07201 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07201 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05011 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05018 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05043 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05043 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05064 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05068 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05068 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05089 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05089 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05089 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05089 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05116 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05116 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05186 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05193 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05453 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05453 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05453 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05453 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05453 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05473 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06545 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06545 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06545 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06947 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06947 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05708 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05708 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05708 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05708 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05708 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.068 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.068 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.068 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07201 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07201 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11546 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11546 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0855 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08553 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08554 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08577 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08577 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0859 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08612 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08623 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08623 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08624 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08624 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08631 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08637 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08639 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08648 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0865 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0865 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08654 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08656 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08658 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08658 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08658 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0866 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0866 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0866 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08664 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08666 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08666 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08666 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08666 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08667 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0867 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08671 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08672 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08673 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08676 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08677 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08678 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08678 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08699 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08702 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08709 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08715 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08715 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08739 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08743 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08758 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08758 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08762 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08767 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08826 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08826 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08828 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08828 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08831 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08831 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08831 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08849 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08849 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08849 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08901 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08901 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08911 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08919 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08962 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08962 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09017 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09032 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09057 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09057 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09057 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09057 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09164 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09409 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09466 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09674 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09674 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09674 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09674 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09674 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10441 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10441 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10441 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10962 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10962 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10962 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11291 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11291 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09929 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09929 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09929 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09929 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09929 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10696 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10696 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10696 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11217 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11217 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11217 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11546 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11546 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09071 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09907 | 102.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09907 | 102.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09907 | 102.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09936 | 103.68 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09936 | 103.68 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09981 | 104.16 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13156 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13572 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14553 | 107.83 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14553 | 108.41 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14553 | 108.41 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14581 | 109.17 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14581 | 109.17 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14628 | 109.67 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1334 | 138.46 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17264 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17359 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17359 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1736 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17363 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17363 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17364 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17364 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17364 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17364 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17364 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17365 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17365 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17365 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17365 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17365 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17366 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17369 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17372 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17373 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17375 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17375 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17375 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17375 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1738 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17386 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17386 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17413 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17414 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17414 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17419 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17419 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17422 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17422 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17427 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17445 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17454 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17454 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17475 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17497 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.175 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.175 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17559 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17562 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17565 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17571 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17571 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17624 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17746 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17746 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18039 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18097 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18156 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18156 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18648 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18717 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18835 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18835 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18835 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18835 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18835 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18835 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19572 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22637 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22637 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22637 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2265 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2265 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22679 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22519 | 114.05 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22519 | 114.9 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09549 | 112.47 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17054 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17054 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17072 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17072 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17074 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17074 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17081 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17081 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17081 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17082 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17082 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17084 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17084 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17084 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17085 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17085 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17085 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17093 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17097 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17103 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17103 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17107 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17113 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17124 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17124 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17176 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17177 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17177 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17187 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17187 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17191 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17191 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17201 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17204 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1727 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17282 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17317 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17317 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17318 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17322 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17345 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17345 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1745 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17457 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17473 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17473 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17582 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17772 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17772 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18428 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18428 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19354 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19779 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28277 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15227 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15227 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15322 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15488 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15488 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16059 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16059 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16867 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17237 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18226 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18226 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18226 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27282 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11077 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2165 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21817 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22106 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22117 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22347 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22357 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22373 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22378 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22379 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22383 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22527 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22613 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22618 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22618 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22828 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23839 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24762 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26647 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37017 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4113 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41245 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41604 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41604 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41604 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41604 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21872 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24448 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36984 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41089 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41203 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41561 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41561 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41561 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41561 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09549 | 113.2 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17054 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17054 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17072 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17072 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17074 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17074 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17075 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17082 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17082 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17084 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17084 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17084 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17085 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17085 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17085 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17085 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17093 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17097 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17103 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17103 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17107 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17113 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17124 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17124 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17176 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17177 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17177 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17187 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17187 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17191 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17191 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17201 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17204 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1727 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1727 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17282 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17317 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17317 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17318 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17322 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17345 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17345 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1745 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17457 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17473 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17473 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17582 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17713 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17772 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17772 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18428 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18428 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19354 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19779 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19872 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20914 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28277 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15227 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15227 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15322 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15488 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15488 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16059 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16059 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16867 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17237 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17318 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18226 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18226 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18226 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27282 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08907 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08946 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08946 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08946 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08946 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08946 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08946 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08946 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08946 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09034 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10477 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11978 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11978 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08909 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08912 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08913 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08936 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08936 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08943 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08949 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08965 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08971 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08982 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08982 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08983 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08983 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0899 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08996 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08998 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09006 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09007 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09008 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09009 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09009 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0901 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0901 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09011 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09011 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09011 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09011 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09011 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09012 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09012 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09013 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09015 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09017 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09017 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09017 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09018 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09019 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09019 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09021 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09023 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09024 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09024 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09025 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09025 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09026 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09029 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09029 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0903 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09031 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09033 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09036 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09036 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09036 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09057 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0906 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09066 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0907 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09072 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09072 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.091 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09116 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0912 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09125 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09125 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09139 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09151 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0918 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0918 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09182 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09183 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09183 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09185 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09185 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09189 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09189 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09189 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09267 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09275 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09283 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09283 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09391 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09432 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09432 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09432 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09432 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09573 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09573 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09595 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0985 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09963 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10072 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10072 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10072 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10072 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10072 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10968 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10968 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10968 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11399 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11399 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11399 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11723 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11723 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10327 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10327 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10327 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10327 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10327 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11222 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11222 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11222 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11654 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11654 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11654 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11978 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11978 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06038 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07827 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06126 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06239 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06265 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06536 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06562 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06562 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06563 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06564 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06566 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06567 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06567 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06567 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06567 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06567 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06567 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06568 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06568 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06568 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06569 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06569 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06569 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06573 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06575 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06576 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06579 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06579 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06579 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06579 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06584 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06591 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06591 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06619 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06619 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0662 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0662 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06625 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06625 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06626 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06626 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0663 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0663 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06635 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06643 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06656 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06682 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06705 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06735 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06735 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0677 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06774 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06782 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06782 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06851 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07004 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07004 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07561 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07561 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07768 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09215 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09215 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09215 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09215 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09215 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09215 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10349 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07675 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07675 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07675 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09256 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09344 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09344 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09362 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09362 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09364 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09364 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09371 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09371 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09371 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09372 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09372 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09375 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09375 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09389 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09393 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09393 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09403 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09469 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09469 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09473 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09483 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09483 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09484 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09484 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09503 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09508 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09528 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09555 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09555 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09578 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0962 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09662 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09663 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09756 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09763 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09779 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09779 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09919 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1016 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1016 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11062 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11062 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13266 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14328 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15509 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06688 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06688 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06688 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08522 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08522 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08644 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08854 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08854 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0964 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0964 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1156 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12486 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14963 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.07665 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15556 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17108 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18405 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18599 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18714 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18958 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18967 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18983 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18988 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1899 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18994 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19181 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19233 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19239 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19239 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19557 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20942 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26671 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26814 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34826 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34972 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35098 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35098 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35098 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35098 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19214 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2447 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26791 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34791 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.34937 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35061 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35061 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35061 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.35061 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07675 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07675 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07675 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09148 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09256 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09256 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09344 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09344 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09362 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09362 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09364 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09364 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09365 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09372 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09372 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09375 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09375 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09375 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09384 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09389 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09393 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09393 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09403 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09469 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09469 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09473 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09483 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09483 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09484 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09484 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09503 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09508 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09528 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09555 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09555 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09578 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0962 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09662 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09663 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09756 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09763 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09779 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09779 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09919 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1016 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1016 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11062 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11062 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13266 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14328 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14395 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15509 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06688 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06688 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06688 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08522 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08522 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08644 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08854 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08854 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0964 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0964 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1156 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12486 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12545 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14963 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.0762 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09533 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09557 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09561 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09561 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09561 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09561 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09561 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09561 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09561 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-201 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09561 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11503 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11503 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08497 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08501 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08502 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08525 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08525 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08532 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08538 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08554 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0856 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08572 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08572 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08579 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08585 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08587 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08596 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08598 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08598 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08611 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08612 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08619 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0862 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08621 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08624 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08625 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08626 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08626 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08658 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08691 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08705 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08705 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0871 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08714 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08724 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08726 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08777 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08778 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08797 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08797 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08797 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08841 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08842 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08859 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08867 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08963 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09003 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09003 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09003 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09003 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09121 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09289 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09289 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09411 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09417 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09616 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09616 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09616 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09616 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09616 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10339 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10339 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10339 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10919 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10919 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10919 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11248 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11248 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09871 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09871 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09871 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09871 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09871 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10594 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10594 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10594 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11173 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11173 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11173 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11503 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11503 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06185 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.05162 | 107.58 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07664 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05299 | 162.73 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05299 | 164.74 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05299 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05337 | 165.01 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05337 | 165.01 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05403 | 165.4 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05832 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05837 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05844 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05922 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05922 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05923 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05924 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05927 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05927 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05927 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05928 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05928 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05928 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05928 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05928 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05928 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05928 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05929 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05929 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05929 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05933 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05935 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05936 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05939 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05939 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05939 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05939 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05944 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0595 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0595 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05976 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0598 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05982 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05982 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05985 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05985 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05989 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05989 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0599 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05995 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06011 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06039 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06061 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0607 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06071 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06121 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06125 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0618 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06317 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06317 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06775 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06775 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07616 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09093 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09168 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09168 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09168 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09168 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09168 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09168 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10118 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10118 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10118 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10537 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10552 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10552 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1057 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1057 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10572 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10572 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10578 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10578 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10578 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10579 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1058 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10582 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10583 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10583 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10591 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10595 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.106 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10601 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10601 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1061 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10622 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10622 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10673 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10674 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10674 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10683 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10683 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10688 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10688 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10701 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10701 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10733 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1076 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1076 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1078 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10821 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10827 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10827 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10945 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10952 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11066 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11283 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11283 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1202 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1202 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13838 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16649 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17509 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08818 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08818 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08818 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09558 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09558 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09643 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09832 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09832 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10475 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10475 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12059 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14509 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16893 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10915 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21306 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21655 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21845 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21953 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21956 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22181 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22191 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22207 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22212 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22213 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22218 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22345 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22446 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22451 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22451 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22684 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23818 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28574 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31158 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.40846 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4094 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41294 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41294 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41294 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41294 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21852 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26216 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31131 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40806 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40898 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41252 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41252 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41252 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41252 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09963 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10118 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10118 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10118 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10537 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10537 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10552 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10552 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1057 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1057 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10572 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10572 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10573 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10579 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1058 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10581 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10582 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10582 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10583 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10583 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10591 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10595 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.106 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10601 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10601 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1061 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10622 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10622 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10673 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10674 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10674 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10683 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10683 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10688 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10688 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10701 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10701 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10733 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1076 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1076 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1078 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10821 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10827 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10827 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10945 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10952 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10968 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11066 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11283 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11283 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1202 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1202 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13838 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16649 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16727 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17509 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08818 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08818 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08818 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09558 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09558 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09643 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09832 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09832 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10475 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10475 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12059 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14509 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14577 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16893 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10075 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11615 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12818 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12851 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12851 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12851 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12851 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12851 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12851 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12851 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-203 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.12851 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05652 | 135.01 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05652 | 135.02 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05652 | 135.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05652 | 135.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05672 | 138.19 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05652 | 128.95 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05652 | 129.04 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05652 | 129.06 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05652 | 129.06 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05672 | 130.1 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05652 | 133.67 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05652 | 133.68 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05652 | 133.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05652 | 133.92 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05672 | 137.17 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13249 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13249 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10107 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10111 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10112 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10134 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10134 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10141 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10147 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10164 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10169 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1018 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1018 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10181 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10181 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10188 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10195 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10196 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10204 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10205 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10205 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10206 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10207 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10207 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10207 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10208 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10208 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10208 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10208 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10208 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10209 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1021 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1021 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10211 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10213 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10214 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10214 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10215 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10215 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10216 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10217 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10218 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10221 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10221 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10221 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10223 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10223 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10223 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10224 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10225 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10227 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10227 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10229 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10232 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10232 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10233 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10251 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10256 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10258 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10264 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10264 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10293 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10297 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10301 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10306 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1035 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10351 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10351 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10351 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10352 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10352 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10361 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10361 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10364 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10371 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10371 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10374 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10374 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10376 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10376 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10456 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10464 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10508 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10593 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10594 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10637 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10683 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10683 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10683 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10683 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10858 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11058 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11074 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11403 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11403 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11403 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11403 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11403 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12682 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12682 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12682 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12956 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12956 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12956 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12994 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12994 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11658 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11658 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11658 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11658 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11658 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12936 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12936 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12936 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13211 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13211 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13211 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13249 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13249 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05086 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05086 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09732 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10043 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10043 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10061 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10061 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10063 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10063 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10069 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10069 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10069 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10071 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10071 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10073 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10073 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10074 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10074 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10075 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10075 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10086 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1009 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10093 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10093 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10103 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10119 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10119 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10143 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10177 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10177 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10192 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10192 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10195 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10206 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10206 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10222 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10225 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10225 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10225 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10235 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10282 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10328 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10351 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10352 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10508 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10514 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10531 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10531 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10841 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1093 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10946 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10946 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10957 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10957 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11181 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11512 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11577 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11577 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16666 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08481 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08911 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08911 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08911 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09177 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09177 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09539 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09539 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10032 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10089 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10089 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16079 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11886 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12142 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12589 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12713 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12906 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13219 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13227 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13243 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13248 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1325 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13255 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13523 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1353 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1353 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13621 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13678 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13869 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14852 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21545 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23879 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24008 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24008 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24008 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24008 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24385 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.10906 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.13627 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21526 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23855 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23983 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23983 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23983 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23983 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24361 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09732 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10043 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10043 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10061 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10061 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10063 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10063 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10064 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10071 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10071 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10073 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10073 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10073 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10074 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10074 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10075 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10075 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10086 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1009 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10093 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10093 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10103 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10119 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10119 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10143 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10175 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10177 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10177 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10192 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10192 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10195 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10206 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10206 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10222 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10225 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10225 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10225 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10235 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10282 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10328 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10351 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10352 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10508 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10514 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10531 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10531 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10841 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1093 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10946 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10946 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10957 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10957 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11181 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11181 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11512 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11566 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11577 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11577 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16666 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08481 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08911 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08911 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08911 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09177 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09177 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09539 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09539 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10032 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1008 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10089 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10089 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-208 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16079 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0554 | 135.01 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0554 | 135.02 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0554 | 135.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0554 | 135.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05589 | 138.19 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0554 | 128.95 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0554 | 129.04 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0554 | 129.06 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0554 | 129.06 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05589 | 130.1 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0554 | 133.67 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0554 | 133.68 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0554 | 133.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.0554 | 133.92 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 279 | 330 | 0.05589 | 137.17 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13073 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13073 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09947 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0995 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09951 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09974 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09974 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09981 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09987 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10003 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10009 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1002 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1002 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10021 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10021 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10028 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10034 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10036 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10044 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10045 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10046 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10046 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10047 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10047 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10048 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10048 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10048 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10048 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10048 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10048 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10049 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1005 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1005 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10053 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10054 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10054 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10055 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10055 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10056 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10056 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10058 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1006 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10061 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10061 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10062 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10062 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10063 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10064 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10065 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10066 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10067 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10069 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10072 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10072 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10072 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10091 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10096 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10099 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10104 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10104 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10133 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10139 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10143 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10148 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10188 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10189 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10189 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10197 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10197 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10197 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10203 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10203 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10207 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10212 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10212 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10213 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10213 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10216 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10216 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10297 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10305 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10332 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10419 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10419 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1047 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10515 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10515 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10515 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10515 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10684 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10882 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10909 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11225 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11225 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11225 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11225 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11225 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12504 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12504 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12504 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12697 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12697 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12697 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12818 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12818 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1148 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1148 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1148 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1148 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1148 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12759 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12759 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12759 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12952 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12952 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12952 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13073 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.13073 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05061 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05061 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05061 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05061 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05061 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05061 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05148 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05148 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10862 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11049 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11049 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11067 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11067 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11069 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11069 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11075 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11075 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11075 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11077 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11077 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11079 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11079 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1108 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1108 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11081 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11081 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11092 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11096 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11099 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11099 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11109 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11125 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11125 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11142 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11182 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11182 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11197 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11197 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11198 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11209 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11209 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11225 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11238 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11287 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11332 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11351 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11352 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1138 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1138 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1138 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11507 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11513 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1153 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1153 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11819 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11888 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11915 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11915 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11933 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11933 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12137 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12505 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12557 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12557 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18332 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09466 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09917 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09917 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09917 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10048 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10048 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.103 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10399 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10399 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10898 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10943 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10943 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17687 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13115 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13153 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13556 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13793 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13871 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14174 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14183 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14199 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14204 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14206 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14211 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14475 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14482 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14482 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14529 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14606 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14807 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15779 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23403 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25697 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2585 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2585 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2585 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2585 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26138 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.12033 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.14477 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23382 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25671 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25823 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25823 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25823 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25823 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.26113 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10862 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11049 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11049 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11067 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11067 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11069 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11069 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1107 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11077 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11077 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11079 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11079 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11079 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1108 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1108 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11081 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11081 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11092 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11096 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11099 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11099 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11109 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11125 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11125 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11142 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11182 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11182 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11196 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11197 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11197 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11198 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11209 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11209 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11225 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11238 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11287 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11332 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11351 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11352 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1138 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1138 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1138 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11507 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11513 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1153 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1153 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11819 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11888 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11915 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11915 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11933 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11933 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12137 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12137 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12505 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12557 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12557 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12564 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18332 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09466 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09917 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09917 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09917 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10048 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10048 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.103 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10399 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10399 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10898 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10943 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10943 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10949 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-209 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17687 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08021 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08021 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05363 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05396 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05396 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05435 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05439 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0544 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05458 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05462 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05463 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05469 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05475 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05476 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05492 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05497 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05508 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05509 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0551 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0551 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05516 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05523 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05524 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05528 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05532 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05533 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05533 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05533 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05533 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05533 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05534 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05535 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05536 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05537 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05538 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05538 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05538 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05538 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05539 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05539 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05539 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05539 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05539 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0554 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05541 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05541 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05541 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05546 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05546 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05546 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05548 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05549 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0555 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05551 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05552 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05553 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05553 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05553 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05556 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05556 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05556 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05557 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05557 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05564 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05567 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05567 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05567 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05569 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05569 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05569 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05573 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05573 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05573 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05595 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05596 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05611 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05618 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05618 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05632 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05634 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05645 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05692 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05693 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05693 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05693 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05724 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05737 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05737 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05741 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05741 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05779 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05781 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05781 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05807 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05807 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05807 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05807 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05848 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05855 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06207 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06217 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06217 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06217 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06217 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06217 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07384 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07384 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07384 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07766 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07766 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05828 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05828 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05828 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06471 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06471 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06471 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06471 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06471 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07639 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07639 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07639 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08021 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-228 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08021 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11825 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11825 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08775 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0878 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08802 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08803 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0881 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08816 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08832 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08838 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08849 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08849 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0885 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0885 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08856 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08863 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08865 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08873 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08875 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08876 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08876 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08877 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08877 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08877 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08877 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08877 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08877 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08878 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08878 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0888 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08882 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08884 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08884 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08884 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08885 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08886 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08886 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08888 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0889 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08891 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08891 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08893 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08896 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08896 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08897 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08899 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08901 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08902 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08903 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08903 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08924 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08927 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08933 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08936 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08939 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08939 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08967 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08984 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08988 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08989 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08989 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09005 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09009 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09049 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09049 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0905 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0905 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09051 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09053 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09053 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09062 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09062 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09062 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09135 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0914 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09143 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09252 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09293 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09293 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09293 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09293 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09442 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09514 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09514 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0971 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09786 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09925 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09925 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09925 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09925 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09925 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10763 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10763 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10763 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11244 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11244 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11244 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1157 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1157 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10179 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10179 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10179 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10179 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10179 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11018 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11018 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11018 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11499 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11499 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11499 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11825 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11825 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05998 | 111.5 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07659 | 114.4 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05519 | 142.55 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05884 | 138.53 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05903 | 138.2 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06086 | 134.22 | 560022 CRAWFISH_DR 345 774180 G23-110-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06132 | 134.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06132 | 134.32 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.07 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.08 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.08 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.09 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.09 | P23:345:XEL:8N17 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.09 | P23:345:XEL:8N22 SHC | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.1 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.62 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.65 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.65 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.67 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.67 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.7 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.7 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.71 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.71 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.74 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.74 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.75 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.77 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.8 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.81 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.87 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.88 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.88 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.88 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.89 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.89 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.9 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.91 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.91 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.91 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.93 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.93 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.94 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 134.95 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.03 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.05 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.11 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.11 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.12 | P11:21:EES:RVB:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.12 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.12 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.14 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.14 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.17 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.19 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.19 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.19 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.44 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.44 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.5 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.67 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.67 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 135.67 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 136.51 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 138.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06136 | 134.33 | 539784 ENSNGW 3 115 3WXFMR ENSIGN WIND 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06137 | 134.35 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06137 | 134.36 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06137 | 134.36 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06137 | 134.36 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06137 | 134.58 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06137 | 134.58 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06138 | 134.62 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06138 | 134.68 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06138 | 134.68 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06139 | 133.94 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06139 | 134.74 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06139 | 134.74 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06143 | 134.64 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 134.89 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06146 | 134.82 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06149 | 134.81 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06149 | 134.81 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06149 | 134.81 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06149 | 134.81 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06154 | 134.86 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0616 | 135.18 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0616 | 135.18 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06188 | 136.26 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06188 | 136.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06188 | 136.3 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06189 | 136.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06194 | 136.03 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06194 | 136.03 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06196 | 135.85 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06196 | 135.9 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06198 | 136.42 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06198 | 136.42 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06204 | 136.2 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0621 | 135.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0622 | 138.37 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06251 | 137.2 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06273 | 136.64 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06297 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06297 | 136.74 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06337 | 140.07 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06341 | 140.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06349 | 140.41 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06349 | 140.41 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06411 | 140.35 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06559 | 141.43 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06559 | 141.57 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07086 | 146.73 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07086 | 147.76 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07408 | 148.33 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09129 | 150.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09129 | 154 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09129 | 156.76 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09129 | 157.19 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09129 | 159.91 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09129 | 161.9 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09787 | 159.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07887 | 116.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07887 | 119.14 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07887 | 119.15 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09094 | 110.39 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09167 | 108.23 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09167 | 108.23 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09185 | 107.69 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09185 | 107.69 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09187 | 107.69 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09187 | 108.08 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.35 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.38 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.39 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.39 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.4 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.4 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.4 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.6 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.67 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.69 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.84 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.85 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.86 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.88 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.88 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.91 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.02 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.02 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.08 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.1 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.1 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.1 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.12 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.15 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.15 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.19 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.2 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.23 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.34 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.35 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.36 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.36 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.37 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.37 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.37 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.38 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.39 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.39 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.42 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.42 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.43 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.44 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.45 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.5 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.55 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.59 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.67 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.67 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.69 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.69 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.69 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.71 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.71 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.73 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.78 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.78 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.78 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.91 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.91 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.91 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.96 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.97 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.99 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109.92 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109.95 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 110.21 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 110.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 112.46 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09193 | 107.69 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09193 | 107.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09193 | 107.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09194 | 107.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09195 | 107.91 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09196 | 107.96 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09197 | 107.18 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09197 | 108.02 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09197 | 108.03 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09198 | 108.11 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09198 | 108.11 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09206 | 107.98 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09211 | 108.21 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09215 | 108.41 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09216 | 108.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09216 | 108.21 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09225 | 108.27 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09238 | 108.64 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09238 | 108.64 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09291 | 109.95 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09291 | 109.95 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09293 | 110.01 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09303 | 109.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09303 | 109.68 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09306 | 109.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09306 | 109.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09322 | 109.91 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09326 | 109.29 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09347 | 112.06 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 111.18 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 111.18 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09399 | 111 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 110.36 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09471 | 110.26 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09472 | 110.27 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09572 | 114.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09579 | 114.62 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09595 | 114.95 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09595 | 114.95 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09722 | 115.01 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09956 | 115.82 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09956 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10808 | 120.81 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10808 | 121.59 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12952 | 121.87 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14802 | 136.58 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 126.41 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 130.57 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 133.59 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 134.05 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 136.94 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 137.75 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 137.78 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 138.96 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15215 | 181.06 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06873 | 101.8 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06873 | 103.84 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06873 | 103.84 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08362 | 100.18 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08362 | 100.18 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08472 | 100.23 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08676 | 100.94 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08676 | 101.06 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09419 | 105.29 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09419 | 105.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11287 | 106.21 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.129 | 119.03 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 110.17 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 113.79 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 116.43 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 116.82 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 119.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 120.05 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 120.08 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 121.11 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1468 | 175.43 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.08696 | 100.95 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18438 | 102.06 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19436 | 100.95 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19626 | 100.3 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19743 | 100.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1998 | 103.13 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1999 | 103.19 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20006 | 102.2 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20011 | 102.05 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20013 | 103.5 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20017 | 101.44 | Potential P4 Event - POI 523823_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20184 | 103.37 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20252 | 104.75 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20258 | 104.09 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20258 | 104.59 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2055 | 104.71 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21859 | 109.27 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27414 | 117.59 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27702 | 152.61 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.28766 | 101.96 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36766 | 183.79 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36836 | 184.51 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37064 | 179.87 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37064 | 179.92 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37064 | 184.88 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37064 | 191.94 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20056 | 100.16 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25152 | 107.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.27677 | 153.1 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36729 | 184.16 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.368 | 184.91 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37026 | 180.34 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37026 | 180.35 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37026 | 185.27 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37026 | 192.34 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07887 | 117.81 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07887 | 120.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07887 | 120.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08884 | 110.28 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09094 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09094 | 110.7 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09167 | 108.46 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09167 | 108.46 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09185 | 107.93 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09185 | 107.93 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09187 | 107.93 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09187 | 108.31 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.6 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.64 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.64 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.64 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.65 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.65 | P23:345:XEL:8N8 MNN | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.84 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.91 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.93 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.93 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 107.93 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.08 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.09 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.1 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.14 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.14 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.15 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.24 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.26 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.26 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.31 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.33 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.34 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.34 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.36 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.38 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.38 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.43 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.43 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.47 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.48 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.57 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.58 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.59 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.59 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.6 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.6 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.6 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.61 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.62 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.62 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.65 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.65 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.66 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.67 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.69 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.73 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.78 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.82 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.9 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.9 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.94 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.94 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 108.96 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109.26 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109.26 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109.26 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109.33 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109.33 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 109.38 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 110.13 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 110.7 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09188 | 113.2 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09194 | 108.15 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09195 | 108.15 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09196 | 108.2 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09197 | 107.43 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09197 | 107.43 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09197 | 108.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09197 | 108.27 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09198 | 108.34 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09198 | 108.34 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09206 | 108.22 | 539671 FTDODGE3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09211 | 108.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09215 | 108.64 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09216 | 108.38 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09216 | 108.38 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB :::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09225 | 108.5 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09238 | 108.87 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09238 | 108.87 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09291 | 110.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09291 | 110.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09293 | 110.2 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09303 | 109.88 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09303 | 109.88 | P23:345:SUNC:BU_BRK488:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09306 | 109.68 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09306 | 109.73 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09322 | 110.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09326 | 109.48 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09347 | 112.33 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 111.45 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09374 | 111.45 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09399 | 111.12 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 110.52 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09471 | 110.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09472 | 110.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09572 | 114.65 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09579 | 114.7 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09595 | 115.03 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09595 | 115.03 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09722 | 115.2 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09956 | 115.8 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09956 | 115.96 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10808 | 121.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10808 | 121.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12952 | 122.24 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14802 | 139.23 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 127.99 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 132.76 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 135.94 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 136.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 139.53 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 140.37 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 140.41 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14872 | 141.59 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15215 | 181.04 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06873 | 102.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06873 | 104.7 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06873 | 104.7 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08362 | 100.26 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08362 | 100.26 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08472 | 100.4 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08676 | 100.92 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08676 | 101.05 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09419 | 105.57 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09419 | 106.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11287 | 106.54 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.129 | 121.34 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 111.55 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 115.7 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 118.48 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 118.89 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 121.6 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 122.33 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 122.37 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1296 | 123.4 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1468 | 175.32 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.07905 | 111.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09813 | 106.67 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10314 | 116.16 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10343 | 104.1 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10343 | 107.2 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10343 | 111.56 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10343 | 112.2 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10343 | 116.48 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10343 | 117.09 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10343 | 117.11 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-236 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10343 | 118.06 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08782 | 107.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08782 | 107.29 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05989 | 103.86 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05989 | 104.57 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06123 | 103.35 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06125 | 104.57 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06129 | 106.59 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0613 | 106.62 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06152 | 103.97 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06153 | 106.9 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0616 | 106.53 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06166 | 103.66 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06182 | 103.29 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06187 | 103.13 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06198 | 103.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06199 | 103.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.062 | 102.88 | 652607 WESSINGTON 4 230 659295 SD.PW1__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.062 | 103.12 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06206 | 102.89 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06213 | 103.45 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06214 | 102.64 | 655841 ARNEGARD-MK7 115 659346 LC_SWY.S-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 102.47 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 102.47 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 102.5 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 102.65 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 102.91 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.1 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.11 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.18 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.18 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.18 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.19 | 620482 J510 ASTOR 3 345 620083 J510 ASTORG1 20.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.2 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.35 | GEN-2023-116_POI_640252_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.37 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.44 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.51 | P15:230:UMZB:# 2982 #:: DHC IN NE. STEGALL DC CONVERTER STATION AND SHUNT DEVICE:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.54 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.63 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.93 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 103.98 | P23:345:XEL:8P2 KING | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 104 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 104.01 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 104.02 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 104.06 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 104.12 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 104.12 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 104.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 104.3 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.2 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.27 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.38 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.43 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.44 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.53 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.56 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.64 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.65 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.79 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 105.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06222 | 111.13 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06223 | 102.48 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06223 | 105.07 | P23:345:XEL:8N8 MNN | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06223 | 105.12 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06223 | 105.13 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06223 | 105.26 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06224 | 105.53 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06225 | 102.76 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06226 | 102.54 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06227 | 102.66 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06228 | 102.73 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06228 | 102.76 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06229 | 102.54 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06229 | 102.61 | P12:345:AMMO::MAYWOOD:SUBT:77 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06229 | 103.18 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06229 | 103.18 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06229 | 103.18 | P23:500:EES:PERRYVILLE:R9872::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06229 | 103.23 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0623 | 102.91 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0623 | 103.82 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06231 | 102.76 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06235 | 102.79 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06236 | 103.18 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06236 | 103.28 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06238 | 103.23 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06238 | 103.48 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06239 | 103.58 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0624 | 102.61 | 300143 4VALLEY 138 514830 FITZGRD4 138 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0624 | 103.24 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06242 | 103.57 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06243 | 103.52 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06243 | 103.52 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06243 | 104.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06245 | 102.86 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06246 | 103.04 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06247 | 103.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06256 | 102.79 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06256 | 103.02 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06256 | 104.57 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06257 | 103.26 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06258 | 104.77 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0626 | 103.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0626 | 103.74 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06283 | 102.8 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06283 | 103.95 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06283 | 103.95 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06284 | 103.57 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06287 | 105.91 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06287 | 105.96 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.063 | 103.37 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06307 | 103.75 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06307 | 103.75 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06322 | 108.32 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06329 | 111.11 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06331 | 103.64 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0637 | 104.88 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06374 | 103.64 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06409 | 108.81 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06413 | 104.13 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06413 | 104.13 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06438 | 103.92 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06438 | 103.92 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06447 | 105.73 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06447 | 105.73 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06449 | 103.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06496 | 108.66 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06507 | 105.39 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06514 | 105.24 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06527 | 106.49 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06527 | 106.62 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06527 | 106.74 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06527 | 108.72 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06528 | 104.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06528 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06528 | 104.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06679 | 124.17 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06679 | 124.17 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06679 | 124.17 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06925 | 111.24 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06983 | 119.41 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06983 | 119.41 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06983 | 119.41 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06983 | 119.41 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06983 | 119.41 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0817 | 124.55 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0817 | 124.55 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0817 | 124.55 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08527 | 134.94 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08527 | 134.94 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06933 | 109.24 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06933 | 109.24 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06933 | 109.24 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07238 | 104.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07238 | 104.23 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07238 | 104.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07238 | 104.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07238 | 104.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08424 | 109.9 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08424 | 109.9 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08424 | 109.9 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08782 | 121.32 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27SP | GEN-2023-237 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.08782 | 121.32 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07618 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07882 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05964 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07824 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05964 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05841 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05842 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05865 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06133 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06137 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06143 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06145 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06148 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06148 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0615 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0615 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0615 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06151 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06151 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06151 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06151 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06155 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06156 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06158 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06158 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0616 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06169 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06173 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06173 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06174 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0618 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.062 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06204 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06207 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06207 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06208 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0621 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06214 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06214 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06217 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06217 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06221 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06222 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06229 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06264 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06289 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06332 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06333 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06359 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06364 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06373 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06459 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0647 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06611 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06611 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07213 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07238 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07238 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08355 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08355 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08355 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08355 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08355 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08355 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10604 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07231 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07231 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07231 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08665 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08667 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08792 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08792 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08807 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08814 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08814 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08815 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08817 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08817 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08817 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08817 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08822 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08822 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08825 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08825 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08825 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08826 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08827 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08827 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08833 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08837 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08839 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08842 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08846 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0886 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08869 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08928 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08933 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08933 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08936 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08939 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08961 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08967 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08972 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09015 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09015 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09029 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09075 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0914 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09141 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0922 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09229 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09247 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09419 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09426 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09656 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09656 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10674 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10674 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12948 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13412 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14599 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06301 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06301 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06301 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07552 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07553 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07662 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07662 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07675 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07681 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07681 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07684 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07684 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07688 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07688 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0769 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0769 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0769 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07692 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07692 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07692 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07692 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07698 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07701 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07703 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07706 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07709 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07721 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07728 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07728 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07729 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0778 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07785 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07785 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07787 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0779 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07801 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07801 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07809 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07814 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07819 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07856 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07856 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07868 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07908 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07965 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07966 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08035 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08042 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08058 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08209 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08214 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08415 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08415 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09302 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09302 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11283 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11688 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14085 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.05576 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14219 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15114 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15114 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15114 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16203 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16203 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16331 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16488 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16497 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16497 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.165 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16504 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16516 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16522 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16522 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16535 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16549 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16567 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16567 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1664 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16706 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16809 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1681 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16903 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16914 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1694 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16943 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16947 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17176 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17189 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17196 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17196 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17549 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19109 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20808 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24231 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26067 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30918 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31141 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31141 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31141 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31141 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31197 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.17532 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23916 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2421 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30887 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31109 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31109 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31109 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31109 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31166 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07231 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07231 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07231 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08665 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08667 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08792 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08792 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08807 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08814 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08814 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08815 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08816 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08817 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08817 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08817 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08822 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08822 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08825 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08825 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08825 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08826 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08827 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08827 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08833 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08837 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08839 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08842 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08846 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0886 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08869 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08928 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08933 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08933 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08934 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08936 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08939 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08951 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08961 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08972 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09015 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09015 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09029 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09075 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0914 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09141 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0922 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09229 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09247 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09419 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09426 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09656 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09656 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10674 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10674 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12948 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13008 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13412 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14599 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06301 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06301 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06301 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07552 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07553 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07662 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07662 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07675 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07681 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07681 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07683 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07684 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07684 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07688 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07688 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0769 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0769 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0769 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07692 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07692 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07692 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07692 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07698 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07701 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07703 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07706 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07709 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07721 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07728 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07728 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07729 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0778 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07785 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07785 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07786 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07787 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0779 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07801 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07801 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07809 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07819 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07856 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07856 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07868 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07908 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07965 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07966 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08035 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08042 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08058 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08209 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08214 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08415 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08415 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09302 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09302 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11283 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11336 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11688 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | ASGI-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14085 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07956 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08352 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06016 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07599 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06016 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05151 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05841 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05854 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05944 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05994 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05998 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06001 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06008 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0601 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06013 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06013 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06014 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06014 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06014 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06015 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06015 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06015 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06015 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0602 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06021 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06021 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06024 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06032 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06036 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06036 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06037 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06064 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06064 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06068 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0607 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0607 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0607 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06079 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06079 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06079 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06079 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06079 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06083 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0609 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06125 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06148 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06167 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06168 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06213 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06217 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06227 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06287 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06319 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0642 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0642 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06928 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06928 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07465 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08929 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08929 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08929 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08929 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08929 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08929 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0946 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09719 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10024 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10087 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1012 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1012 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10135 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10142 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10143 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10143 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10146 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10146 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10146 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10146 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1015 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1015 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10152 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10152 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10153 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10155 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10155 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10155 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10164 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10166 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1017 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10172 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10187 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10194 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10194 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10196 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10247 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10255 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10258 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10258 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10258 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10276 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10276 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10277 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10278 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.103 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10343 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10343 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10352 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10395 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10418 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10418 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10528 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10536 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10554 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10677 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10725 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10885 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10885 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11705 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11705 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13701 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1561 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16798 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08074 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08074 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08074 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0847 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08736 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08791 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08819 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08819 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08832 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08839 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08839 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08841 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08841 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08845 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08845 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08847 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08847 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08848 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08849 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08849 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08849 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08849 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08858 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08859 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08863 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08865 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08878 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08883 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08883 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08886 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0893 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08937 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08939 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08939 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0894 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08955 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08955 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08956 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08957 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08976 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09013 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09013 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09021 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09058 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09079 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09079 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09174 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09182 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09198 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09305 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09346 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09486 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09486 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10201 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10201 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1194 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13603 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16207 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09353 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19004 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19433 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19433 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19433 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20059 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20059 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20108 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20252 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20264 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20268 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20268 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20269 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20293 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20294 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20294 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20296 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20301 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20344 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20344 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20409 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2047 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20512 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20513 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2065 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20662 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20688 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20691 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20694 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20855 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20925 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20932 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20932 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21183 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22269 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22442 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27642 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29213 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38025 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38025 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38344 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38344 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38344 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38344 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2059 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25361 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.29187 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37986 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37988 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38304 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38304 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38304 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38304 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09265 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09719 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10024 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10087 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1012 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1012 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10135 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10142 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10143 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10143 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10144 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10146 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10146 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10146 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1015 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1015 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10152 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10152 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10153 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10155 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10155 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10155 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10164 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10166 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1017 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10172 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10187 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10194 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10194 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10196 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10247 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10255 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10258 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10258 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10258 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10266 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10276 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10276 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10278 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.103 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10343 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10343 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10352 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10395 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10418 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10418 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10528 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10536 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10554 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10677 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10725 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10885 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10885 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11705 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11705 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13701 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1561 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15683 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16798 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08074 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08074 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08074 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0847 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08736 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08791 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08819 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08819 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08832 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08839 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08839 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0884 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08841 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08841 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08845 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08845 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08847 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08847 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08848 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08849 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08849 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08849 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08849 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08858 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08859 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08863 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08865 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08878 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08883 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08883 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08886 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0893 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08937 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08939 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08939 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0894 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08946 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08955 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08955 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08957 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08976 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09013 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09013 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09021 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09058 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09079 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09079 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09174 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09182 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09198 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09305 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09346 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09486 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09486 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10201 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10201 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1194 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13603 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.13667 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16207 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-001 | FROM->TO | 528413 TAYLOR 3 115 528449 W_BENDER 3 115 1 | 159 | 165 | 1 | 133.01 | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1 | Cumulative Impact | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08561 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13563 | 101.14 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.05 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13838 | 109.93 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17197 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17572 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 111.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18677 | 113.77 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 104.62 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.59 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 106.03 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 106.06 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 109.93 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 116.31 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 103.54 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08643 | 104.65 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 103.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 104.24 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 104.7 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 108.19 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 114.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10959 | 143.58 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14889 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14981 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14984 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14991 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15002 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15004 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15006 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15007 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15015 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15045 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1505 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15051 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1506 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15061 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15084 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15106 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15192 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15206 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15264 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15298 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15603 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15613 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15667 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16105 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1663 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16889 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19856 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17755 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15473 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11163 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17803 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15515 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-005 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.09183 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.10059 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.05917 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.05994 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.05917 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.05994 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28037 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3489 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.34961 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3555 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3555 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35564 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35572 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35572 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35573 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35579 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35579 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3558 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3558 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35581 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35583 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35583 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35584 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35589 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3559 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35592 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35598 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35602 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35613 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35614 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35614 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3562 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35643 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35644 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35651 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35655 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35664 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35669 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3567 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35691 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35691 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35718 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35726 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35726 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35761 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35794 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3584 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35879 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35889 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35905 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35962 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35962 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36044 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36117 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36117 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36612 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.58908 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.24433 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30405 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30467 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3098 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3098 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30993 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31002 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31002 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31008 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31009 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31009 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3101 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3101 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31014 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31015 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31017 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31022 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31026 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31042 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31062 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31062 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31069 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31072 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3108 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31085 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31085 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31088 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31088 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31096 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31103 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31103 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31127 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31134 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31134 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31165 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31193 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31233 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31267 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31276 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3129 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3134 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3134 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31411 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31474 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31474 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31906 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.56835 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23006 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33761 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33858 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33862 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3387 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33875 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33884 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33884 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33888 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33891 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33902 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33902 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33902 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33902 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33926 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33926 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33942 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33942 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34033 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3408 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34134 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34152 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34192 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34206 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3423 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34235 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34237 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34324 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34408 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34423 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34429 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34429 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34545 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34545 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34545 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.34573 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.35961 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.62715 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.63714 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6438 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6438 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6438 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.6438 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.65295 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3172 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32994 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.62654 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.63649 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64314 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64314 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64314 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.64314 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.65237 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28037 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3489 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.34961 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35054 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3555 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3555 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35564 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35572 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35572 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35573 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35574 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35575 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35579 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35579 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3558 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3558 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35581 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35583 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35583 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35584 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35589 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3559 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35592 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35598 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35602 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35613 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35614 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35614 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3562 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35643 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35651 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35655 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35664 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35669 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3567 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35673 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35683 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35686 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35691 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35691 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35718 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35726 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35726 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35761 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35794 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.3584 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35879 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35889 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35905 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35962 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.35962 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36044 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36117 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36117 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36596 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36612 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.58908 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.24433 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30405 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30467 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30548 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3098 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3098 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.30993 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31001 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31002 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31002 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31006 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31008 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31009 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31009 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3101 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3101 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31014 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31015 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31017 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31022 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31026 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31036 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31042 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31062 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31069 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31072 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3108 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31085 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31085 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31088 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31088 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31096 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31099 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31103 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31103 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31127 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31134 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31134 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31165 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31193 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31233 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31267 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31276 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3129 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3134 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.3134 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31411 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31474 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31474 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31892 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.31906 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-008 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.56835 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06672 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.06708 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 115.41 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 115.42 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 115.42 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 115.46 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 115.46 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 114.08 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 114.1 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 114.1 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 114.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05072 | 114.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.06834 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07247 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07247 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07247 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07382 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07382 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07398 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07405 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07407 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07407 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07408 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07408 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07408 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07408 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07413 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07413 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07417 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07417 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07417 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07417 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0742 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0742 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07432 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07434 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07437 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07454 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07459 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07467 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07467 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07469 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07477 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07546 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07546 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07556 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07559 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07566 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07566 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07587 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0759 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07595 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07598 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07618 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07671 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07682 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07683 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07906 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07949 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07949 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07962 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07965 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07985 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08225 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08246 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08254 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08254 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08707 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08723 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08857 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08857 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12265 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.05955 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06315 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06315 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06315 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06434 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06434 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06447 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06453 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06455 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06456 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06456 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0646 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0646 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06463 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06464 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06464 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06464 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06464 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06466 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06466 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06477 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06479 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06481 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06496 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.065 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06507 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06507 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06509 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06516 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06576 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06576 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06585 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06587 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06593 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06593 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06612 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06614 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06619 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06622 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06639 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06685 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06695 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06695 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0689 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06927 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06927 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06938 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06942 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06959 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07168 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07186 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07193 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07193 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07588 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07602 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07718 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07718 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11833 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.08518 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09239 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09454 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09609 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09609 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09609 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09731 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09929 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09929 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09943 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09952 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09956 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09956 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09985 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09997 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10001 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10039 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10115 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10138 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10139 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10326 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10377 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10377 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10452 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10452 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10516 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10522 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1055 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10551 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10559 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10883 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10893 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10893 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1096 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11554 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.119 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16326 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18481 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18557 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18557 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18557 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18557 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19065 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.07815 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.10918 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.16311 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18463 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18538 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18538 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18538 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18538 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19047 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.06834 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07247 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07247 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07247 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07382 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07382 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07398 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07405 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07406 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07407 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07407 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07408 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07408 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07408 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07413 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07413 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07417 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07417 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07417 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07417 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0742 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0742 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07432 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07434 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07437 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07454 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07459 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07467 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07467 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07469 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07477 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07546 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07546 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07556 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07566 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07566 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07587 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0759 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07595 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07598 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07618 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07671 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07682 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07683 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07906 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07949 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07949 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07962 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07965 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07985 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08225 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08246 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08254 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08254 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08707 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08723 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08764 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08857 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08857 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09176 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12265 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.05955 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06315 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06315 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06315 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06434 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06434 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06447 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06453 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06454 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06455 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06456 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06456 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0646 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0646 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06463 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06464 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06464 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06464 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06464 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06466 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06466 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06477 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06479 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06481 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06496 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.065 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06507 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06507 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06509 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06516 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06576 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06576 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06585 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06593 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06593 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06612 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06614 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06619 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06622 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06639 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06685 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06695 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06695 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0689 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06927 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06927 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06938 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06942 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06959 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07168 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07186 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07193 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07193 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07588 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07602 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07638 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07718 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07718 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07996 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11833 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08103 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.08561 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13563 | 101.14 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.05 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13777 | 108.5 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13804 | 109.35 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13838 | 109.93 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17197 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17572 | 110.53 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 111.67 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18616 | 112.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18641 | 113.15 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18677 | 113.77 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 104.62 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.24 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 105.59 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 105.84 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 106.03 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 106.06 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 109.93 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 116.31 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12885 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0809 | 103.54 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08643 | 104.65 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 103.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08955 | 104.24 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0896 | 104.5 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08967 | 104.7 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09211 | 108.19 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10284 | 114.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10959 | 143.58 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14889 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14981 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14984 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14991 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14993 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14995 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14997 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.14998 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15002 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15004 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15006 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15007 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15015 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15019 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1502 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15045 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1505 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15051 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15052 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1506 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15061 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15062 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15084 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15098 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15106 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15127 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15129 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15192 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15206 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15264 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15298 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15371 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15603 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15613 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15667 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15767 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16105 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16339 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1663 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16889 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19822 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19833 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19856 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.2 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 121.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 560 | 644 | 0.20345 | 103.84 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20608 | 122.42 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 129.93 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17755 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 113.23 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15473 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11163 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21918 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21945 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22059 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22071 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22076 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22077 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22096 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22101 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22158 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22215 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22228 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22267 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22268 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22274 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22279 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22389 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22452 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22464 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22489 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22493 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22496 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22648 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22723 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2273 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22908 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24614 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26059 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37603 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41286 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4143 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41796 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21915 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23909 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3757 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41245 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41387 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41753 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10095 | 131.12 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17442 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17608 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17623 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1763 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17631 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17632 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17634 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17638 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17641 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17643 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17652 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17653 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17658 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17665 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17675 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1768 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17684 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17733 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17741 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17744 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17745 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17762 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17803 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17836 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17869 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17878 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17893 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17911 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17936 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1801 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18018 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18036 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18154 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18183 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18204 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18315 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18948 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19587 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20093 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20187 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21147 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29198 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08797 | 114.27 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.152 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15345 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15358 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15364 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15367 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15371 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15375 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15383 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15384 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15388 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15395 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15403 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15408 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15411 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15453 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15461 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15463 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15464 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15479 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15515 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15544 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15572 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1558 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15593 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15609 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15631 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15695 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15702 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15718 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1582 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15846 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15864 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15961 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16513 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17069 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1751 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17593 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18428 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.2817 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07697 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07992 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05949 | 117.25 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07836 | 118.44 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05949 | 102.46 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06513 | 143.91 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06547 | 143.57 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06703 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0693 | 139.98 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06933 | 139.42 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06933 | 144.04 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0694 | 139.44 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.34 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.42 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.44 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.45 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.45 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.46 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.72 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.74 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.74 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.78 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.8 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.81 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.81 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.83 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.84 | GEN-2011-025_POI_525803_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.86 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.86 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.86 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.87 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.88 | GEN-2012-001_POI_526679_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.9 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.9 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.91 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.94 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 139.97 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.02 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.05 | P11:16:EES-EAI:MAGNET:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.05 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.05 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.06 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.06 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.07 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.07 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.08 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.1 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.1 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.11 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.11 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.12 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.17 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.21 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.23 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.3 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.3 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.3 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.3 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.3 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.32 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.32 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.33 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.36 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.36 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.37 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.61 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.61 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.67 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.85 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.85 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 140.85 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 141.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06942 | 143.58 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06945 | 139.69 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06945 | 139.7 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06947 | 139.79 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06947 | 139.81 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06947 | 139.81 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06948 | 139.31 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06948 | 139.31 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06948 | 139.83 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06948 | 139.84 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06952 | 139.75 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06954 | 139.92 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06954 | 139.99 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06956 | 139.93 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06965 | 140 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0697 | 139.8 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0697 | 140.23 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0697 | 140.23 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06995 | 142.47 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06998 | 142.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07 | 141.75 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07004 | 140.79 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07004 | 140.79 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07004 | 141.34 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07006 | 141.5 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07013 | 140.47 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07013 | 140.52 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07013 | 141.14 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07013 | 141.14 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07016 | 141.15 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07023 | 140.94 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07039 | 143.07 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0706 | 141.77 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07084 | 141.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 142.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07123 | 142.19 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07154 | 143.57 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07158 | 143.53 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07168 | 143.69 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07248 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07264 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07394 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07394 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07988 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07988 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08063 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0924 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0924 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0924 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0924 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0924 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0924 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10796 | 166.36 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07185 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07185 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07185 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.093 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09303 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09402 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09409 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0942 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0942 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0942 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0942 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09424 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09424 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09439 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09445 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09448 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09462 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0947 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0947 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09471 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09528 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09535 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09535 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09536 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0954 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09553 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09553 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09561 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09565 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09579 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09622 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09622 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0963 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09675 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0973 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09731 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09818 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09826 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09845 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10007 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10022 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10234 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10234 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11197 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11197 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1339 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13713 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15596 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06261 | 117.13 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06261 | 119.07 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06261 | 119.07 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08105 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08107 | 111.08 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08187 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08187 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08194 | 113.67 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.082 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08206 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08206 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08209 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08209 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08213 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08213 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08215 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08215 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08215 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08217 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08217 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08217 | 109.41 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08217 | 109.42 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08226 | 109.33 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08227 | 109.5 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08231 | 109.51 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08234 | 109.66 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08246 | 109.58 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08252 | 109.81 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08252 | 109.81 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08254 | 109.38 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08303 | 111.32 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08309 | 110.37 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08309 | 110.37 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08311 | 110.92 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08313 | 111.07 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08325 | 110.06 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08325 | 110.11 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08332 | 110.76 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08335 | 110.47 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08348 | 112.66 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08385 | 111.44 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08385 | 111.44 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08392 | 111.29 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08431 | 111.35 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0848 | 111.5 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0848 | 111.51 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08556 | 113.16 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08563 | 113.12 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08579 | 113.27 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08721 | 115.88 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08733 | 115.5 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08919 | 116.16 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08919 | 116.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09758 | 120.13 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09758 | 120.94 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11669 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11951 | 132.28 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 126.95 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 128.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 129.77 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 131.84 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 132.66 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 132.66 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 132.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 132.66 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15047 | 203.21 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.06472 | 103.24 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14914 | 103.19 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15513 | 101.72 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15513 | 104.75 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15513 | 104.75 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17128 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17128 | 100.36 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.02 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.1 | P11:21:EES:RVB:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.12 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.12 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.13 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.18 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.18 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.18 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.27 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.27 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.27 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.3 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 100.3 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 101.32 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 101.75 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 103.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17226 | 103.24 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17381 | 101.62 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17391 | 100.58 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17391 | 100.58 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17393 | 101.18 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17397 | 101.35 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17417 | 100.24 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17417 | 100.28 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17418 | 102.46 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17427 | 101.02 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17439 | 100.73 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17469 | 101.28 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17469 | 101.29 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17534 | 101.69 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17599 | 101.73 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17688 | 101.89 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17689 | 101.9 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17792 | 103.64 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17804 | 103.6 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1783 | 103.77 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17832 | 103.39 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17837 | 103.51 | Potential P4 Event - POI 523823_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18051 | 106.58 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18076 | 106.63 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18083 | 106.08 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18083 | 106.4 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18314 | 101.86 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1841 | 107.58 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19886 | 111.97 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25641 | 122.1 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25664 | 159.35 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.32604 | 187.51 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.32816 | 188.69 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3285 | 188.56 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3285 | 188.56 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3285 | 188.56 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.3285 | 196.01 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18245 | 102.64 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23526 | 111.92 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25642 | 160.18 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.3257 | 188.08 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32784 | 189.3 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32816 | 189.17 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32816 | 189.17 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32816 | 189.17 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32816 | 196.69 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07185 | 136.37 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07185 | 138.58 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07185 | 138.58 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.093 | 128.58 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09303 | 128.3 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 126.52 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09394 | 126.52 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09402 | 131.58 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09409 | 125.9 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09416 | 126.28 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09417 | 126.11 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.89 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.89 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.9 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.93 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 125.94 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.09 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.09 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.09 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.1 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.1 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.12 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.13 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.15 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.18 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.21 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.21 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.25 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.26 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.29 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.29 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.34 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.35 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.36 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.36 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.38 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.4 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.4 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.45 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.46 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.5 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.57 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.6 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.6 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.61 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.61 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.62 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.62 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.63 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.63 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.64 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.67 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.67 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.68 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.68 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.7 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.74 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.81 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.84 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.92 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.92 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.92 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.92 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.92 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.94 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.96 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 126.96 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.33 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.33 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.33 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.39 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.39 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 127.45 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 128 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 128.77 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 130.63 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09418 | 131.12 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0942 | 126.09 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0942 | 126.1 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0942 | 126.1 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09424 | 126.14 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09424 | 126.14 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 126.25 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 126.26 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09427 | 126.26 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 125.72 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 126.29 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 126.3 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09439 | 126.2 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 126.39 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09445 | 126.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09448 | 126.58 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09462 | 126.49 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0947 | 126.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0947 | 126.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09471 | 126.26 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09528 | 128.46 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09535 | 127.38 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09535 | 127.38 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09536 | 128 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09539 | 127.5 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0954 | 128.18 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09553 | 127.03 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09553 | 127.08 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09561 | 127.78 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09579 | 130.08 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09622 | 128.69 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09622 | 128.69 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0963 | 128.37 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09675 | 128.45 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0973 | 128.71 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09731 | 128.72 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09818 | 130.56 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09826 | 130.51 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09845 | 130.68 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10007 | 133.73 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10022 | 133.15 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10234 | 133.73 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10234 | 133.85 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11197 | 138.8 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11197 | 139.72 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1339 | 139.88 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13713 | 155.33 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 148.52 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 151.14 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 152.15 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 154.71 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 155.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 155.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 155.73 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13778 | 155.73 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15596 | 210.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06261 | 118.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06261 | 120.77 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06261 | 120.78 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08105 | 112.06 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08107 | 111.82 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08187 | 110.27 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08187 | 110.27 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08194 | 114.68 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.082 | 109.72 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08206 | 109.91 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08206 | 110.05 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.69 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.71 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.72 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.73 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.9 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.92 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.92 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.94 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.97 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.99 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 109.99 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.03 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.04 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.06 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.06 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.11 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.12 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.13 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.13 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.15 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.16 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.16 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.2 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.21 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.25 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.31 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.33 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.34 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.34 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.34 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.35 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.35 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.36 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.36 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.37 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.4 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.4 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.41 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.41 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.43 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.46 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.52 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.55 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.62 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.62 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.62 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.62 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.62 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.64 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.65 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.65 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.69 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.69 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.69 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.97 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.97 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 110.97 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 111.02 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 111.02 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 111.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 111.55 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 112.23 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 113.85 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08208 | 114.27 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08209 | 109.9 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08209 | 109.9 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08213 | 109.93 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08213 | 109.94 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08215 | 110.03 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08215 | 110.04 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08215 | 110.04 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08217 | 109.57 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08217 | 109.57 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08217 | 110.07 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08217 | 110.07 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08226 | 109.98 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08227 | 110.15 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08231 | 110.06 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08234 | 110.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08246 | 110.24 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08252 | 110.47 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08252 | 110.47 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08254 | 110.04 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08303 | 111.95 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08309 | 111.01 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08309 | 111.01 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08311 | 111.56 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08313 | 111.12 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08313 | 111.71 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08325 | 110.71 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08325 | 110.75 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08332 | 111.37 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08348 | 113.37 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08385 | 112.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08385 | 112.16 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08392 | 111.88 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08431 | 111.95 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0848 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0848 | 112.18 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08556 | 113.79 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08563 | 113.74 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08579 | 113.89 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08721 | 116.55 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08733 | 116.04 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08919 | 116.55 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08919 | 116.65 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09758 | 120.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09758 | 121.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11669 | 121.91 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11951 | 135.37 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 129.44 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 131.72 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 132.6 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 134.83 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 135.72 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 135.72 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 135.72 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12007 | 135.72 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15047 | 203.95 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.26 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.29 | 511568 TERRYRD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.3 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.3 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.3 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB :::: | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.3 | Potential P4 Event - POI 511568_1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.3 | Potential P4 Event - POI 511568_4 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.3 | Potential P4 Event - POI 511568_5 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.36 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.36 | Potential P4 Event - POI 760938_3 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.4 | Potential P4 Event - POI 511468_7 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07424 | 114.4 | Potential P4 Event - POI 760938_0 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 956 | 956 | 0.07631 | 112.13 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 115.41 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 115.42 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 115.42 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 115.46 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 115.46 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 114.08 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 114.1 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 114.1 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 114.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 331 | 373 | 0.05233 | 114.18 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05063 | 148.79 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05101 | 146.07 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05134 | 146.3 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0522 | 146.94 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0522 | 147.07 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0528 | 151.92 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05471 | 172.75 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05477 | 172.27 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05477 | 172.27 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0548 | 169.96 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0548 | 171.98 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0548 | 171.99 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05576 | 157.46 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05576 | 159.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05576 | 160.38 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05576 | 162.63 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05576 | 163.55 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05576 | 163.55 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05685 | 152.03 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05685 | 153.24 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12213 | 138.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12253 | 125.77 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12253 | 125.77 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12268 | 125.15 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12275 | 125.53 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12276 | 125.34 | 635740 DIAMOND TRL3 345 636399 HILLS-DT-RX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12276 | 125.36 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.18 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.34 | 640460 KEAR.NE.CN 9 34.5 3WXFMR KEARNEYNE T2 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.34 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.34 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.35 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.37 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.38 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.4 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.43 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.44 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.44 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.5 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.51 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.54 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.54 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.59 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.61 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.61 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.61 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.63 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.66 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.66 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.7 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.71 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.75 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.82 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.85 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.85 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.86 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.86 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.87 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.87 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.88 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.88 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.89 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.92 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.92 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.93 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.94 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 125.96 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.06 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.09 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.18 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.18 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.18 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.18 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.18 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.2 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.21 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.21 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.26 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.26 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.27 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.46 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.46 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.46 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.51 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.51 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 126.55 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.28 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 127.75 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 129.87 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12277 | 129.92 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12279 | 125.34 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12279 | 125.34 | P12:230:UMZ:# 20013 #:: PROPER N-1 FOR TAP BISON___-GE4:HV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12279 | 125.35 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12279 | 125.35 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12283 | 125.39 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12283 | 125.39 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12286 | 125.5 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12286 | 125.51 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12286 | 125.51 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12287 | 124.96 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12289 | 125.55 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12289 | 125.55 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.123 | 125.45 | 539783 CRKCK 3 115 766081 G21-085-TAP 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12301 | 125.65 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12304 | 125.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12321 | 125.74 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12329 | 125.83 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1233 | 130.43 | Potential P4 Event - POI 560022_14 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12331 | 126.01 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12331 | 126.01 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12332 | 125.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12398 | 126.64 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12398 | 126.64 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12401 | 127.73 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12409 | 127.27 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12412 | 127.45 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12417 | 126.29 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12417 | 126.34 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12427 | 126.76 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12429 | 127.51 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12434 | 127.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1249 | 127.7 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12537 | 127.77 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12574 | 127.94 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12575 | 127.95 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12708 | 129.85 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12715 | 129.79 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12734 | 129.97 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12803 | 134.4 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12803 | 136.62 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12803 | 136.62 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12809 | 129.27 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12852 | 127.87 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12852 | 127.87 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12924 | 132.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13003 | 132.96 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13114 | 133.28 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13114 | 133.4 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13373 | 127.45 | 523961 POTTER_CO 7 345 523959 POTTER_CO 6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13767 | 151.79 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 145.67 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 147.96 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 148.9 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 151.28 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 152.22 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 152.22 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 152.22 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13832 | 152.22 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13856 | 137.84 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13856 | 138.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2033 | 209.91 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10643 | 120.95 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10678 | 109.61 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10678 | 109.61 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10691 | 109.07 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10698 | 109.25 | 507760 SW SHV 7 345 769140 G22-108-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10698 | 109.4 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.04 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.05 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.06 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.07 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.25 | 505552 GORE 5 161 505554 WEBFALL5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.26 | 345609 4RIVMIN 1 138 345831 4TAUM S 1 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.27 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.29 | P23:500:EES:MOUNTSOLIVE:R3976::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.31 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.32 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.32 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.37 | 539654 CIM-PLT3 115 539780 CIM-PLT 13.8 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.39 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.41 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.41 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.46 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.47 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.47 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.47 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.49 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.51 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.51 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.55 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.56 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.6 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.66 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.68 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.68 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.69 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.69 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.7 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.7 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.71 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.71 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.71 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.74 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.74 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.75 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.75 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.77 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.81 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.96 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.96 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.97 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.97 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.97 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.99 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.99 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 109.99 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.04 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.04 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.04 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.21 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.21 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.21 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.26 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.26 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.29 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 110.92 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 111.34 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 113.18 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10699 | 113.23 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.107 | 109.24 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.107 | 109.25 | 652573 STEGALL4 230 652873 STEGALL-LNX3 230 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10704 | 109.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10704 | 109.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10707 | 109.38 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10707 | 109.39 | 514778 CLEOCOR4 138 514788 GLASMTN4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10707 | 109.39 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10708 | 108.91 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 27WP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.10708 | 108.91 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4